## Prj Legend
MTEP11 MISO Transmission Expansion Plan 2011 |  | Appendices A, B, C
Project Table Field Legend
Appendix A contains projects which are being or have been approved by MISO Board of Directors.
Transmission Owners are obligated to make a good faith effort to construct projects in Appendix A.
Appendix B projects have been reviewed by MISO staff for need and effectivenes.
Appendix C projects are new to planning process or conceptual
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Project Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEP11 planning cycle. "A in MTEP11" projects were reviewed and approved in MTEP11. This column also indicates what projects were approved in prior MTEPs that are not yet in service.
Region | MISO Planning Region: Central, East or West
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Project ID: MISO project identifier
Project Name | Project name (short name)
Project Description | A description of the project's components
State 1 | State project is located or first state if in multiple states
State 2 | If applicable, the second state the project is located
Allocation Type per FF | Project Type per Attachment FF of Tariff. BaseRel is Baseline Reliability, GIP is Generator Interconnection Project, TDSP is Transmission Delivery Service Project, RegBen is Regionally Beneficial Project, Other is non of the above. Preliminary project types may be designated for Appendix B and C projects
Share Status | Projects moving to Appendix A in current planning cycle are eligible for cost allocation per terms in Attachment FF. Projects are Shared, Not Shared or Excluded. Preliminary sharing designations may be input for Appendix B or C projects.
Other Type | Indicates the project driver behind Other type projects.
Estimated Cost | Total estimated project cost from Facility table
Expected ISD (Min/Max) | Dates when project is expected to be in service. Min and Max dates. Expected ISD are in Facility table.
Plan Status | Indicates where project is in planning or implementation. Proposed, Planned, Under Construction, In Service. Minimum of information in Facility table
Max kV | Maximum facility voltage in project. Summary information from Facility table
Min kV | Minimum facility voltage in project. Summary information form Facility table
App ABC | Appendix the project is in. B>A or C>B for projects moving during this planning cycle.
MISO Facility | Y for facilities under MISO functional control. NT for non-transferred facilities under Agency Agreements

## Projects
MTEP11 MISO Transmission Expansion Plan 2011 | [21 empty] | Appendices A, B, C
| Appendices A, B, C: Project Table 9/7/2011 | [13 empty] | Project Summary Information from Facility table
Target Appendix | Planning Region | Geographic Location by TO Member System | PrjID | Prj_Rec_Date | Owner_PrjID | Project Name | Project Description | State 1 | State2 | Board Approved | Allocation Type per FF | Share Status | Other Type | Estimated Cost | Expected ISD (Min) | Expected ISD (Max) | Min of Plan Status | Max kV | Min kV | App ABC | MISO Facility
.
A in MTEP11 | Central | AmerenIL | 2065 | 2011-04-22 |  | Stallings 345/138 kV Sub - Replace 560 MVA 345/138 kV transformer | Stallings 345/138 kV Substation-Replace 560 MVA, 345/138 kV Transformer with 700 MVA unit. Install a 345kV ring bus | IL |  |  | BaseRel | Shared |  | 10075000 | 2012-06-01 | 2012-06-01 | Planned | 345 | 138 | B>A | Y
A in MTEP11 | Central | AmerenIL | 2239 | 2011-09-06 | 17 Cand. MVP Port.1 (64) FG9 | Proposed MVP Portfolio 1 - Sidney to Rising 345 kV line | Sidney to Rising 345 kV line, plus 345 kV ring bus at Rising and breaker-and-a-half arrangement at Sidney. | IL |  |  | MVP | Shared |  | 83230000 | 2016-06-01 | 2016-11-15 | Planned | 345 |  | B>A | Y
A in MTEP11 | Central | AmerenIL | 2980 | 2010-12-06 |  | Tazewell-San Jose Rail - Reconductoring | Tazewell-San Jose Rail Substation section of East Springfield-Tazewell-1384 138 kV Line - Reconductor 3.67 miles of 927 kcmil ACAR conductor at the Tazewell end of the line with conductor capable of carrying at least 1278 A under summer emergency conditions | IL |  |  | BaseRel | Not Shared |  | 3251000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | B>A | Y
A in MTEP11 | Central | AmerenIL | 2981 | 2011-04-22 |  | McLean-Oglesby 138 kV Reconductor | Replace 9.72 miles of 138 kV line on L1382, from McLean County Substation to El Paso Tap to a minimum 1200A SE capability | IL |  |  | BaseRel | Not Shared |  | 5100000 | 2013-09-01 | 2013-09-01 | Planned | 138 |  | B>A | Y
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Palmyra Tap-Quincy-Meredosia - Ipava & Meredosia-Pawnee 345 kV Line | Palmyra Tap to Quincy to Meredosia to Ipava 345 line and Meredosia to Pawnee 345 kV line. Install additional transformers at Quincy, Meredosia and Pawnee. 345 kV ring bus at Quincy, Meredosia, and Ipava, with breaker-and-a-half arrangement at Pawnee and Palmyra Tap Substations. | IL |  |  | MVP | Shared |  | 432160000 | 2016-06-01 | 2017-11-15 | Planned | 345 | 138 | B>A | Y
A in MTEP11 | Central | AmerenIL | 3169 | 2011-09-06 | 10 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Pawnee to Pana - 345 kV Line | Pawnee to Pana 345 kV, 31 mile line including additional transformer at Pana | IL |  |  | MVP | Shared |  | 99360000 | 2018-11-15 | 2018-11-15 | Planned | 345 | 138 | B>A | Y
A in MTEP11 | Central | AmerenIL | 3337 | 2011-04-22 | G931 | G931 Paxton-Gilman Reconductoring | Reconductor to 1200 A summer emergency capability | IL |  |  | GIP | Not Shared |  | 7390000 | 2013-12-01 | 2013-12-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL | 3357 | 2011-04-22 | G545, G569 | Hennepin-E. Kewanee L1552 - Increase Ground Clearance | G545 and G569 Increase ground clearance on 477 kcmil ACSR conductor to permit operation at 120 degrees C. Upgrade E. Kewanee breaker and terminal equipment to 1200 A capability | IL |  |  | GIP | Not Shared |  | 3180000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL | 3358 | 2011-04-22 |  | G545 Generator connection and bus rearrangement - E. Kewanee | Rearrange 138 kV bus at E. Kewanee and install terminal equipment (including 1200 A breaker) to connect wind farm (G545) | IL |  |  | GIP | Not Shared |  | 1501000 | 2012-10-15 | 2012-10-15 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL | 3359 | 2011-04-22 |  | G569 Generator connection and bus upgrade - E. Galesburg | Upgrade 138 kV bus at E. Galesburg and install terminal equipment, including 1200 A breaker, to facilitate connection of wind farm (G569). | IL |  |  | GIP | Not Shared |  | 834000 | 2012-10-01 | 2012-10-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL | 3360 | 2011-04-22 | AMRN21 | G931 Generator connection and Establishment of Sheldon Soth Switching Station | Construct a new 138 kV switching station to connect a new wind farm (G931) to the Watseka-Morrison Ditch-1 138 kV line. Upgrade relaying at Watseka terminal. | IL |  |  | GIP | Not Shared |  | 4425000 | 2011-05-06 | 2011-05-06 | In Service | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL | 3361 | 2011-04-22 |  | G996 Generator connection and bus upgrade - Paxton, South | Install terminal equipment, including 2000 A breaker, to facilitate connection of wind farm (G996). Install 2000 A bus-tie breaker | IL |  |  | GIP | Not Shared |  | 1512200 | 2011-07-26 | 2011-07-26 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL | 3370 | 2011-04-22 |  | Oreana Substation - Add 138-69 kV Transformer | To accommodate the installation of a new 138-69 kV transformer at Oreana, install 1-2000 A breaker and 2-2000 A disconnect switches to expand ring bus. Install 138 kV, 600 A motor operated disconnect switch at high-side of new 138-69 kV transformer. | IL |  |  | Other | Not Shared | Condition | 750000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenIL, DEM | 2237 | 2011-09-06 | 11 Cand. MVP Port.1 (62) | Proposed MVP Portfolio 1 - Pana - Mt. Zion - Kansas - Sugar Creek 345 kV line | Pana to Mt. Zion to Kansas to Sugar Creek 345 kV line. Install transformers at Mt. Zion and Kansas, with 345 kV ring bus at Mt. Zion and breaker-and-a-half arrangement at Kansas and Pana. | IL |  |  | MVP | Shared |  | 318410000 | 2018-11-15 | 2019-11-15 | Planned | 345 | 138 | B>A | Y
A in MTEP11 | Central | AmerenIL, MEC | 3022 | 2011-09-06 | 16 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Fargo-Galesburg-Oak Grove 345 kV Line | Fargo-Galesburg-Oak Grove (MEC) 345 kV Line - New 70 mile, 3000 A summer emergency capability line. 345 kV ring bus at Fargo. | IA | IL |  | MVP | Shared |  | 272249969 | 2014-12-01 | 2019-11-15 | Planned | 345 | 138 | B>A | Y
A in MTEP11 | Central | AmerenMO | 2306 | 2011-04-22 | AMRN2 | Nortwest Cape Area 345/161 kV Substation | Install 560 MVA, 345/161 kV Transformer. Provide 345 kV supply from 11 mile 345 kV line extension from Lutesville Substation | MO |  |  | BaseRel | Shared |  | 30751000 | 2016-06-01 | 2016-06-01 | Planned | 345 | 161 | B>A | Y
A in MTEP11 | Central | AmerenMO | 3170 | 2011-09-06 | 08 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Adair-Palmyra Tap 345 kV Line | Adair - Palmyra 345 kV, 58 miles of line; Establish Palmyra Tap Substation | MO |  |  | MVP | Shared |  | 112790000 | 2016-11-15 | 2020-11-15 | Planned | 345 |  | B>A | Y
A in MTEP11 | Central | AmerenMO | 3355 | 2011-04-22 | AMRN20 | Labadie Breaker Replacements | Replace Breakers on Bland and Montgomery line positions with 3000 A, 50 kA breakers | MO |  |  | Other | Not Shared | Reliability | 2610000 | 2011-12-31 | 2011-12-31 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | Central | AmerenMO | 3368 | 2011-04-22 |  | Bailey Substation | Install 2-2000 A bus-tie breakers and 2-138 kV circuit switchers | MO |  |  | Other | Not Shared | Reliability | 4000000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | AmerenMO, ITCM | 2248 | 2011-09-06 | 07 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Adair - Ottumwa 345 | Adair Substation - New 560 MVA, 345/161 kV Transformer. New 71 mile 345 kV line from Adair to Ottumwa with 3000 A summer emergency capability. 345 kV ring bus at West Adair | IA | MO |  | MVP | Shared |  | 244627764 | 2017-06-01 | 2020-11-15 | Planned | 345 | 161 | B>A | Y
A in MTEP11 | Central | DEM | 3377 | 2010-09-15 | AMIN0342 | Scottsburg 69kV - 28.8MVAR Capacitor | Replace Scottsburg 69kV - 7.2Mvar capacitor with a 28.8 Mvar capacitor and upgrade 69kV capacitor switching equipment | IN |  |  | Other | Not Shared | Reliability | 500000 | 2015-12-31 | 2015-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3378 | 2010-09-15 | AMOH0286 | Canal 69kV Dist Sub | Canal Sub - Purchase land and build 22.4MVA, 69/12kV sub near Canal Road and Allison Street in the 5762 ckt. | OH |  |  | Other | Not Shared | Reliability | 756196 | 2012-06-01 | 2012-06-01 | Planned | 69 | 12 | C>B>A | Y
A in MTEP11 | Central | DEM | 3379 | 2010-09-15 | AMIN0138 | Shelbyville McKay Rd. 69kV Dist Sub | Shelbyville McKay Rd. - add new 69/12kV distribution sub in the 6976 ckt. Loop through with 954acsr and a set of 1200A line switches. | IN |  |  | Other | Not Shared | Reliability | 303710 | 2014-06-01 | 2014-06-01 | Planned | 69 | 12 | C>B>A | Y
A in MTEP11 | Central | DEM | 3380 | 2010-09-15 | AMIN0340 | Noblesville Sta. 138kV Brkrs and 345kV Ckt Sws | Noblesville Gen. Sta. - Replace 138KV OB OCB: 138TR, 13869-9, 138230-7, 13886 and Circuit Switchers: 345230-11, 34519. | IN |  |  | Other | Not Shared | Condition | 2909606 | 2011-12-31 | 2011-12-31 | Planned | 345 | 138 | C>B>A | Y
A in MTEP11 | Central | DEM | 3383 | 2010-10-12 | AMIN0364 | H.E. Rocklane Alternate 69kV Feed | Ckt. 6999 new Sherman Rd. Jct. to H.E. Rocklane line section. Replace DEM 69kV poles to accommodate new H.E. tap line. This will be an alternate feed to Rocklane - operated N.O. - built and owned by HE, inside DEM area. | IN |  |  | Other | Not Shared | Reliability | 64568 | 2011-02-06 | 2011-02-06 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3384 | 2010-09-15 | AMIN0382 | Hortonville to Marathon Jct. 69kV Reconductor | Hortonville to Marathon Jct. section of ckt. 6917 - Replace 336ACSR and 477ACSR with 954ACSS@200C. Upgrade Marathon Jct 600A switches to 1200A. | IN |  |  | Other | Not Shared | Reliability | 1409099 | 2012-12-01 | 2012-12-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3385 | 2010-09-15 | AMIN0376 | Carmel Homeplace to Springmill Jct 69kV Reconductor | Carmel Homeplace to Springmill Jct. section of ckt. 69155 - Reconductor with 954ACSS@200C | IN |  |  | Other | Not Shared | Reliability | 1691315 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3386 | 2010-09-15 | AMIN0379 | Carmel Springmill Rd. to Hortonville 69kV Line and Brkrs | Carmel Springmill Rd. Sub - Add 3-69kV breakers in straight bus config and build new .23 mile 69kV 954ACSS@200C line from Springmill Sub to old Springmill Jct. to complete circuit to Hortonville. Change operating mode at Homeplace to close loop from 146th to Springmill. | IN |  |  | Other | Not Shared | Reliability | 3000000 | 2016-06-01 | 2016-06-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3387 | 2010-09-15 | AMIN0386 | Tri-County Wind Energy 230kV Station - DPP J028 | J028 - 230kV - Gen. interconnect sub - install three brkr ring bus for 200MW wind farm between Attica and Lafayette in the 23027 ckt. | IN |  |  | GIP | Not Shared |  | 3778246 | 2013-06-01 | 2013-06-01 | Planned | 230 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3388 | 2010-09-15 | AMIN0396 | Walton to Logansport S. 69kV Reconductor | Walton to Logansport S. - Reconductor 69kV - 69110 line with 477acsr at 100C | IN |  |  | Other | Not Shared | Reliability | 1900000 | 2015-06-01 | 2015-06-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3389 | 2011-03-25 | DEM-WVPA01 | WVPA Center Valley 138kV Dist Sub | DEM to install new line switching in the 138kV - 13867 ckt. at intersection with SR39 for tap line to radially feed new WVPA Center Valley dist sub | IN |  |  | Other | Not Shared | Reliability | 236677 | 2011-12-01 | 2011-12-01 | Planned | 138 | 12 | C>B>A | Y
A in MTEP11 | Central | DEM | 3390 | 2010-10-12 | AMIN0414 | Inland Container to Hillsdale 69kV Line Rebuild | Rebuild 69kV - 6906 line from Inland Container to WROW Jct. to Hillsdale - 477acsr26x7 at 100C | IN |  |  | Other | Not Shared | Condition | 3663434 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3391 | 2010-09-15 | AMIN0415 | Elnora to Newberry 69kV Line Rebuild | Rebuild 69kV - 6959 line section from Elnora to Newberry - 477acsr26x7 at 100C | IN |  |  | Other | Not Shared | Condition | 1716818 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | Central | DEM | 3392 | 2011-01-24 | DEM-LGEE01 | DEM Speed to LGEE Paddys West 345kV tie | New DEM Speed to LGEE Paddys West 345kV tie line | IN |  |  | Other | Not Shared | Reliability | 15000000 | 2012-12-31 | 2012-12-31 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | Central | DEM, NIPS | 2202 | 2011-07-18 | 14 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Reynolds to Greentown 765 kV line | Reynolds to Greentown 765 kV line | IN |  |  | MVP | Shared |  | 186875000 | 2018-06-01 | 2018-08-01 | Planned | 765 | 345 | B>A | Y
A in MTEP11 | Central | IPL | 3273 | 2010-09-15 |  | Southwest - Stout CT Line Rating Upgrade | Increase line rating above 322 MVA to mitigate the potential overload | IN |  |  | Other | Not Shared | Reliability | 300000 | 2011-06-01 | 2011-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | IPL | 3274 | 2010-09-15 |  | South - Stout S Line Rating Upgrade | Increase line rating above 272 MVA to mitigate the potential overload | IN |  |  | Other | Not Shared | Reliability | 350000 | 2011-06-01 | 2011-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | Central | Vectren (SIGE) | 2460 | 2008-10-31 | SIGE1 | Leonard Rd 69kV Substation | Add new 69kV switching substation near Leonard Rd | IN |  |  | Other | Not Shared | Reliability | 2150000 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | C>B>A | NT
A in MTEP11 | Central | Vectren (SIGE) | 2462 | 2008-10-31 | SIGE3 | Y53 Stringtown to Folz Reconductor | Reconductor existing 69kV line for more capacity | IN |  |  | Other | Not Shared | Condition | 2500000 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | C>B>A | NT
A in MTEP11 | Central | Vectren (SIGE) | 2463 | 2008-10-31 | SIGE4 | Y31 Mt Vernon to Givens 69kV recond. | Reconductor existing 69kV line for more capacity | IN |  |  | Other | Not Shared | Condition | 5700000 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | C>B>A | NT
A in MTEP11 | Central | Vectren (SIGE) | 2464 | 2008-10-31 | SIGE5 | Y33 Mt Vernon to New Harmony 69kV recond. | Reconductor existing 69kV line for more capacity | IN |  |  | Other | Not Shared | Condition | 10600000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | C>B>A | NT
A in MTEP11 | East | ITC | 1868 | 2010-10-20 |  | Cato GIS replacement | Replace GIS Equipment | MI |  |  | Other | Not Shared | Condition | 5400000 | 2012-12-01 | 2012-12-01 | Planned | 120 |  | C>B>A | Y
A in MTEP11 | East | ITC | 2931 | 2009-09-14 |  | Adams-Spokane/Burns1-Jewel 120 kV Rebuild | Rebuild 2.4 miles of DC 3/0 Cu 120 kV lin to 1431 ACSR 230 kV construction. | MI |  |  | BaseRel | Not Shared |  | 3200000 | 2012-06-30 | 2012-06-30 | Proposed | 120 |  | C>B>A | Y
A in MTEP11 | East | ITC | 3276 | 2010-09-15 | 2 | ITCT Annual Breaker Replacement Program for 2013 | Annual Breaker Replacement Program | Mi |  |  | Other | Not Shared | Condition | 9000000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3277 | 2010-09-15 | 3 | ITCT Annual NERC Relay Loadability Compliance Program for 2013 | Annual NERC Relay Loadability Program | Mi |  |  | Other | Not Shared | Reliability | 2400000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3278 | 2010-09-15 | 4 | ITCT Annual Potential Device Replacement Program for 2013 | Annual Potential Device Replacement Program | Mi |  |  | Other | Not Shared | Condition | 300000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3279 | 2010-09-15 | 5 | ITCT Annual Relay Betterment Program for 2013 | Annual Relay Betterment Program | Mi |  |  | Other | Not Shared | Condition | 1800000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3280 | 2010-09-15 | 6 | ITCT Annual Wood Pole Replacement Program for 2013 | Annual Wood Pole Replacement Program | Mi |  |  | Other | Not Shared | Condition | 3000000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3281 | 2010-09-15 | 7 | Lima Substation | Distribution Interconnection Request | Mi |  |  | Other | Not Shared | Distribution | 8400000 | 2012-12-31 | 2012-12-31 | Planned | 120 |  | C>B>A | Y
A in MTEP11 | East | ITC | 3283 | 2010-09-15 | 9 | Dexter Township Substation | Distribution Interconnection Request | Mi |  |  | Other | Not Shared | Distribution | 2676000 | 2012-11-01 | 2012-11-01 | Planned | 120 |  | C>B>A | Y
A in MTEP11 | East | ITC | 3284 | 2010-09-15 | 10 | ITCT Customer Interconnections - Year 2015 | Distribution Interconnection Request | Mi |  |  | Other | Not Shared | Distribution | 2000000 | 2015-12-31 | 2015-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3285 | 2011-07-18 | 11 | Fermi & Shoal 120kV Capacitors | 33.3 Mvar Capacitors at Fermi and Shoal 120kV | Mi |  |  | BaseRel | Not Shared |  | 3800000 | 2013-06-01 | 2014-06-01 | Planned | 120 |  | C>B>A | Y
A in MTEP11 | East | ITC | 3286 | 2011-07-18 | 12 | Fermi 345kV Disconnect Replacement Project - 3rd Row | Replace 345kV Disconnects, add 3rd 345kV Row | Mi |  |  | Other | Not Shared | Condition | 5050000 | 2012-04-30 | 2013-12-31 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | East | ITC | 3495 | 2011-03-28 |  | NERC Alert Facility Ratings for 2011 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI |  |  | Other | Not Shared | Reliability | 1700000 | 2011-12-31 | 2011-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | ITC | 3503 | 2011-03-28 |  | Air Flow Spoilers Installation | Install air flow spoilers on approximately 15 miles of the targeted areas of the Belle River-Greenwood-Pontiac and Belle River-Blackfoot 345 kV double circuit tower lines. | MI |  |  | Other | Not Shared | Reliability | 1620000 | 2012-12-31 | 2012-12-31 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | East | ITC | 3516 | 2011-06-30 | J025 | J025-Macomb County LF Gas Gen. Facility | 12.8 MW LF Gas Gen. tapping the Carbon Tap on the 120kV Jewell - St. Clair 120kV line. | MI |  |  | GIP | Shared |  | 485000 | 2011-09-01 | 2011-09-01 | Planned | 120 |  | C>B>A | Y
A in MTEP11 | East | METC | 1809 | 2010-10-20 |  | Keystone-Hodenpyl 138 kV Rebuild | Rebuild the 27 mile Keystone to Hodenpyl 138 kV line to 954 ACSR (Pre-build to 230 kV construction). | Mi |  |  | BaseRel | Shared |  | 32600000 | 2013-12-31 | 2013-12-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 2812 | 2010-10-20 |  | Twining - Alcona 138kV Rebuild | Rebuild the Twining-Mio 138kV 38 mile line to 954 ACSR future-double-circuit (pre-built to 230kV) | MI |  |  | BaseRel | Shared |  | 43300000 | 2012-05-31 | 2012-05-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3139 | 2010-10-20 |  | Tippy-Wexford 138 kV Circuit Uprgrade | Terminal Equipment upgrade at Tippy | MI |  |  | Other | Not Shared | Reliability | 20000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3287 | 2010-09-15 | 1 | Riggsville Rebuild | Rebuild 138 kV bus and switches | Mi |  |  | Other | Not Shared | Condition | 4600000 | 2011-09-30 | 2011-09-30 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3288 | 2010-09-15 | 2 | METC Annual Breaker Replacement Program for 2013 | Annual Breaker Replacement Program | Mi |  |  | Other | Not Shared | Condition | 6000000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3289 | 2010-09-15 | 3 | METC Annual NERC Relay Loadability Compliance Program for 2013 | Annual NERC Relay Loadability Program | Mi |  |  | Other | Not Shared | Reliability | 2400000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3290 | 2010-09-15 | 4 | METC Annual Potential Device Replacement Program for 2013 | Annual Potential Device Replacement Program | Mi |  |  | Other | Not Shared | Condition | 300000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3291 | 2010-09-15 | 5 | METC Annual Relay Betterment Program for 2013 | Annual Relay Betterment Program | Mi |  |  | Other | Not Shared | Condition | 1200000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3292 | 2010-09-15 | 6 | METC Annual Wood Pole Replacement Program for 2013 | Annual Wood Pole Replacement Program | Mi |  |  | Other | Not Shared | Condition | 4800000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3293 | 2010-09-15 | 7 | METC Annual Battery Replacement Program for 2013 | Annual Battery Replacement Program | Mi |  |  | Other | Not Shared | Condition | 100000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3294 | 2010-09-15 | 8 | METC Annual Power Plant Control Relocation Program for 2013 | Annual Power Plant Control Relocation Program | Mi |  |  | Other | Not Shared | Operations | 3120000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3295 | 2010-09-15 | 9 | METC Sag Clearance Program for 2013 | Sag Clearance Program | Mi |  |  | Other | Not Shared | Clearance | 3600000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3296 | 2010-09-15 | 10 | METC Spill Prevention Control and Countermeasure Program for 2011 | Annual SPCC Program | Mi |  |  | Other | Not Shared | Condition | 3100000 | 2011-12-31 | 2011-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3297 | 2010-09-15 | 11 | METC Spill Prevention Control and Countermeasure Program for 2012 | Annual SPCC Program | Mi |  |  | Other | Not Shared | Condition | 3100000 | 2012-12-31 | 2012-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3298 | 2010-09-15 | 12 | METC Spill Prevention Control and Countermeasure Program for 2013 | Annual SPCC Program | Mi |  |  | Other | Not Shared | Condition | 3100000 | 2013-12-31 | 2013-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3299 | 2010-09-15 | 13 | METC Customer Interconnections - Year 2015 | Distribution Interconnection Request | Mi |  |  | Other | Not Shared | Distribution | 2500000 | 2015-12-31 | 2015-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3303 | 2010-10-20 |  | Cottage Grove-East Tawas 138 kV Rebuild | Rebuild 12.3 miles of 138 kV line | MI |  |  | BaseRel | Shared |  | 11400000 | 2015-06-01 | 2015-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3304 | 2011-03-28 | 18 | Croton-Nineteen Mile 138 kV Rebuild | Rebuild 21.5 miles of 138 kV 110 CU to 954 ACSR (Pre-build to 230 kV construction). | Mi |  |  | BaseRel | Shared |  | 26600000 | 2013-12-31 | 2013-12-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3306 | 2010-09-15 | 20 | Karn-Cottage Grove 138 (Karn Position 488) Relay Replacement Project |  | Mi |  |  | Other | Not Shared | Reliability | 200000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3308 | 2010-09-15 | 22 | Livingston to Gaylord 138 kV Dual Pilot Relay Protection Scheme Installation | Install new dual pilot relay scheme on 138kV circuit | Mi |  |  | Other | Not Shared | Reliability | 315000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3491 | 2011-03-28 |  | NERC Alert Facility Ratings for 2011 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI |  |  | Other | Not Shared | Reliability | 2100000 | 2011-12-31 | 2011-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | East | METC | 3505 | 2011-04-19 | 1 | Eaton Rapids Load Interconnection | Serve new load in Eaton Rapids with 2 new 138kV circuits from Clinton Jct. and the Delhi-Tompkins circuit | MI |  | 2011-06-14 | Other | Not Shared | Distribution | 28500000 | 2013-01-01 | 2013-01-01 | Planned | 138 |  | A | Y
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | G905-Gratiot County Wind Generation | 200 MW wind farm connecting at the new METC owned Redstone substation | MI |  |  | GIP | Shared |  | 21630500 | 2011-10-31 | 2012-12-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3518 | 2011-06-30 | G809 | G809-MCV | 190 MW increase of the existing MCV Co-generation plant | MI |  |  | GIP | Shared |  | 64000 | 2012-06-01 | 2012-06-01 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | East | METC | 3520 | 2011-07-18 | NERC Alert Ratings | NERC Alert Facility Ratings for 2011: Eureka - Vestaburg 138 kV line upgrade | Eureka - Vestaburg 138 kV line upgrade: Remediate sag limits to conductor rating of circuit | Mi |  |  | BaseRel | Not Shared |  | 1100000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | METC | 3521 | 2011-07-18 | NERC Alert Ratings | NERC Alert Facility Ratings for 2011: Bullock - Summerton 138 kV line upgrade | Bullock - Summerton 138 kV line upgrade: Remediate sag limits to conductor rating of circuit | Mi |  |  | BaseRel | Not Shared |  | 3600000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | East | NIPS | 3203 | 2011-07-18 | 12 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Reynolds to to Burr Oak to Hiple 345 kV | Reynolds to Burr Oak to Hiple 345 kV line and tie in second AEP 345 kV circuits at Reynolds and Hiple | IN |  |  | MVP | Shared |  | 271000000 | 2019-12-31 | 2019-12-31 | Planned | 345 |  | B>A | Y
A in MTEP11 | East | WPSC | 3328 | 2010-09-15 | Barryton Tap | Barryton | New Distribution Interconnection from the Hersey to Weidman circuit | MI |  |  | Other | Not Shared | Distribution | 100000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3329 | 2010-09-15 | BP-WD | Burnips to Wayland | Rebuild the Burnips to Wayland line section with a larger conductor | MI |  |  | Other | Not Shared | Reliability | 7250000 | 2011-12-31 | 2013-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3330 | 2010-09-15 | Casnovia Cap Bank | Cansovia Capacitor Bank | Install a Capacitor Bank tap at the Casnovia substation | MI |  |  | Other | Not Shared | Reliability | 260000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3331 | 2010-09-15 | RW-HT | Redwood to Hart | Rebuild the Redwood to Hart line section with a larger conductor | MI |  |  | Other | Not Shared | Reliability | 750000 | 2015-12-31 | 2015-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3332 | 2011-03-17 | Bass Lake Xsmn | Bass Lake Transmission Upgrade | Install Relaying | MI |  |  | Other | Not Shared | Reliability | 250000 | 2011-02-28 | 2011-02-28 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3333 | 2010-09-15 | Lemon Jct Xsmn | Lemon Junction Transmission Station | Construct a single breaker station | MI |  |  | Other | Not Shared | Reliability | 350000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3334 | 2011-06-23 | CV-SG | Casnovia to Sternberg | Rebuild a portion of the line for Distibution Underbuild | MI |  |  | Other | Not Shared | Reliability | 400000 | 2011-06-30 | 2011-06-30 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | East | WPSC | 3335 | 2010-09-15 | Burnips Xmsn | Burnip Transmission Station Upgrade | Upgrade to replace outdated equipment. Bus, breakers, relays, and other equipment as necessary. | MI |  |  | Other | Not Shared | Condition | 900000 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 174 | 2010-09-15 | 152, F1358 | Canal-Dunn Road 138 kV | Construct a 7.7 mile Canal - Dunn Road 138 ckt , Sum rate 400; install a new 138/69 kV transformer at Dunn Road substation. | WI |  |  | Other | Not Shared | Reliability | 24763300 | 2012-03-01 | 2012-03-01 | Planned | 138 | 69 | B>A | Y
A in MTEP11 | West | ATC LLC | 333 | 2010-09-15 | F3068 | Hiawatha-Indian Lake conversion to 138 kV | Hiawatha-Indian Lake conversion to 138 kV | MI |  |  | Other | Excluded | Condition | 4900000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 1143 | 2010-12-03 | G282, F0339 | G282, 37628-02 | Net: rating of HILLMAN 138/69 kV TRANSFORMER 1 is upgraded to 100 MVA. Int: The Generator is required to provide a 138/34.5kV transformer, a circuit breaker and a disconnect switch on the high side of the 138/34.5kV transformer and 34.5kV facilities to c | WI |  |  | GIP | Not Shared |  | 4200000 | 2012-12-31 | 2012-12-31 | Planned | 0.6 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 1699 | 2010-10-21 |  | Mckenna & Chaffee Ck Capacitor Banks Upgrades | Upgrade Mckenna 6.3 MVAR capacitor bank to 15.3 MVAR and upgrade Chaffee Ck 10.8 MVAR to 14.4 MVAR capacitor bank | WI |  |  | Other | Not Shared | Reliability | 686750 | 2011-07-31 | 2011-07-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 1705 | 2010-09-15 |  | Bass Creek area upgrades | Install a 138/69 kV transformer at Bass Creek substation, Uprate Townline Road-Bass Creek 138 kV line | WI |  |  | Other | Not Shared | Reliability | 6975946.49 | 2011-04-01 | 2011-04-01 | In Service | 138 | 69 | B>A | Y
A in MTEP11 | West | ATC LLC | 1729 | 2010-09-15 | PR03341 | Uprate Straits-McGulpin 138 kV | Uprate overhead portions of Straits-McGulpin 138-kV circuits #1 & #3 to 200 F degree summer emergency ratings | MI |  |  | BaseRel | Not Shared |  | 300000 | 2011-04-20 | 2011-04-20 | In Service | 138 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 1950 | 2010-09-15 | PR01874 | 2nd Kewaunee 345-138 kV Transformer | Reconfigure Kewaunee 345/138 kV switchyard and install a 2nd Kewaunee 345-138 kV transformer of 500 MVA. | WI |  |  | BaseRel | Shared |  | 17697000 | 2011-03-17 | 2011-03-17 | In Service | 345 | 138 | B>A | Y
A in MTEP11 | West | ATC LLC | 2036 | 2010-09-15 | F1444 | Uprate Y-40 Gran Grae-Boscobel 69 kV | Increase line clearance to 200/300 deg F SN/SE | WI |  |  | Other | Not Shared | Condition | 5291028 | 2011-12-15 | 2011-12-15 | Planned | 69 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 2037 | 2011-04-19 | F1602 | Rebuild Dane-Okee 69 kV | Rebuild Dane-Okee 69 kV | WI |  |  | Other | Not Shared | Reliability | 6798033 | 2012-06-19 | 2012-06-19 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 2055 | 2010-09-15 | F2495 | Clear Lake-Woodmin 115 kV | Construct a 7.5 mile 115 kv line from Clear Lake to a new Woodmin distribution substation | WI |  |  | Other | Not Shared | Reliability | 21331000 | 2012-06-01 | 2012-06-01 | Planned | 115 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 2800 | 2010-09-15 | F3042 | Uprate Arpin-Hume 115-kV | Marshfield Electric & Water Department project to increase ground clearance to operate the line at 200 Deg F | WI |  |  | BaseRel | Not Shared |  | 191000 | 2010-09-10 | 2010-09-10 | In Service | 115 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 2820 | 2010-12-03 | F2799 | Replace Bluemound 230/138kV transformerT1 | Replace Bluemound 230/138kV transformer T1 with a 400 MVA unit | WI |  |  | Other | Not Shared | Condition | 8200000 | 2012-05-31 | 2012-05-31 | Planned | 230 | 138 | B>A | Y
A in MTEP11 | West | ATC LLC | 2842 | 2010-09-15 | F1656 | Uprate Spring Green-Stage Coach 69-kV | Uprate Spring Green-Stage Coach 69-kV | WI |  |  | Other | Not Shared | Reliability | 6957394 | 2011-04-08 | 2011-04-08 | In Service | 69 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 2844 | 2011-07-18 | 15 Cand. MVP Port.1 F3123 | Proposed MVP Portfolio 1 - Pleasant Prairie-Zion Energy Center 345 kV line | Construct a new Pleasant Prairie-Zion Energy Center 345-kV line | WI | IL |  | MVP | Shared |  | 28856000 | 2014-03-16 | 2014-03-16 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 2846 | 2010-12-03 | F2894 | Straits power flow control | Install AC-DC-AC Back to Back Voltage Source Converterpower (VSC) flow controller at the Straits 138-kV substation | MI |  | 2011-06-14 | BaseRel | Shared |  | 90000000 | 2014-05-01 | 2014-05-01 | Planned | 138 | 138 | A | Y
A in MTEP11 | West | ATC LLC | 3095 | 2010-09-15 | PR03410 | Uprate 9Mile-Roberts 69 kV line 6952 | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components | MI |  |  | Other | Not Shared | Reliability | 19743031.9999 | 2012-04-01 | 2012-04-01 | Planned | 69 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 3108 | 2010-09-15 | PR03754 | Rebuild Pine River-Straits 69kV dbl ckt line | Rebuild Pine River-Straits 69kV dbl ckt line with t2-477 ACSR | MI |  |  | Other | Not Shared | Reliability | 40804513 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 3126 | 2010-09-15 | PR03911 | Install a 2nd Chandler Transformer | Install a 2nd Chandler Transformer & reconfigure bus to 138 kV Ring bus | MI |  |  | Other | Not Shared | Reliability | 9700000 | 2012-12-09 | 2012-12-09 | Planned | 138 | 69 | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3157 | 2010-09-15 | F2386 | Line Y-95 Fount Valley-Fountain Valley Tap-Red Granite Tap-ACEC Spring Lake Tap-Silver Lake-Wautoma Uprate | Line Y-95 Fount Valley-Fountain Valley Tap-Red Granite Tap-ACEC Spring Lake Tap-Silver Lake-Wautoma Uprate | WI |  |  | Other | Not Shared | Reliability | 362468 | 2011-06-17 | 2011-06-17 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3160 | 2010-09-15 | F3180 | G706-H012 Line X-6 Portage-Hamilton-Staff-Friesland-North Randolph 138 kV Uprate | G706-H012 Line X-6 Portage-Hamilton-Staff-Friesland-North Randolph 138 kV Uprate | WI |  |  | GIP | Not Shared |  | 1447679 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3161 | 2010-09-15 | F3094 | G749 EcoMont Wind Farm | New EcoMont substation tapped into Belmont Tap-Rewey Tap 69 kV Line for G749 | WI |  |  | GIP | Not Shared |  | 4569183 | 2012-11-30 | 2012-11-30 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3188 | 2010-10-21 | F3056 | Pleasant Prairie-Zion 345-kV uprate | Replace 345kV Wave traps at the ComEd Zion SS and Jumpers | IL |  |  | Other | Not Shared | Economic | 1544571 | 2011-03-25 | 2011-03-25 | In Service | 345 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | G833-4_J022-3 Long Term Solution | 1) Construct a new Barnhart 345 & 138 kV substation 2) Install a new 345/138 kV transformer at Barnhart 3) Loop Edgewater-South Fond du Lac, Edgewater-Cedarsauk, Sheboygan Energy Center-Granville 345 kV lines into Barnhart 4) Loop the South Sheboygan Falls-Mullet River 138 kV line into Barnhart 138 kV 5) Construct a new 138 kV line from Barnhart to Plymouth #4 6) Construct a new 138 kV line from Plymouth #4 to Howards Grove 7) Construct a new 138 kV line from Howards Grove to Erdman 8) Convert the existing Forest Junction-Howards Grove-Plymouth #4 138 kV line and the northern portion of the existing Plymouth #4-Holland 138 kV line to 345 kV 9) Terminate the not-converted Holland 138 kV line at Barnhart 138 kV 10) Terminate the southern end of the converted 345 kV line at Barnhart 11) Construct a new Branch River 345 kV substation 12) Loop the converted 345 kV line into Branch River 345 kV substation 13) Loop the Point Beach-Forest Juction, Point Beach-Sheboygan Energy Center 345 kV lines into Branch River 14) Uprate Barnhart-Cedarsauk 345 kV line to 960 MVA for SN/SE | WI |  |  | GIP | Shared |  | 173309000 | 2018-06-01 | 2018-06-01 | Planned | 345 |  | B>A | Y
A in MTEP11 | West | ATC LLC | 3395 | 2010-10-20 | F2906 | Milwaukee Co T-D | Install a new Milwaukee Co T-D substation by looping in line 5042 (Bluemound-Everett 138kV) | WI |  |  | Other | Not Shared | Distribution | 33500000 | 2015-04-01 | 2015-04-01 | Planned | 138 | 13.2 | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3396 | 2010-09-15 | PR04184 | Uprate Blue River Tap-Muscoda 69 kV | Uprate Blue River Tap-Muscoda 69 kV line by increasing clearance at a distribution crossing to 564 Amps | WI |  |  | Other | Not Shared | Condition | 580000 | 2010-11-15 | 2010-11-15 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3427 | 2010-10-20 | PR04090 | Nordic-Perch Lk Uprate (AM) | Increase ground clearance for the Nordic-Perch Lk 138 kV line | MI |  |  | BaseRel | Not Shared |  | 1543040 | 2011-03-07 | 2011-03-07 | In Service | 138 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3428 | 2010-10-20 | PR04181 | Stage Coach-Timberlane 69kV uprate | Increase ground clearance for the Stage Coach-Timberlane 69kV line | WI |  |  | Other | Not Shared | Reliability | 35000 | 2011-04-08 | 2011-04-08 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3432 | 2010-10-08 | PR04259 | Uprate Stoughton-Oregon 69kV line | Uprate Stoughton-Oregon 69kV line | WI |  |  | Other | Not Shared | Reliability | 570000 | 2011-04-21 | 2011-04-21 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3433 | 2010-10-08 | PR04260 | Uprate Stagecoach-Mt Horeb NE-Mt Horeb 69 kV line Y-128 | Uprate Stagecoach-Mt Horeb NE-Mt Horeb 69 kV line Y-128 | WI |  |  | Other | Not Shared | Reliability | 36505 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3447 | 2010-12-02 | PR04350 | Ontonagon 138/69kV Tr uprate | Retap CT related to Ontonagon 138/69 kV Tr to obtain a higher rating | MI |  |  | Other | Not Shared | Reliability | 12410 | 2010-12-07 | 2010-12-07 | In Service | 138 | 69 | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3448 | 2010-12-02 | PR04350 | Ontonagon 138/69kV Tr Replacement | Replace the Ontonagon 138/69 kv Tr with a larger unit | MI |  |  | Other | Not Shared | Reliability | 935786 | 2011-12-01 | 2011-12-01 | Planned | 138 | 69 | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3449 | 2010-12-03 | PR04376 | Rebuild the Atlantic-M38 69kV line | Rebuild the Atlantic-M38 69kV line with a larger conductor | MI |  |  | Other | Not Shared | Reliability | 18878963 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3451 | 2010-12-06 | PR04338 | Y-136 Mt Horeb-Verona 69kV Rerate | Increase ground clearance on the Mt Horeb-Verona 69kV line | WI |  |  | Other | Not Shared | Reliability | 710000 | 2011-11-01 | 2011-11-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3452 | 2010-12-06 | PR04340 | Y-158 Bass Ck-Sheepskin 69kV Rerate | Increase ground clearance on the Bass Ck-Sheepskin 69kV line | WI |  |  | Other | Not Shared | Reliability | 920000 | 2011-11-01 | 2011-11-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3453 | 2010-12-06 | PR04374 | Y-25 Waupun-S Fond du Lac 69kV Rerate | Increase ground clearance on the Waupun-S Fond du Lac 69kV line | WI |  |  | Other | Not Shared | Reliability | 2186630 | 2012-02-28 | 2012-02-28 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3457 | 2011-01-04 | PR04372 | GIC J060 Garden City Wind Phase I | Interconnect GIC J060 Garden City Wind | MI |  |  | GIP | Not Shared |  | 4779758 | 2011-12-30 | 2011-12-30 | Planned | 138 | 0.69 | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3458 | 2011-01-04 | PRF2015a | Aurora 115-69kV T3 Replacement | Aurora 115-69kV T3 Replacement | WI |  |  | Other | Not Shared | Condition | 2958914 | 2011-06-03 | 2011-06-03 | In Service | 115 | 69 | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3459 | 2011-01-04 | PR04423 | A-157 Hume-Wildwood 115kV Uprate | Increase ground clearance on the Hume-Wildwood 115kV line | WI |  |  | BaseRel | Not Shared |  | 50000 | 2011-04-12 | 2011-04-12 | In Service | 115 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3460 | 2011-01-04 | PR04420 | Y-93 Berlin-Ripon 69kV Uprate | Increase ground clearance on the Berlin-Ripon 69kV line | WI |  |  | Other | Not Shared | Reliability | 1389745 | 2011-02-28 | 2011-02-28 | In Service | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3461 | 2011-01-05 | PR04411 | N-144 McMillan-Wildwood 115kV Uprate | Increase ground clearance on the McMillan-Wildwood 115kV line | WI |  |  | BaseRel | Not Shared |  | 50000 | 2011-02-28 | 2011-02-28 | In Service | 115 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3472 | 2011-02-01 | PR04325 | Pleasant Prairie Bus Reconfiguration | Construct a new 6-rung breaker-and-a-half 345 kV bus at the P4 site adjacent to the existing P4 yard. | WI |  |  | Other | Not Shared | Reliability | 39400000 | 2013-03-22 | 2013-03-22 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3479 | 2011-02-15 | PR04452 | Progress-Aviation 138 kV Uprate | Increase ground clearance for the Progress-Aviation line to 187 degrees F | WI |  |  | Other | Not Shared | Condition | 492563 | 2012-03-01 | 2012-03-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3480 | 2011-02-15 | PR04040 | Engadine Load Move | Construct a new radial 69-kV tap from the existing Indian Lake-Hiawatha 69-kV line 6913 to the Engadine Substation | WI |  |  | Other | Not Shared | Reliability | 810804 | 2012-10-01 | 2012-10-01 | Planned | 138 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3488 | 2011-03-22 | PR04502 | Uprate Brick Church to Walworth 69 kV line | Asset management project to uprate Y-159 from Brick Church to Walworth 69 kv Line | WI |  |  | Other | Not Shared | Condition | 532000 | 2012-03-01 | 2012-03-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3489 | 2011-03-22 | PR04503 | UprateY-34 Jennings Road to Darlington 69 kV line | Asset management project to uprate Y-34 from Jennings Road to Darlington 69 kv Line | WI |  |  | Other | Not Shared | Condition | 314000 | 2012-03-01 | 2012-03-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC | 3504 | 2011-03-28 | PR04529 | Y-80 Omro to Winneconne Rerate | Rerate Line Y-80 conductor from Omro sub to Winneconne sub to a rating of 580 amps | WI |  |  | Other | Not Shared | Condition | 205000 | 2012-12-01 | 2012-12-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ATC LLC, XEL, ITCM | 3127 | 2011-07-18 | 05 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - N LaCrosse-N Madison-Cardinal -Spring Green - Dubuque area 345-kV | N LaCrosse- N Madison - Cardinal 345-kV & Dubuque County - Spring Green - Cardinal 345 kV line. Spring Green and Briggs Road transformers | IA | WI/IA |  | MVP | Shared |  | 679260000.01 | 2018-12-31 | 2020-12-31 | Planned | 345 | 138 | B>A | Y
A in MTEP11 | West | DPC | 3397 | 2010-09-15 | DPC | Genoa to La Crosse Tap 161 Rebuild | Rebuild of the 161 kV line from Genoa to the La Crosse tap. | WI |  |  | BaseRel | Shared |  | 18000000 | 2014-06-01 | 2014-06-01 | Planned | 161 |  | C>B>A | Y
A in MTEP11 | West | DPC | 3434 | 2010-11-10 | DPC | Lufkin 161 kV substation | Build a new 161 kV substation on the Alma to Elk Mound 161 line in the Eau Claire area. | WI |  |  | Other | Not Shared | Reliability | 2164000 | 2012-09-01 | 2012-09-01 | Planned | 161 |  | C>B>A | Y
A in MTEP11 | West | GRE | 2571 | 2010-09-15 | 20222 | MN Pipeline-Menahga 8.0 mile line | MN Pipeline-Menahga 8.0 mile line. Built 115 kV but will be operated at 34.5. | MN |  |  | Other | Not Shared | Distribution | 4199990 | 2014-11-15 | 2014-11-15 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | GRE | 2599 | 2010-09-15 | 20338 | Shell Lake (IM) 5.0 mile, 115 kV line | Shell Lake (IM) 5.0 mile, 115 kV line | MN |  |  | Other | Not Shared | Distribution | 4201000 | 2014-10-31 | 2014-10-31 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | GRE | 2643 | 2010-09-15 | 20401 | Parkers Prairie 115 kV conversion | Parkers Prairie 115 kV conversion, New Distribution tap | MN |  |  | Other | Not Shared | Distribution | 1220998 | 2013-05-01 | 2013-05-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | GRE | 2679 | 2010-09-15 | 200331 | Ramsey-Grand Forks (81.02 mi.) 230 kV Rebuild | Ramsey-Grand Forks (81.02 mi.) 230 kV Rebuild | MN |  |  | Other | Not Shared | Condition | 40500000 | 2019-11-01 | 2019-11-01 | Planned | 230 |  | C>B>A | Y
A in MTEP11 | West | GRE | 3467 | 2011-01-11 | 200608 | MISO G604 | Connect Oak Glen Wind Farm to 69 kV system | MN |  |  | GIP | Not Shared |  | 1722464 | 2011-07-01 | 2011-07-01 | Under Construction | 69 |  | B>A | Y
A in MTEP11 | West | GRE | 3468 | 2011-01-11 | 200698 | MISO H062 | Connect H062 Wind Generation | MN |  |  | GIP | Not Shared |  | 1312741 | 2011-09-01 | 2011-09-01 | Under Construction | 69 |  | B>A | Y
A in MTEP11 | West | GRE | 3469 | 2011-01-11 | 200784 | MISO H061 | Connect H061 Wind generation | MN |  |  | GIP | Not Shared |  | 192530 | 2011-10-01 | 2011-10-01 | Planned | 69 |  | B>A | Y
A in MTEP11 | West | GRE/MP | 2634 | 2010-09-15 | 20388 | Savanna-Cromwell | Savanna-Cromwell | MN |  |  | BaseRel | Shared |  | 30000225 | 2012-11-02 | 2014-12-01 | Planned | 115 |  | B>A | Y
A in MTEP11 | West | ITCM | 3191 | 2010-06-28 | G164 | G164-Lakefield Jct 345 kV Breaker & Half | Convert the Lakefield 345kV ring bus to breaker and a half. | MN |  |  | GIP | Shared |  | 8148000 | 2011-04-29 | 2011-04-29 | In Service | 345 |  | B>A | Y
A in MTEP11 | West | ITCM | 3192 | 2010-06-28 | G604 | G604-Ellendale 69 kV Switch Station | Construct a new Ellendale 69kV four terminal breaker station. The Hayward-West Owatanna 69kV line will be rerouted into the Ellendale breaker station. Then change the N.O. point on the line to closed. | MN |  |  | GIP | Shared |  | 1913706 | 2010-08-15 | 2011-12-31 | In Service | 69 |  | B>A | Y
A in MTEP11 | West | ITCM | 3193 | 2010-06-28 | G741 | G741-Martin Co Waste Heat | Construct a new 69kV tap to the G741 customer. Tap the Trimont (IPL)-Sherburn(SCREC) 69kV line. | MN |  |  | GIP | Shared |  | 223884 | 2010-10-01 | 2010-10-01 | In Service | 69 |  | B>A | Y
A in MTEP11 | West | ITCM | 3194 | 2010-06-28 | G798 | G798-Story County Upgrades | Expand the ring bus at Story County. | IA |  |  | GIP | Shared |  | 422664 | 2010-07-31 | 2010-07-31 | In Service | 161 |  | B>A | Y
A in MTEP11 | West | ITCM | 3195 | 2010-06-28 | G870 | G870-Freeborn | Tap the Hayward-Winnebago Jct 161kV and construct a new Freeborn 161kV three terminal breaker station. Approximately 4 mile tap will connect Freeborn to the new G870 customer substation. | MN |  |  | GIP | Shared |  | 3516163 | 2010-10-01 | 2010-10-01 | In Service | 161 |  | B>A | Y
A in MTEP11 | West | ITCM | 3196 | 2010-06-28 | H007 | H007-Bond Breaker Station | Tap the Hayward-Winnebago Jct 161kV and construct a new Bond 69kV three terminal breaker station. | IA |  |  | GIP | Shared |  | 3560163 | 2011-07-01 | 2011-07-01 | In Service | 69 |  | B>A | Y
A in MTEP11 | West | ITCM | 3406 | 2010-09-15 | Adams-Roch | Adams-Rochester Terminal Upgrades | Upgrade the Adams terminal equipment to winter conductor limit | MN |  |  | Other | Not Shared | Reliability | 360000 | 2011-04-29 | 2011-04-29 | In Service | 161 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3407 | 2010-09-15 | Bluff | Bluff Substation Additions | Add 69kV breakers to the Bluff Substation 69kV and install associated relay equipment. | IA |  |  | Other | Not Shared | Distribution | 1920000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3408 | 2010-09-15 | BooneQuartz | BooneQuartz Sustation | This project performs the conversion of the Boone Quartz substation from 34.5kV to 69kV as part of the overall rebuild and conversion of the 34.5kV system. The Boone Quartz substation was constructed with a dual high side transformer and the high side was laid out for 69kV operation in preparation for the conversion. Two 69kV line breakers will be installed at the Boone Quartz substation. Existing 69kV lines and 34.5kV lines already constructed for 69kV operation will be re-configured along with installation of 69kV taps into the Boone Quartz substation to make the change to 69kV. No new load is being added during the conversion to 69kV. | IA |  |  | Other | Not Shared | Reliability | 1700000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3409 | 2010-09-15 | Bricelyn-Walters | Bricelyn-Walters Rebuild | The recommended project is to completely rebuild a 5 mile section of the Bricelyn - Walters 69 kV line with standard T2-477 construction and shield wire. | IA |  |  | Other | Not Shared | Condition | 2625000 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3410 | 2010-09-15 | Bridgeport TEQ | Bridgeport Terminal Upgrades | Upgrade the Bridgeport-Ottumwa 161kV terminal equipment | IA |  |  | BaseRel | Not Shared |  | 200000 | 2011-12-31 | 2011-12-31 | Planned | 161 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3411 | 2010-09-15 | Bridgeport T8 | Bridgeport T8 | Add a 69kV breaker to the Bridgeport North 69kV ring and install associated relay equipment. | IA |  |  | Other | Not Shared | Distribution | 360000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3412 | 2010-09-15 | FTMadison | Fort Madison Interconnection | Install tap capable of double circuit 69kV to Fort Madison substation and install associated relay equipment. | IA |  |  | Other | Not Shared | Distribution | 360000 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3413 | 2010-09-15 | Gladbrook | Gladbrook 161kV tap | Install a 161kV tap pole in the Marshalltown to Traer line with two line switches. Construct a 161kV tap line to the new Gladbrook substation. | IA |  |  | Other | Not Shared | Distribution | 300000 | 2013-12-31 | 2013-12-31 | Planned | 161 | 161 | C>B>A | Y
A in MTEP11 | West | ITCM | 3414 | 2010-09-15 | Magnolia Cap | Magnolia 7.1 MVAR 69kV Cap | ITCM will move the existing Lewisville 69kV 7.1 MVAR capacitor to the 69kV bus at Magnolia. Recent system changes have opened up a 69kV bay at Magnolia and this will be used for the capacitor bank and 69kV breaker. | IA |  |  | Other | Not Shared | Reliability | 480000 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3415 | 2010-09-15 | Marion TEQ | Marion Termianl Upgrades | Uprate 115 kV breaker 3710 terminal equipment at Marion. | IA |  |  | BaseRel | Not Shared |  | 10000 | 2011-12-31 | 2011-12-31 | In Service | 115 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3416 | 2010-09-15 | Marion 0410 | Marion Circuit 0410 Rebild to 69kV | This project rebuilds the sections (approximately 25 miles) of Marion circuit 0410 that will be utilized in the overall 34.5kV to 69kV conversion plan but have not yet been constructed for 69kV operation. | IA |  |  | Other | Not Shared | Distribution | 10500000 | 2012-12-31 | 2012-12-31 | Planned | 34 | 34 | C>B>A | Y
A in MTEP11 | West | ITCM | 3417 | 2010-09-15 | Marshalltown East Nevada | Marshalltown East Nevada | Construct a 1-2 span 34.5kV tap, install new relays for Marshalltown circuits 1810 and 2620, and upgrade terminal limit to address overload during contingency. Remove two normally open switches to limit system configuration to address system protection coordination issues which can occur when rural and city circuits are tied together. | IA |  |  | Other | Not Shared | Reliability | 280000 | 2011-12-31 | 2011-12-31 | In Service | 34 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3418 | 2010-09-15 | Mt Vernon 6420 | Mount Vernon Circuit 6420 Rebild to 69kV | This project rebuilds the sections (approximately 17 miles) of Mount Vernon circuit 6420 that will be utilized in the overall 34.5kV to 69kV conversion plan but have not yet been constructed for 69kV operation. | IA |  |  | Other | Not Shared | Distribution | 7150000 | 2013-12-31 | 2013-12-31 | Planned | 34 | 34 | C>B>A | Y
A in MTEP11 | West | ITCM | 3419 | 2010-09-15 | Bertram Sewage | Bertram161kV tap | The new transformer high side voltage is 69/34.5kv; it will need a 0.5 mile tap line built to the substation from the existing 34.5kV system with the future plans of 69kV rebuild. Adding the double-circuit tap to the substation will allow connection to the new transformers. The double circuit tap will provide additional reliability, with switching, to have the ability to separate the parallel transformers in the situation a transformer fails, no load will be lost. | IA |  |  | Other | Not Shared | Distribution | 270000 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3420 | 2010-09-15 | OGS BKR | OGS Breaker | Install new 345kV breaker in the Ottumwa Generating Station substation to replace the failed 345kV circuit switcher. Replace the transformer lockout/breaker control panel. Replace the existing 345kV relay panel with two new panels and one lockout panel, which will allow for the retirement of an existing transfer trip scheme. The new line panels will implement a new redundant transfer trip scheme. Install second set of battery back up. | IA |  |  | Other | Not Shared | Condition | 1350000 | 2011-12-31 | 2011-12-31 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3421 | 2010-09-15 | S Centervlle Cap | Centervile 7.1 MVAR 69kV Cap | nstall a 7 MVAR 69 kV capacitor, breaker with synchronous closing control, switch, and 0.5 mH reactor. 69 kV breakers 0-6961-1 and 0-6921-2 will be replaced due to condition. A 69 kV bus tie breaker and switch will be added for reliability between transformers 2 and 3. | IA |  |  | Other | Not Shared | Reliability | 1350000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3422 | 2010-09-15 | S Brdwy TEQ | South Broadway TEQ | Install Sub | IA |  |  | Other | Not Shared | Distribution | 150000 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3423 | 2010-09-15 | Truro | Truro Line Rebuild | Rebuild the line between the Truro substation and the White Oak tap and operate the line at 69 kV. | IA |  |  | Other | Not Shared | Reliability | 3360000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3425 | 2010-09-15 | VMEU | VMEU Interconnect | Install line switches at the interconnection point. | IA |  |  | Other | Not Shared | Reliability | 110000 | 2011-12-31 | 2011-12-31 | In Service | 34 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3426 | 2010-09-15 | DPC/ITC Osage | DPC/ITC Interconnect move | The recommended project is to move the existing interconnection point approximately 0.6 miles south. ITC will install a laminate structure and associated equipment to accommodate DPC’s project. | IA |  |  | Other | Not Shared | Distribution | 0 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | ITCM | 3499 | 2011-03-28 |  | NERC Alert Facility Ratings for 2011 | Verify and remediate facilities as required due to the industry-wide NERC alert | IA |  |  | BaseRel | Not Shared |  |  | 2011-12-31 | 2011-12-31 | Planned |  |  | C>B>A | Y
A in MTEP11 | West | MDU | 3199 | 2010-07-12 | G359 | G359, 38073-01 | 230 kV line from project interconnection to Ellendale Jct substation and new 230/115 kV transformer at Ellendale | ND |  |  | GIP | Not Shared |  | 19130000 | 2011-03-21 | 2011-12-01 | Planned | 230 | 115 | B>A | Y
A in MTEP11 | West | MEC | 3268 | 2011-02-15 | G1393 | Lehigh: 345 kV 50 MVAr Reactor | Add a 345 kV, 50 MVAr reactor | IA |  |  | BaseRel | Not Shared |  | 2750000 | 2012-11-01 | 2012-11-01 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | West | MEC | 3270 | 2011-02-15 | G1375 | CBEC-River Bend 161 kV Rebuild | Increase 161 kV line rating. | IA |  |  | Other | Not Shared | Reliability | 675000 | 2011-06-01 | 2011-06-01 | Planned | 161 |  | C>B>A | Y
A in MTEP11 | West | MEC | 3271 | 2011-02-15 | G1377 | River Bend-Bunge 161 kV Rebuild | Increase 161 kV line rating. | IA |  |  | Other | Not Shared | Reliability | 700000 | 2011-06-01 | 2011-06-01 | Planned | 161 |  | C>B>A | Y
A in MTEP11 | West | MEC | 3272 | 2010-09-07 | 02321 | Raun 345 kV Breaker Replacement | Replace existing SFA 345 kV breaker 0170 with a new unit. | IA |  |  | Other | Not Shared | Condition | 500000 | 2011-06-01 | 2011-06-01 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | West | MEC, ITCM | 3205 | 2011-07-18 | 03 Cand. MVP Port.1 | Proposed MVP Portfolio 1: Lakefield Jct. - Winnebago - Winco - Burt area & Sheldon - Burt Area - Webster 345 kV line | New 345 kV line from Lakefield Junction to Burt via Winnebago and Winco and a new 345 kV line from Sheldon to Webster via Burt. Includes 161 kV rebuild as underbuild along portions of the route. | IA | MN/IA |  | MVP | Shared |  | 514069787 | 2015-12-31 | 2016-12-01 | Planned | 345 | 161 | B>A | Y
A in MTEP11 | West | MEC, ITCM | 3213 | 2011-07-18 | 04 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Winco to Hazelton 345 kV line | Winco to Lime Creek to Floyd to Blackhawk to Hazelton 345 kV line and Lime Creek, Floyd and Black Hawk transformers | IA |  |  | MVP | Shared |  | 591551532 | 2015-12-01 | 2015-12-31 | Planned | 345 | 161 | B>A | Y
A in MTEP11 | West | MP | 2549 | 2010-12-18 | 15L | 15L Upgrade | Thermal Upgrade of MP Line #15 | MN |  |  | Other | Not Shared | Reliability | 3179000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | MP | 3373 | 2010-11-01 | MP | 9 Line | Thermal Upgrade | MN |  |  | BaseRel | Shared |  | 8000000 | 2012-12-30 | 2012-12-30 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | MP | 3374 | 2010-09-15 | MP | Greenway | Re-energize existing 115/23 kV substation | MN |  |  | Other | Not Shared | Distribution | 700000 | 2012-11-01 | 2012-11-01 | Planned | 115 | 23 | C>B>A | Y
A in MTEP11 | West | OTP | 2856 | 2011-07-01 | OTP1 | Victor-New Effington 41.6 kV Line Upgrade | Rebuild Existing 4-Mile 41.6 kV Line | SD |  |  | Other | Not Shared | Reliability | 200000 | 2011-06-30 | 2011-06-30 | In Service | 41.6 |  | C>B>A | Y
A in MTEP11 | West | OTP | 3466 | 2011-01-11 | OTP1 | Project J-035 5 MW Wind Farm on OTP Doran 41.6 kV line. | Add 3 Way Switch on 41.6 kV line between Doran 41.6 kV substation to Doran Jct. | MN |  |  | GIP | Not Shared |  | 140000 | 2012-08-01 | 2012-08-01 | Planned | 41.6 |  | B>A | Y
A in MTEP11 | West | OTP | 3481 | 2011-02-24 | OTP | Buffalo - Casselton 115 kV Line | Construct 16 mile 115 kV line from Buffalo - Casselton (ND); Replace Buffalo 345/115 kV Transformer; Rebuild portion of Sheyenne - Mapleton 115 kV Line | ND |  |  | BaseRel | Shared |  | 14000000 | 2013-07-01 | 2014-12-31 | Planned | 345 | 115 | C>B>A | Y
A in MTEP11 | West | OTP, MDU | 2220 | 2011-07-18 | 06 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Ellendale to Big Stone South | Big Stone to Ellendale 345 kV double circuit line | ND | SD/ND |  | MVP | Shared |  | 326164000 | 2019-12-31 | 2019-12-31 | Planned | 345 | 230 | B>A | Y
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 Cand. MVP Port.1 (46) | Proposed MVP Portfolio 1 - Big Stone South to Brookings | Brookings to Big Stone 345 kV double circuit | SD |  |  | MVP | Shared |  | 226720000 | 2017-12-31 | 2017-12-31 | Planned | 345 | 230 | B>A | Y
A in MTEP11 | West | XEL | 3309 | 2010-09-15 | Buffalo Ridge Sub Equipment | Buffalo Ridge Substation Equipment Upgrade | Upgrade the wave traps and line switches at Buffalo Ridge to 2000 A going to Lake Yankton and Pipestone. Retap the Pipestone CTs to 2000 A going to Buffalo Ridge. | MN |  |  | BaseRel | Not Shared |  | 286000 | 2011-08-01 | 2011-08-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway212 | Highway 212 Corridor upgrade | This project is to complete the conversion of 69 kV line between Scott County and West Waconia substation to 115 kV. The scope also involves building new West Creek distribution substation and converting the Chaska, Victoria and Augusta substations to 115 kV. | MN |  |  | Other | Not Shared | Distribution | 19450000 | 2012-06-01 | 2012-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3312 | 2010-09-15 | MN Valley - Maynard - Kerkhoven tap upgrade | Minn Valley - Maynard - Kerkhoven tap upgrade | This project is to upgrade the Minn Valley - Maynard - Kerkhoven tap 115 kV line to 795 ACSS conductor | MN |  |  | BaseRel | Shared |  | 13660000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3313 | 2010-09-15 | New Prague switch | New Prague switch | This project is to install a 69 kV 1 way switch to provide SMMPA's New Prague substation a new interconnection point. The existing interconnection would require cutting the line jumpers phisically when the New Prague - Veslie line is out of service. | MN |  |  | Other | Not Shared | Reliability | 180000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3314 | 2010-09-15 | Kohlman Lake - Long Lake 2nd circuit | Kohlman Lake - Long Lake 2nd circuit | This project is to convert the Kohlman Lake - Long Lake 115 kV bifurcated line to double circuit with separate line terminations at Kohlman Lake and Long Lake | MN |  |  | BaseRel | Not Shared |  | 3000000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3315 | 2010-09-15 | ChisagoCo 2nd TR | Chisago County 2nd 345/115 kV transformer | This project is to install a 2nd 345/115 kV transformer at Chisago County | MN |  |  | BaseRel | Not Shared |  | 7000000 | 2014-06-01 | 2014-06-01 | Planned | 345 | 115 | C>B>A | Y
A in MTEP11 | West | XEL | 3316 | 2010-09-15 | Riverside - Apache upgrade | Riverside - Apache lie upgrade | This project is to upgrade Riverside - Apache line to 360 MVA and upgrade Apache switch to 2000A | MN |  |  | BaseRel | Not Shared |  | 3000000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3317 | 2010-09-15 | Goose Lake - Kohlman Lake 2nd circuit | Goose Lake - Kohlman Lake 2nd circuit | This project is to convert the single circuit line between Goose Lake and Kohlman Lake to double circuit. | MN |  |  | BaseRel | Shared |  | 6000000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3318 | 2010-09-15 | Parkers Lake Overstressed Breakers | Parkers Lake Overstressed Breakers | This project replaces some of the 115 kV breakers at Parkers Lake with 63 kA rated breakers | MN |  |  | BaseRel | Not Shared |  | 1900000 | 2011-10-01 | 2011-10-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3319 | 2010-09-15 | Split Rock Overstressed Breakers | Split Rock Overstressed Breakers | This project replaces some of the 115 kV breakers at Split Rock with 63 kA rated breakers | SD |  |  | BaseRel | Not Shared |  | 1344000 | 2011-12-01 | 2011-12-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3320 | 2010-09-15 | Split Rock Reactor | Split Rock Reactor Replacement | This project is needed to replace the failed 50 MVAR reactor and associated breaker. | SD |  |  | BaseRel | Not Shared |  | 100000 | 2011-12-01 | 2011-12-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3321 | 2010-09-15 | Chemolite Breaker Addition | Chemolite Breaker Addition | This project adds two breakers at Chemolite to insure only one line at a time will be removed from service during a breaker failure. | MN |  |  | BaseRel | Not Shared |  | 580000 | 2011-01-14 | 2011-01-14 | In Service | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3322 | 2010-09-15 | Cedar Falls - Clear Lake Rebuild | Cedar Falls - Clear Lake Rebuild | Rebuild 43 Miles of 69 kV line to 477 ACSR | WI |  |  | Other | Not Shared | Reliability | 14000000 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3323 | 2010-09-15 | Park Falls Bio-Refinery | Park Falls Bio-Refinery | Build radial 115 kV line from Park Falls sub to a new customer and install a new distribution sub for the customer | WI |  |  | Other | Not shared | Distribution | 23769000 | 2012-12-01 | 2013-06-01 | Planned | 115 | 13.8 | C>B>A | Y
A in MTEP11 | West | XEL | 3324 | 2010-09-15 | Eau Claire Overstressed Breakers | Eau Claire Overstressed Breakers | Replace overstressed Eau Claire 69 kV breakers. 4E185, 4E186, 4E187, 4E188, 4E189, 4E190, 4E191, 4E192, 4E193, 4E195. | WI |  |  | Other | Not Shared | Reliability | 1683000 | 2011-12-01 | 2011-12-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3325 | 2010-09-15 | Orono 115 kV conversion | Orono 115 kV conversion | This project will move the supply for Orono from its current 69 kV supply to the 115 kV line from Medina to Crow River | MN |  |  | Other | Not Shared | Reliability | 5340000 | 2012-12-01 | 2012-12-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3326 | 2010-09-15 | Black Dog Outlet | Black Dog Outlet | This line will rebuild the 115 kV line from Black Dog to Savage to 795 ACSS conductor. | MN |  |  | BaseRel | Not Shared |  | 4564000 | 2012-06-01 | 2012-06-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3327 | 2010-09-15 | Eau Claire - Madison Street Rebuild | Eau Claire - Madison Street Rebuild | This project will replace 1 mile of 4/0 Cu conductor with 795 ACSS on the 69 kV line between Eau Claire - Sterling - Madison St. | WI |  |  | Other | Not Shared | Reliability | 1600000 | 2011-12-01 | 2011-12-01 | Planned | 69 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3473 | 2011-01-28 | Sioux Falls 115 kV Phase 1 | Sioux Falls 115 kV Phase 1 | This project re-constructs 10 miles of existing 69 kV line in Sioux Falls, SD to 115 kV; 6 miles of the new line will be double circuit with existing 69 kV. | SD |  |  | Other | Not Shared | Reliability | 35000000 | 2014-06-01 | 2014-06-01 | Planned | 115 | 13.8 | C>B>A | Y
A in MTEP11 | West | XEL | 3474 | 2011-01-28 | Adams 345 kV Reactor Installation | Adams 345 kV Reactor Installation | Installing a 50 MVAR reactor at Adams substation on the Pleasant Valley line, along with a breaker and disconect switch | MN |  |  | Other | Not Shared | Reliability | 2260000 | 2012-06-01 | 2012-06-01 | Planned | 345 |  | C>B>A | Y
A in MTEP11 | West | XEL | 3475 | 2011-01-28 | Prairie 3rd transformer | Prairie 3rd transformer | This project is to install a 3rd 230/115 kV transformer at Prairie substation | ND |  |  | BaseRel | Not Shared |  | 12000000 | 2014-06-01 | 2014-06-01 | Planned | 230 | 115 | C>B>A | Y
A in MTEP11 | West | XEL | 3476 | 2011-02-14 | Maple River - Cass County 345 kV line | Maple River - Cass County 345 kV line | This project is to build a new 4.5 mile 345 kV line from Maple River to Cass County substation along with the 345/115 kV transformer at Cass County substation. | ND |  |  | BaseRel | Not Shared |  | 13226000 | 2014-06-01 | 2014-06-01 | Planned | 345 | 115 | C>B>A | Y
A in MTEP11 | West | XEL | 3509 | 2011-05-10 | Stinson to Bayfront Rebuild | Stinson to Bayfront 115 kV line rebuild | Rebuild approximately 33 miles of 115 kV line from 336 ACSR to 795 ACSR | WI |  |  | Other | Not Shared | Condition | 15400000 | 2013-01-01 | 2013-01-01 | Planned | 115 |  | C>B>A | Y
A in MTEP11 | West | XEL, GRE | 1203 | 2011-07-18 | 02 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Brookings, SD - SE Twin Cities 345 kV | Brookings Cty-Lyon Cty (Single Ckt 345 kV); Lyon Cty-Cedar Mountain-Helena (Double Ckt 345 kV); Helena-Lake Marion-Hampton Corner (Single Ckt 345 kV); Lyon Cty-Hazel (Single Ckt 345 kV); Hazel-Minnesota Valley (Single Ckt 345 kV, initially operate at 230 kV); Cedar Mountain-Franklin (Single Ckt 115 kV) | MN | SD/MN |  | MVP | Shared |  | 738400000 | 2011-06-01 | 2015-02-16 | Planned | 345 | 69 | B>A | Y
A in MTEP11 | West | XEL, GRE | 3454 | 2010-12-06 | Hollydale 115 kV upgrade | Hollydale 115 kV upgrade | This project will upgrade the 69 kV line from GRE's Medina to Plymouth substations. A new switching station will be added on GRE's 115 kV line between Parkers Lake and Elm Creek north or south of the Plymouth Substation depending on the permitted location. Joint project with GRE P3394 at Medina | MN |  |  | Other | Not Shared | Reliability | 24676164 | 2013-05-01 | 2013-06-01 | Planned | 115 | 13.8 | C>B>A | Y
A in MTEP10 | Central | AmerenIL | 1528 | 2008-02-14 |  | Rising Substation - Increase Xfmr Rating | Increase rating of existing 345/138 kV 450 MVA Transformer | IL |  | 2010-12-02 |  |  |  | 5000000 | 2012-06-01 | 2012-06-01 | Proposed | 345 | 138 | A | Y
A in MTEP10 | Central | AmerenIL | 1535 | 2010-06-04 |  | Wood River-Stallings | Replace terminal equipment at Stallings, reconductor 6 miles of 138 kV Line 1456 and upgrade Stallings bus conductor to a minimum capability of 1200 A | IL |  | 2010-12-02 | BaseRel | Not Shared |  | 2036000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenIL | 2064 | 2010-06-04 |  | South Bloomington - Old Danvers 138 kV line - Reconductor | S Bloomington-Old Danvers 138 kV Line 1364 Reconductor 3.33 miles from S. Bloomington to West Washington (S Bloomington to Diamond Star Tap) | IL |  | 2010-12-02 | BaseRel | Not Shared |  | 2113000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenIL | 2288 | 2010-06-04 |  | Washington Street Substation 'In-Out' | Re-Route S. Bloomington to Danvers Line 1364 through the West Washington St. Substation with an “in-and-out” arrangement Replace existing tap to 138 kV Line 1326 with 'in and out' arrangement. | IL |  | 2010-12-02 | Other | Not Shared | Reliability | 4155000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenIL | 2957 | 2010-06-04 |  | Edwards-Tazewell 138 kV Line 1373 | Edwards-Tazewell 138 kV Line 1373 - Reconductor 1.57 miles of 795 kcmil ACSR conductor and 7.5 miles of 927 kcmil ACAR conductor with conductor capable of carrying 1600 A under summer emergency conditions. Replace a 1200 A wavetrap and CT's at the Edwar | IL |  | 2010-12-02 | BaseRel | Not Shared |  | 121000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenIL | 2986 | 2010-05-08 | AMRN7 | North Alton Substation Supply | North Alton 138-34.5 kV Substation Supply - Supply new 138-34.5 kV Substation from an in-out by tapping the existing Wood River to Stallings 138 kV line (“in and out”). Build approximately 4 miles of double-circuit 138 kV line to the new North Alton Substation connection to the Wood River-Stallings-1456 138 kV line. Approximately 4 miles of double-circuit 138 kV line needed. | IL |  | 2010-12-02 | Other | Not Shared | Distribution | 12891000 | 2014-06-01 | 2015-12-01 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenIL | 2992 | 2010-05-08 |  | Bondville-S.W. Campus | Bondville-S.W. Campus 138 kV - Construct 8 miles of new 138 kV line. Construct 138 kV Ring Bus at Bondville (2 new PCB's) and a 138 kV Ring Bus at Champaign S.W. Campus (4 new PCB's). | IL |  | 2010-12-02 | Other | Not Shared | Distribution | 10000000 | 2014-06-01 | 2014-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | Central | AmerenIL | 2273 | 2010-04-05 |  | Supply to LaFarge Customer Substation | Provide 161 kV supply to customer substation | IL |  | 2009-12-04 | Other | Not Shared | Distribution | 570000 | 2013-06-01 | 2013-06-01 | Planned | 161 |  | A | Y
A in MTEP09 | Central | AmerenIL | 2279 | 2010-04-05 |  | 'Grand Tower-Steeleville 138 kV Reconductor | Reconductor 6.19 miles of 477 kcmil ACSR to carry 1200 A under summer emergency conditions | IL |  | 2009-12-04 | BaseRel | Not Shared |  | 1866000 | 2011-10-05 | 2011-10-05 | Planned | 138 |  | A | Y
A in MTEP09 | Central | AmerenIL | 2472 | 2010-04-05 | AMRN3 | New 345kV Supply at Fargo Substation | Tap existing 345kV line from Duck Creek to Tazewell and create new Maple Ridge Substation ($6.5M) Build a new supply line to the Fargo Substation by extending 20 miles of 345kV from the new Maple Ridge Substation ($50.1M) Create Fargo Station and install 560 MVA 345/138kV Transformer ($9.4M) | IL |  | 2009-12-04 | BaseRel | Shared |  | 78168000 | 2016-12-01 | 2016-12-01 | Planned | 345 | 138 | A | Y
A in MTEP08 | Central | AmerenIL | 1529 | 2010-04-05 |  | Brokaw-State Farm Line 1596 - Reconductor | Reconductor 3.3 miles of 138 kV line to 2000 A Summer Emergency capability | IL |  | 2008-12-04 | BaseRel | Not Shared |  | 2566900 | 2011-12-22 | 2011-12-22 | Planned | 138 |  | A | Y
A in MTEP08 | Central | AmerenIL | 2060 | 2010-06-28 |  | East Peoria - Flint : Increase Clerances to ground | Reconductor 4.54 miles of 477 kcmil ACSR with condcutor capable of carrying 1200 A under summer emergency conditions | IL |  | 2008-12-04 | BaseRel | Not Shared |  | 2113000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP08 | Central | AmerenIL | 2068 | 2010-04-05 |  | Latham - Oreana 345 kV line | Convert Oreana 345 kV Bus to 6-Position Ring Bus with 3000 A Capability; Construct 8.5 miles of 345 kV line (2-954 kcmil ACSR conductor or equivalent capability) from Oreana Substation to 345 kV Line 4571 tap to Latham Substation. 3-345 kV PCB's at Oreana Substation. | IL |  | 2008-12-04 | BaseRel | Shared |  | 35077000 | 2014-12-01 | 2014-12-01 | Planned | 345 |  | A | Y
A in MTEP08 | Central | AmerenIL | 2069 | 2010-04-05 |  | South Bloomington - Install new 560 MVA 345 /138 Xfmr | South Bloomington Area 345/138 kV Substation - Install 345/138 kV, 560 MVA Transformer. Extend new 345 kV line approximately 5 miles from Brokaw Substation to South Bloomington Substation. Install 1-138 kV PCB at South Bloomington Substation, and 2-345 kV PCB's at Brokaw Substation | IL |  | 2008-12-04 | BaseRel | Shared |  | 20029000 | 2014-12-01 | 2014-12-01 | Planned | 345 | 138 | A | Y
A in MTEP06 | Central | AmerenIL | 739 | 2006-03-17 |  | Franklin County Power Plant Connection | Franklin County Power Plant Connection - Tap 345 kV Line 4561 Tap, and Install new 345 kV ring bus | IL |  | 2007-02-15 | Other | Not Shared (Pre-RECB 1) |  | 6410900 | 2012-11-01 | 2012-11-01 | Planned | 345 |  | A | Y
A in MTEP05 | Central | AmerenIL | 725 | 2010-06-28 | 725 | LaSalle Area Development | N. LaSalle-Wedron Fox River 138 kV - 24 miles new line, 2-138 kV breakers at N. LaSalle, 1 138 kV Breaker at Wedron Fox River | IL |  | 2005-06-16 | Other | Excluded |  | 21357530 | 2012-04-26 | 2012-04-26 | Planned | 138 |  | A | Y
A in MTEP05 | Central | AmerenIL | 726 | 2010-06-28 | 725 | LaSalle Area Development | Ottawa-Wedron Fox River 138 kV - Construct 9 miles new 138 kV line, 1 new 138 kV breaker at Ottawa | IL |  | 2005-06-16 | Other | Excluded |  | 8962967 | 2013-07-30 | 2013-07-30 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenMO | 2972 | 2010-05-08 |  | Sandy Creek-Joachim Reconductoring | Sandy Creek-Joachim-1 138 kV Line - Reconductor 6.2 miles of 795 kcmil ACSR with conductor having 1600 A summer emergency capability between Sandy Creek and Bailey Substations | MO |  | 2010-12-02 | BaseRel | Not Shared |  | 3305700 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenMO | 2976 | 2010-05-08 | AMRN6 | Central Substation Relocation | Central 138-34.5 kV Substation - Move Central 138-34 kV Substation approximately one-half mile and reterminate existing 138 kV supply lines (Cahokia-Central-1&2 and Central-Watson-1) | MO |  | 2010-12-02 | Other | Not Shared | Relocation | 4632900 | 2012-12-01 | 2012-12-01 | Planned | 138 |  | A | Y
A in MTEP10 | Central | AmerenMO | 3107 | 2010-01-05 | AMRN19 | Arnold Substatsion : Install 4-138 kV Breakers | Install 4-138 kV Breakers at Arnold Substation. Install 138 kV breaker on the Arnold-Meramec-3 line position. Establish 138 kV Bus #3, install 138 kV Bus 2-3 tie breaker, and rearrange the existing Tyson-Meramec-4 line connection to an in-out arrangement | MO |  | 2010-12-02 | BaseRel | Not Shared |  | 2283200 | 2011-06-17 | 2011-06-17 | Planned | 138 |  | A | Y
A in MTEP09 | Central | AmerenMO | 1240 | 2008-12-10 |  | Reconductor Sioux-Huster-1 and -3 138 kV | Reconductor 9.1 miles of 138kV line on Sioux-Huster 1 and 3 lines | MO |  | 2009-12-04 | BaseRel | Shared |  | 11100000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP08 | Central | AmerenMO | 1235 | 2010-04-05 |  | Fredericktown-AECI Fredericktown | Increase ground clearance on 12 miles | MO |  | 2008-12-04 | Other | Not Shared |  | 1200000 | 2016-06-01 | 2016-06-01 | Planned | 161 |  | A | Y
A in MTEP08 | Central | AmerenMO | 1238 | 2006-03-17 |  | GM-Point Prairie 161 kV to AECI Enon Sub. | Extend 1 mile of 161 kV to AECI Enon Substation | MO |  | 2008-12-04 | BaseRel | Not Shared |  | 1896500 | 2011-11-17 | 2011-11-17 | Planned | 161 |  | A | Y
A in MTEP07 | Central | AmerenMO | 152 | 2010-04-05 | 130 | Big River-Rockwood 138 kV | Big River-Rockwood 138 kV - Construct new line | MO |  | 2007-12-13 | BaseRel | Shared |  | 13381100 | 2011-11-30 | 2011-11-30 | Planned | 138 |  | A | Y
A in MTEP10 | Central | DEM | 1520 | 2009-09-17 | 502G6713 | Durbin 230/69 | Construct a new Durbin 230/69kv 150mva substation with 2 69kv line terminals. | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 7000000 | 2017-06-01 | 2017-06-01 | Planned | 230 | 69 | A | Y
A in MTEP10 | Central | DEM | 1903 | 2009-09-17 | 504G6710 | Fishers N. to Fishers 69kV reconductor | Reconductor 1.05 miles 69kV line from Fishers No to Fishers with 954ACSR@100C conductor | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 455228.77 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2050 | 2009-09-17 | 802J3041 | Dresser 345/138kV Bank 3 addition | Add a 3rd 345/138kV transformer at Dresser Sub | IN |  | 2010-12-02 | BaseRel | Shared |  | 2980000 | 2011-12-31 | 2011-12-31 | Under Construction | 345 | 138 | A | Y
A in MTEP10 | Central | DEM | 2123 | 2009-09-17 | AMIN0071 | Bloomington to Martinsville 69kV Rebuild | Bloomington to Martinsville 69kV - 6903 ckt. - Rebuild 9.2 miles of 336ACSR with 954ACSR@100C | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 2020000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2134 | 2009-09-17 | 804J3052 | Bloomington 230 to Needmore Jct 69kV reconductor | Bloomington 230kV Sub to Needmore Jct (Pole #825-3379) reconductor 6949 line with 954ACSR 100C conductor and replace (2) Needmore Jct. 69kV - 600 amp switches with 1200 amp switches. | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 2712500 | 2013-06-30 | 2013-06-30 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2136 | 2009-09-17 | 604J3051 | Greenwood HE Honey Creek Jct to Frances Creek Jct 69kV uprate | Greenwood HE Honey Creek Jct to Frances Creek Jct uprate 69kV - 69102 line 1.12 mile for 100C | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 63533 | 2012-06-30 | 2012-06-30 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2137 | 2009-09-17 | 604J3056 | Greenwood Averitt Rd Jct to HE Honey Creek Jct 69 kV Uprate | Greenwood Averitt Rd Jct to HE Honey Creek Jct 69 kV - 69102 Uprate 1.05 mile line section of 477acsr for 100C conductor temperature operation | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 53461 | 2012-06-30 | 2012-06-30 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2143 | 2009-09-17 | 602J3066 | Frances Creek 345/69kV Bank 2 | Add Frances Creek 345/69kV Bank 2 - 200MVA with LTC | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 6887000 | 2014-06-01 | 2014-06-01 | Planned | 345 | 69 | A | NT
A in MTEP10 | Central | DEM | 2858 | 2009-09-14 | 504G6697 | Geist to Fortville 69kv - 69130 ckt. Reconductor | Reconductor 69kV 3.62 mile line from Geist sub to Fortville sub with 954ACSR conductor. | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 1820000 | 2017-06-01 | 2017-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2859 | 2009-09-17 | AMIN0123 | Peru Muni J to Wabash J 69kV - 6986 ckt. Reconductor | Peru Muni J to Wabash J 6986 Reconductor approx., 10.3 miles of 4/0 ACSR with 477 ACSR | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 3810000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2860 | 2009-09-14 | AMIN0130 | Brazil East to Reelsville J 69kV - 6938 ckt. Reconductor | Reconductor 6938 line from Brazil East to Reelsville Jct. with 477ACSR 100C conductor. Replace Reelsville Jct switches with 1200 amp switches. | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 2550000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2861 | 2009-09-14 | AMIN0129 | Greencastle Madison J to Greencastle East J 69kV - 6996 ckt. Reconductor | Reconductor 6996 line from Greencastle Madison Jct to Greencastle East Jct. with 954ACSR 100C conductor. Replace or upgrade 600 amp Greencastle East Jct switches to 1200amp. | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 1482000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2863 | 2009-09-17 | 504H6972 | Carmel SE to new Jct in 69145 ckt - new 69kV line | Build new 69kV-954ACSR circuit from Carmel SE to new Jct in the 69145 line, completing a loop from Carmel 146th St to Geist. | IN |  | 2010-12-02 | Other | Not Shared | Distribution | 4274200 | 2012-06-02 | 2012-06-02 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2865 | 2009-09-14 | 604G6620 | Frankfort Burlington to Middlefork 69kV - 69133 ckt Uprate | Frankfort Brlngtn St to Midfrk - 69133 ckt - uprate 11.5 miles of 4/0ACSR to 100C and reconductor 1.0 mile of 2/0CUB7 to 954ACSR@100C | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 582035 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP10 | Central | DEM | 2869 | 2009-09-14 | 902G1843 | Zimmer 345kV Gas Insulated Sub. Repl. | Replace 345kV gas insulated sub with an air insulated sub | OH |  | 2010-12-02 | Other | Not Shared | Condition | 4032000 | 2012-06-01 | 2012-06-01 | Under Construction | 345 |  | A | Y
A in MTEP10 | Central | DEM | 2871 | 2009-09-17 | AMKY0125 | EKPC Hebron - 138kV ring bus | Add new EKPC Hebron 138/69kV transformer (outside DEM area 208). Includes 3 position – 138kV CB ring bus and associated Duke owned facilities (inside DEM area 208). 138kv Tie from DEM to EKPC is being revised slightly. 100% to be paid for by EKPC. | KY |  | 2010-12-02 | Other | Not Shared | Reliability | 3345000 | 2011-12-31 | 2011-12-31 | Planned | 138 | 69 | A | Y
A in MTEP10 | Central | DEM | 2872 | 2010-06-25 | AMIN0354 | Manhattan Dist Sub 138kV tap switches | Install 1200A - 138kv line switching on both sides of proposed tap line to new joint use DEM/WVPA Manhattan distribution sub. | IN |  | 2010-12-02 | Other | Not Shared | Distribution | 525723 | 2011-12-31 | 2011-12-31 | Planned | 138 | 12 | A | Y
A in MTEP10 | Central | DEM | 2874 | 2009-09-14 | AMIN0233 | Noblesville to Geist 230kV - 23007 line relocate | Relocate section of 23007 between Noblseville and Giest to new RoW around expanding mine operation - approx. 0.6 mile of added line length | IN |  | 2010-12-02 | Other | Not Shared | Relocation | 1766218 | 2011-12-01 | 2011-12-01 | Planned | 230 |  | A | Y
A in MTEP10 | Central | DEM | 2875 | 2010-06-25 | AMIN0230 | Edwardsville 138kV switches and tap line | Construct new Edwardsville 138/12kV distribution substation - single 22.4 MVA transformer | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 467387 | 2011-12-31 | 2011-12-31 | Planned | 138 | 12 | A | NT
A in MTEP10 | Central | DEM | 2876 | 2009-09-14 | AMOH0192 | Redbank 345kV Gas Insulated Bus. Repl. | Replace 345kV gas insulated bus with an air insulated bus | OH |  | 2010-12-02 | Other | Not Shared | Condition | 3467832 | 2013-06-01 | 2013-06-01 | Planned | 345 |  | A | Y
A in MTEP10 | Central | DEM | 2877 | 2009-09-14 | AMOH0194 | West End 138kV relocation for B.S. Bridge | Modifications to West End Substation facilities, 138 kV transmission lines and distribution lines to accommodate Brent Spence Bridge project | OH |  | 2010-12-02 | Other | Not Shared | Relocation | 13780000 | 2015-12-31 | 2015-12-31 | Planned | 138 | 13.2 | A | Y
A in MTEP10 | Central | DEM | 2878 | 2009-09-14 | AMOH0100 | Miami Fort 345kV Gas Insulated Bus. Repl. | Replace 345kV gas insulated bus with an air insulated bus | OH |  | 2010-12-02 | Other | Not Shared | Condition | 1440000 | 2014-06-01 | 2014-06-01 | Planned | 345 |  | A | Y
A in MTEP10 | Central | DEM | 2879 | 2009-09-14 | AMIN0256 | Brazil West 69kV tap switches and tap line | Construct Brazil West 10.5MVA 69/12kV sub in the 6902 Line to be located on 900N east of 425W | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 150000 | 2012-12-31 | 2012-12-31 | Planned | 69 | 12 | A | NT
A in MTEP10 | Central | DEM | 2882 | 2009-09-14 | X02C8883 | Lateral replace CB 840 | Replace bus tie breaker #840 and associated disconnect sw's - new limits will be CB - 3000A and D/S's - 2000A. | OH |  | 2010-12-02 | Other | Not Shared | Reliability | 445302 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | A | Y
A in MTEP09 | Central | DEM | 1647 | 2009-09-17 | 503H6967 | Carmel SE 69/12 KV new distribution substation | Construct Carmel SE Bank 1 22.4MVA bank with 2 exits - extend a new radial 69kv from Carmel 146th St (no new bkr - share dist bk terminal) | IN |  | 2009-12-04 | Other | Not Shared | Distribution | 2000000 | 2012-06-01 | 2012-06-01 | Planned | 69 | 12 | A | NT
A in MTEP09 | Central | DEM | 1880 | 2008-01-10 | 103H9056 | Columbia 138kV-22.4MVA Sub | Columbia 138kV-22.4MVA Sub - New site or purchase and rebuild existing Siemens Sub #537- in F5484 between Warren and Maineville | OH |  | 2009-12-04 | Other | Not Shared | Distribution | 215000 | 2012-12-31 | 2012-12-31 | Planned | 138 | 12 | A | Y
A in MTEP09 | Central | DEM | 2127 | 2008-04-07 | 804H3039 | Martinsville 69163-1 switch replacement | 69163-1 switch replacement near tap to HE Cope with 1200A switch | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 40000 | 2019-06-01 | 2019-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2132 | 2008-04-07 | 602J3049 | Frances Creek 69kV capacitor | Frances Creek Install 36MVAR 69kV capacitor bank | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 615500 | 2012-06-30 | 2012-06-30 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2133 | 2008-04-07 | 604H3011 | Franklin to Forsythe new 69kV line | Franklin 230 sub to Forsythe 69 sub - Build new 3.5 mile 69kV line; new line terminal at Forsythe end only | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 1030000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2148 | 2008-04-07 | 504F6518 | Cadiz to Milner's Corner Jct 69kv reconductor | Cadiz to Markleville to Milner's Corner J - Reconductor 69kv - 69131 ckt - 9.24 mile section with 477ACSR@100C; Replace 69kv three way switch at Milner's Corner Jct with three one way 1200A switches; Upgrade the Markleville 600A switches #1 and #2 to 1200A | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 3208251 | 2012-05-01 | 2012-05-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2149 | 2008-04-07 | X02C7984 | West End 138kv bus tie and 1389 line bkrs | West End substation - Install a 138kV circuit breaker to tie the east and west 138 kV busses together and a line breaker in the 1389 ckt | OH |  | 2009-12-04 | BaseRel | Not Shared |  | 1040000 | 2011-12-31 | 2011-12-31 | Under Construction | 138 |  | A | Y
A in MTEP09 | Central | DEM | 2153 | 2008-04-07 | 504G6695 | Mohawk to Lee Hanna 69kV reconductor | Mohawk to Lee Hanna 69kV reconductor 69130 ckt (5.27 mi) with 954acsr@100C | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 2317000 | 2017-06-01 | 2017-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2154 | 2010-06-25 | AMIN0360 | Carmel Rohrer Rd 69/12kv New Sub | Carmel Rohrer Rd 69/12-22.4MVA sub to looped through the 6989 ckt. at or near the existing Carmel Shell Oil tap | IN |  | 2009-12-04 | Other | Not Shared | Distribution | 591143 | 2013-12-31 | 2013-12-31 | Planned | 69 | 12 | A | NT
A in MTEP09 | Central | DEM | 2327 | 2008-10-01 | 704J3096 | Speed to HE Bethany 69kV - 6955 Reconductor Ph1 | Speed to HE Bethany 69kV - 6955 Reconductor Ph1 - Replace 5.2 miles of 3/0 ACSR with 477 ACSR (new limiter 4/0acsr) | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 1560000 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2331 | 2008-10-01 | 504F6413 | Shelbyville NE to Knauf 69kv - 6946 ckt. Reconductor | Shelbyville NE to Knauf Reconductor 1.75 miles of 397ACSR on 6946 ckt. with 954acsr@100C | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 777000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2332 | 2008-10-01 | 504G6696 | Zionsville Turkeyfoot to Zionsville 96th St Jct 69kV - 69155 ckt. Reconductor | Zionsville Turkeyfoot to Zionsville 96th St Jct Reconductor 1.59 mile 69kV - 69155 ckt with 954ACSR@100C | IN |  | 2009-12-04 | Other | Not Shared | Reliability | 704000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | Central | DEM | 2334 | 2009-09-17 | AMIN0132 | Fishers 106th St 69/12kv New Sub | New Fishers 106th St 69/12 kv sub: Construct 69kV line in and out of sub and 69kv bus including 69kv breaker | IN |  | 2009-12-04 | Other | Not Shared | Distribution | 174000 | 2012-06-01 | 2012-06-01 | Planned | 69 | 12 | A | NT
A in MTEP08 | Central | DEM | 834 | 2005-07-11 | AC | Kingman 69kV Cap | Add 7.2 MVAR 69kV capacitor at Kingman. | IN |  | 2008-12-04 | Other | Not Shared |  | 500000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 835 | 2008-04-07 | 602D6064 | Pittsboro 69kV Cap | Add 14.4 MVAR 69kV capacitor at Pittsboro. | IN |  | 2008-12-04 | Other | Not Shared |  | 422362 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 841 | 2009-02-18 | AJ | Westwood Bk1 Limiting Equipment | Replace 1600A 138kV breaker with 3000A to allow full xfr rating. | IN |  | 2008-12-04 | BaseRel | Not Shared |  | 141623 | 2015-06-01 | 2015-06-01 | Planned | 345 | 138 | A | Y
A in MTEP08 | Central | DEM | 1245 | 2008-04-07 | 604G6616 | Frankfort Jefferson to Potato Creek new 69kV Line | Construct new 69kV line from Frankfort Jefferson to new Potato Creek switching station. | IN |  | 2008-12-04 | Other | Not Shared |  | 2094115.23 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1501 | 2007-03-02 | 502G6712 | Carmel 146th St 69kV Cap 2 | Added second 36 MVAR 69kV capacitor at Carmel 146th St | IN |  | 2008-12-04 | Other | Not Shared |  | 624145 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1512 | 2008-10-01 | AMOH0017 | Ashland to Rochelle 138 | Install underground 138 kV circuit from Ashland to Ridgeway (New Dist Sub) to Rochelle. | OH |  | 2008-12-04 | BaseRel | Not Shared |  | 9634051 | 2012-06-01 | 2012-12-31 | Planned | 138 | 13.1 | A | Y
A in MTEP08 | Central | DEM | 1513 | 2007-03-02 | 602G6719 | Metea 69kV Cap | Install 14.4MVAR 69kV capacitor at Metea. | IN |  | 2008-12-04 | Other | Not Shared |  | 865946 | 2011-07-15 | 2011-07-15 | Under Construction | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1514 | 2007-03-02 | 804H6816 | Wabash River to Staunton 230 100C Uprate | Uprate Wabash River to Staunton 23002 to 100C summer operating temperature and 80C winter (559MVA). | IN |  | 2008-12-04 | Other | Not Shared |  | 1286147 | 2011-12-31 | 2011-12-31 | Under Construction | 230 |  | A | Y
A in MTEP08 | Central | DEM | 1519 | 2007-03-02 | 504G6706 | Noblesville NE to Geist 69 | Build a new 69kV line from Noblesville NE sub to tap the Fishers North - Geist 69kV line | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 2640107 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1560 | 2007-06-30 | 802H6857 | Edwardsport 138kV cap | Install a 138kV 57.6MVAR capacitor at Edwardsport. | IN |  | 2008-12-04 | BaseRel | Not Shared |  | 709293 | 2011-07-15 | 2011-07-15 | Under Construction | 138 |  | A | Y
A in MTEP08 | Central | DEM | 1561 | 2007-06-30 | 602F6500 | Kokomo Webster St 230kv Ring bus | Retire existing 1600A circuit switcher and complete the Webster St ring in order to utilize the full capacity of the bundled 477 ACSS wire on the 23016 line. | IN |  | 2008-12-04 | Other | Not Shared |  | 399579.8 | 2012-06-01 | 2012-06-01 | Planned | 230 |  | A | Y
A in MTEP08 | Central | DEM | 1564 | 2007-06-30 | 502H6902 | Roseburg Switching Station cap | Install 69kV 21.6MVAR std capacitor | IN |  | 2008-12-04 | Other | Not Shared |  | 518503 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1568 | 2007-06-30 | 602H6935 | Qualitech 345/138KV Transformer and breakers | Qualitech Sub- Install one 345/138kv, 300Mva Xtr and 2-345kv Bkrs and 1-138kv Bkr to provide second 138kv source to proposed Hendricks Co 138kv system | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 4561673.88 | 2013-06-01 | 2013-06-01 | Planned | 345 | 138 | A | Y
A in MTEP08 | Central | DEM | 1569 | 2007-06-30 | 604H6936 | Qualitech to Pittsboro new 138kv line | Construct new 138kv line, Qualitech to Pittsboro, and connect to the Pittsboro-Brownsbg line to provide new 954ACSR outlet line from Qualitech 345/138kV Bank | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1507855.84 | 2013-06-02 | 2013-06-02 | Planned | 138 |  | A | Y
A in MTEP08 | Central | DEM | 1570 | 2007-06-30 | 604H6907 | Plainfield South to Pittsboro 69KV to 138KV Conversion | Convert the existing 69KV (69144) line from Plainfield S. to Pittsboro (and 4 distribution subs) over to 138KV operation and connect to the new Qualitech to Pittsboro 138KV line | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 4139000 | 2013-06-03 | 2013-06-03 | Planned | 138 |  | A | Y
A in MTEP08 | Central | DEM | 1650 | 2007-10-05 | 704H6984 | Fairview to HE Fairview 13854 Reconductor | Fairview to HE Fairview 13854 Reconductor with 954ACSR @ 100C | IN |  | 2008-12-04 | BaseRel | Not Shared |  | 1236383.93 | 2014-06-30 | 2014-06-30 | Planned | 138 |  | A | Y
A in MTEP08 | Central | DEM | 1881 | 2008-01-10 | X02P6673 | Bloomington Rogers St - replace 13836 breaker | Bloomington Rogers St - replace 13836 breaker and WT; replace 13871 breaker, WT, and disc sw's - All 2000Amp rated; Replace relays for 13836, 13837, 13871 | IN |  | 2008-12-04 | Other | Not Shared |  | 1051992 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP08 | Central | DEM | 1889 | 2011-06-23 | 604B5486 | Danville to Danville Jct 69kV reconductor | Danville to Preswick Jct to Danville Jct - recond. 5.2 mi of the 6945 ckt. with 954acsr OVAL @100C and replace the 600 amp, two way switches at Danville Jct with two 1200 amp one way switches and replace the 600 amp switch at Prestwick Jct with a 1200 amp | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1622359 | 2011-06-23 | 2011-06-23 | Under Construction | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1890 | 2008-01-10 | 504G6684 | Geist to new Fishers N. Jct. 69kV line | Build new 69kV line - 69181 - 4 miles with 954ACSR along 126th St. (completes approx 5.9 mile line section) | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1977421 | 2011-08-16 | 2011-08-16 | Under Construction | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1893 | 2009-01-05 | AMIN0056 | Mitchell Lehigh Portland to Bedford 25th St 6995 rebuild | Reconductor 10.3 miles of 69kV - 6995 line with 477 ACSR@100C | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 3016000 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1895 | 2010-09-22 | AMIN0418 | Brownsburg to Avon East 138kV Reconductor | Brownsburg to Avon East 138kV Reconductor 4.2 miles of 138kV line with 954 ACSR - AFTER 138KV CONVERSION | IN |  | 2008-12-04 | BaseRel | Not Shared |  | 1433226.94 | 2013-06-04 | 2013-06-04 | Planned | 138 |  | A | Y
A in MTEP08 | Central | DEM | 1896 | 2008-01-10 | 504H6988 | Connersville 138 sub to Connersville 30th St 69kV uprate | Connersville 138 sub to Connersville 30th St 69kV Uprate to 100C - 4/0 acsr sections – 1.2 miles - 6981 ckt | IN |  | 2008-12-04 | Other | Not Shared |  | 16493 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1897 | 2008-01-10 | 604B5492 | Deedsville to Macy 69kV Reconductor | Reconductor Deedsville to Macy section of 6957 circuit with 477ACSR approx 2.5 miles; and replace Macy #1 and #2 - 600A line switches (1955 vintage) with 1200A | IN |  | 2008-12-04 | Other | Not Shared |  | 921919.1 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1899 | 2008-01-10 | 604B5493 | Macy to Rochester Metals Jct 69kV reconductor | Reconductor Macy to Rochester Metals Jct section of 6957 circuit with 477ACSR - approx 9.1 miles | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 3102711.45 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1901 | 2008-10-01 | 504G6707 | Noblesville Station to Noblesville Jct 69kV line rebuild | Reconductor 69kV - 6984 & 6916 ckt. Noblesville Plant to Noblesville 8th St. to Noblesville Jct with 954ACSS @ 200C (5.47 miles) | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1510945.57 | 2013-06-01 | 2013-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | DEM | 1902 | 2008-01-10 | 504G6708 | Zionsville 69 to Zionsville 96th Jct 69kV reconductor | Reconductor .32 miles of the 69kV - 69155 line from Zionsville 69 sub to Zionsville 96th Jct with 954ACSR conductor; replace/upgrade 69kV switches, jumpers and bus at Zionsvile 69 sub for a min. capacity of 152MVA (502G6709) | IN |  | 2008-12-04 | Other | Not Shared |  | 309475 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP07 | Central | DEM | 852 | 2009-01-21 | 604F6348 | Crawfordsville to Tipmont Concord to Lafayette SE 138 Reconductor | Reconductor 13819 circuit with 954ACSR 100C. | IN |  | 2007-12-13 | BaseRel | Shared |  | 8919730 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | A | Y
A in MTEP06 | Central | DEM | 851 | 2005-07-11 | AT | Laf Cumberland to Laf AE Staley 138 Reconductor | Reconductor section of 13806 circuit with 954ACSR 100C. | IN |  | 2007-02-15 | BaseRel | Not Shared |  | 349357.4 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | A | Y
A in MTEP06 | Central | DEM | 853 | 2005-07-11 | AV | West Lafayette to Cumberland 138 Reconductor | Reconductor section of 13806 circuit with 954ACSR 100C. | IN |  | 2007-02-15 | Other | Not Shared |  | 706921.48 | 2015-06-01 | 2015-06-01 | Planned | 138 |  | A | Y
A in MTEP06 | Central | DEM | 1244 | 2006-03-27 |  | Cayuga to Frankfort 23013 Wave Trap Upgrade | Upgrade wave traps at Cayuga and Frankfort to increase line rating to 797 MVA. | IN |  | 2007-02-15 | BaseRel | Not Shared |  | 167560 | 2013-06-01 | 2013-06-01 | Planned | 230 |  | A | Y
A in MTEP10 | Central | HE | 3080 | 2009-09-15 |  | Rocklane Tie to Duke 69kV | Build 69kV Transmission from HE Rocklane to Duke 69kV Transmission | IN |  | 2010-12-02 | Other | Not Shared | Reliability | 3000000 | 2011-06-01 | 2011-06-01 | Planned | 69 |  | A | Y
A in MTEP08 | Central | HE | 1927 | 2008-01-10 | None Yet | Hubbell Primary Ring Bus | 138kV Ring Bus addition / Modification to Hubbell Primary | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 3000000 | 2010-09-01 | 2010-09-01 | Planned | 138 |  | A | Y
A in MTEP08 | Central | HE | 1928 | 2008-01-10 | None Yet | Fairview Primary Ring Bus | 138kV Ring Bus addition / Modification to Fairview Primary | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1500000 | 2011-09-01 | 2011-09-01 | Planned | 138 |  | A | Y
A in MTEP08 | Central | HE | 1929 | 2008-01-10 | None Yet | Georgetown Primary Ring Bus | 138kV Ring Bus addition / Modification to Georgetown Primary | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1250000 | 2012-09-01 | 2012-09-01 | Planned | 138 |  | A | Y
A in MTEP08 | Central | HE | 2082 | 2008-02-15 | 903 | Shelbyville Intel Park | 138kV Substation and Tapline | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1000000 | 2009-09-01 | 2009-09-01 | Planned | 138 | 12.5 | A | Y
A in MTEP08 | Central | HE | 2083 | 2008-02-15 | 913 | Wayne County Industrial Park | 69kV Substation and Tapline | IN |  | 2008-12-04 | Other | Not Shared |  | 750000 | 2009-09-01 | 2009-09-01 | Planned | 69 | 12.5 | A | NT
A in MTEP10 | Central | IPL | 2900 | 2009-09-14 | New3 | Northwest - Southwest 138 kV line rating upgrade | Increase line rating from 242 to 382 MVA | IN |  | 2010-12-02 | BaseRel | Not Shared |  | 1500000 | 2011-06-01 | 2011-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | Central | IPL | 2053 | 2010-04-05 |  | Petersburg 345/138kV East and West Autotransformers and 345 kV breaker | Replace and upgrade existing East and West 345/138kV autotransformer at Petersburg Substation. Add 345kV breaker. | IN |  | 2009-12-04 | BaseRel | Shared |  | 15400000 | 2012-06-01 | 2012-06-01 | Planned | 345 | 138 | A | Y
A in MTEP08 | Central | IPL | 1639 | 2010-04-05 |  | General IPL Capacitor Additions | Add capacitors to the IPL General Distribution System | IN |  | 2008-12-04 | Other | Not Shared |  | 50000 | 2013-06-01 | 2013-06-01 | Planned |  |  | A | Y
A in MTEP08 | Central | SIPC | 1778 | 2008-08-01 |  | Hamilton 138KV Interconnect | Construct a 138KV line connecting SIPC Hamilton Substation to Ameren Norris City Substation. This project includes the construction of 18 miles of 138KV line. | IL |  | 2008-12-04 | Other | Not Shared |  | 5000000 | 2008-07-01 | 2008-07-01 | Planned | 138 |  | A | Y
A in MTEP03 | Central | SIPC | 81 | 2011-04-22 |  | Carrier Mills 161kV | A new 25-mile 161kV transmission line from Southern Illinois Power Cooperative's power plant to a new 161/69kV substation located north of Carrier Mills, IL. | IL |  |  | Other | Excluded |  | 10200000 | 2012-09-01 | 2012-09-01 | Planned | 161 | 69 | A | Y
A in MTEP09 | Central | Vectren (SIGE) | 2461 | 2011-06-29 | SIGE2 | Dubois Sub Z84 terminals | Add 1 new 138kV terminal to existing sub to avoid 3 term line, breaking up Duff - Dubois - Culley 138kV line | IN |  | 2009-12-04 | BaseRel | Not Shared |  | 1000000 | 2014-06-01 | 2014-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | Central | Vectren (SIGE) | 2465 | 2011-06-29 | SIGE6 | Leibert Rd 138/12kV Substation | New 138/12kV Substation for load growth | IN |  | 2009-12-04 | Other | Not Shared | Distribution | 2622781 | 2011-10-01 | 2011-10-01 | Planned | 138 | 12.47 | A | NT
A in MTEP09 | Central | Vectren (SIGE) | 2466 | 2008-10-31 | SIGE7 | Roesner Rd 138/12kV Substation | New 138/12kV Substation for load growth | IN |  | 2009-12-04 | Other | Not Shared | Distribution | 3000000 | 2013-06-01 | 2013-06-01 | Planned | 138 | 12.47 | A | NT
A in MTEP08 | Central | Vectren (SIGE) | 1002 | 2010-04-05 |  | New Northeast to Oak Grove to Culley Line 138 kV | New Northeast to Oak Grove to Culley Line 138 kV | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 4368926 | 2012-06-01 | 2012-06-01 | Under Construction | 138 |  | A | Y
A in MTEP08 | Central | Vectren (SIGE) | 1782 | 2010-04-05 |  | NorthEast Sub Bus re-config | Rebuild existing straight bus with more reliable breaker and half scheme | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 7000000 | 2014-12-31 | 2014-12-31 | Planned | 138 |  | A | Y
A in MTEP08 | Central | Vectren (SIGE) | 1784 | 2008-01-10 |  | Jasper#3 Sub Exp-Victory Line | Extend existing Victory line to new term at existing sub | IN |  | 2008-12-04 | Other | Not Shared |  | 3625000 | 2016-06-01 | 2016-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | Vectren (SIGE) | 1785 | 2010-04-05 |  | Z83 Upgrade | Upgrade terminal equipment at NE and NW. | IN |  | 2008-12-04 | Other | Not Shared |  | 100000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | A | Y
A in MTEP08 | Central | Vectren (SIGE) | 1787 | 2008-01-10 |  | Y75 - Dale to Santa Clause | New 69kV line from Dale Sub to Santa Clause Sub | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 5000000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | Vectren (SIGE) | 1788 | 2008-01-10 |  | Y34 - St. Wendel to Mohr Rd | New 69kV line from St. Wendel Sub to Mohr Rd Sub | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 2750000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | Vectren (SIGE) | 1789 | 2008-01-10 |  | Y56 - City of Boonville Loop | New 69kV line from Boonville Sub to Boonville Pioneer Sub | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 1400000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | Vectren (SIGE) | 1790 | 2008-01-10 |  | Y52 rebuild and Sunbeam loop | Rebuild/Reconductor existing Y52 and loop into Sunbeam | IN |  | 2008-12-04 | Other | Not Shared | Reliability | 2550000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | A | NT
A in MTEP08 | Central | Vectren (SIGE) | 1791 | 2008-01-10 |  | Y66-2 Angel Mounds to Eastside uprate | Uprate Y66-2 from Angel Mounds to East Side to increase transfer capacity | IN |  | 2008-12-04 | Other | Not Shared |  | 300000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP06 | Central | Vectren (SIGE) | 1257 | 2010-04-05 |  | New Transmission Line Gibson (Cinergy) to AB Brown (Vectren) to Reid (BREC) | New 345 kV transmission line Gibson (Cinergy) to AB Brown (Vectren) to Reid (BREC) | IN | KY | 2007-06-20 | BaseRel | Shared |  | 46284114 | 2012-06-01 | 2012-06-01 | Under Construction | 345 |  | A | Y
A in MTEP10 | East | ITC | 2918 | 2009-09-14 |  | Breaker Replacement Program 2012 | Replace defective, damaged, or over dutied breakers throughout system. | MI |  | 2010-12-02 | Other | Not Shared | Condition | 6000000 | 2012-12-31 | 2012-12-31 | Planned | 345 | 120 | A | Y
A in MTEP10 | East | ITC | 2919 | 2009-09-14 |  | NERC Relay Loadability Compliance 2012 | Upgrade relays throughout system | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 2400000 | 2012-12-31 | 2012-12-31 | Planned | 345 | 120 | A | Y
A in MTEP10 | East | ITC | 2920 | 2009-09-14 |  | Potential Device Replacement 2012 | Replace aging potential devices | MI |  | 2010-12-02 | Other | Not Shared | Condition | 300000 | 2012-12-31 | 2012-12-31 | Planned | 345 | 120 | A | Y
A in MTEP10 | East | ITC | 2921 | 2009-09-14 |  | Relay Betterment Program 2012 | Replace aging and electromechanical relays throughout the system. Add OPGW where needed. | MI |  | 2010-12-02 | Other | Not Shared | Condition | 1200000 | 2012-12-31 | 2012-12-31 | Planned | 345 | 120 | A | Y
A in MTEP10 | East | ITC | 2922 | 2009-09-14 |  | Wood Pole Replacement 2012 | Replace deteriorating wood pole | MI |  | 2010-12-02 | Other | Not Shared | Condition | 4800000 | 2012-12-31 | 2012-12-31 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2923 | 2009-09-14 |  | Capacitor Replacement 2012 | Replace capacitor banks | MI |  | 2010-12-02 | Other | Not Shared | Condition | 600000 | 2012-12-31 | 2012-12-31 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2925 | 2009-09-14 |  | Blanket for Customer Interconnection 2011 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2000000 | 2011-12-31 | 2011-12-31 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2926 | 2009-09-14 |  | Blanket for Customer Interconnection 2012 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2000000 | 2012-12-31 | 2012-12-31 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2927 | 2009-09-14 |  | Blanket for Customer Interconnection 2013 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2000000 | 2013-12-31 | 2013-12-31 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2928 | 2009-09-14 |  | Blanket for Customer Interconnection 2014 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2000000 | 2014-12-31 | 2014-12-31 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2929 | 2010-01-06 |  | Ariel Substation (formerly Holland) | Distribution Interconnection to add two new 120/13.2kV transformers at Holland. Connects to the Wheeler to Troy 120kV circuit. | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2800000 | 2012-12-30 | 2012-12-30 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 2930 | 2009-09-14 |  | Upper Rouge | Distribution Interconnection to add a new 120/4.8kV transformer at Upper Rouge. | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 1900000 | 2015-12-30 | 2015-12-30 | Planned | 120 |  | A | Y
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 Cand. MVP Port.1 | Proposed MVP Portfolio 1 - Michigan Thumb Wind Zone | The proposed transmission line will connect into a new station to the south and west of the Thumb area that will tap three existing 345 kV circuits; one between the Manning and Thetford 345 kV stations, one between the Hampton and Pontiac 345 kV stations and one between the Hampton and Thetford 345 kV stations. Two new 345 kV circuits will extend from this new station, to be called Baker (formerly Reese), up to a new station, to be called Rapson (formerly Wyatt or Wyatt East) that will be located to the north and east of the existing 120 kV Wyatt station. In order to support the existing 120 kV system in the northern tip of the Thumb, the two existing 120 kV circuits between the Wyatt and Harbor Beach stations, one that connects directly between Wyatt and Harbor Beach and that connects Wyatt to Harbor Beach through the Seaside station, will be cut into the new Rapson station. From the Rapson station station, two 345 kV circuits will extend down the east side of the Thum to the existing Greenwood 345 kV station and then continue south to the point where the existing three ended Pontiac to Greenwood to Belle River 345 kV circuit combines. To facilitate connection to the existing transmission system a new 345 kV station, to be called Fitz (formerly Saratoga), is included in the plan at a site due south of the existing Greenwood station and just north of where the existing three ended Pontiac to Greenwood to Belle River 345 kV circuit combines. The Fitz station will then tap the existing Pontiac to Belle River to Greenwood 345 kV circuit and the existing Belle River to Blackfoot 345 kV circuit. Transformation from the 345 kV facilities to the 120 kV facilities will be necessary to maintain continuity to the existing system in and around the Sandusky area. The existing 120 kV facilities between the site that will facilitate the new 345 kV to 120 kV transformation can be utilized to facilitate a connection between the new 345 kV to 120 kV transformation and the existing 120 kV facilities in the Sandusky area. | MI |  | 2010-12-02 | MVP | Shared |  | 510000000 | 2013-12-31 | 2015-12-31 | Planned | 345 | 120 | A | Y
A in MTEP09 | East | ITC | 1872 | 2008-12-09 |  | Scio | Distribution Interconnection to add new 120/41kV transformer. Loops the Lark-Spruce 120kV circuit into the station. | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 3000000 | 2013-06-01 | 2013-06-01 | Planned | 120 |  | A | Y
A in MTEP09 | East | ITC | 2519 | 2008-12-09 |  | Breaker Replacement Program 2011 | Replace defective, damaged, or over dutied breakers throughout system. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 5650000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2520 | 2008-12-09 |  | Cable Termination Replacement 2011 | Replace high pressure gas filled underground cable terminations throughout system. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 3000000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2521 | 2008-12-09 |  | Relay Betterment Program 2011 | Replace aging and electromechanical relays throughout the system. Add OPGW where needed. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 1200000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2525 | 2008-12-09 |  | Capacitor Replacement 2011 | Replace capacitor banks | MI |  | 2009-12-04 | Other | Not Shared | Condition | 565000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2528 | 2008-12-09 |  | Potential Device Replacement 2011 | Replace aging potential devices | MI |  | 2009-12-04 | Other | Not Shared | Condition | 300000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2531 | 2008-12-09 |  | Power Plant Control Relocation 2011 | Relocate substation controls currently located in power plant control rooms | MI |  | 2009-12-04 | Other | Not Shared | Condition | 1200000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2534 | 2008-12-09 |  | Wood Pole Replacement 2011 | Replace deteriorating wood pole | MI |  | 2009-12-04 | Other | Not Shared | Condition | 9000000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2537 | 2008-12-09 |  | Synchronizing Sites 2011 | New 120kV synchronizing sites | MI |  | 2009-12-04 | Other | Not Shared | Operations | 565000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | ITC | 2539 | 2008-12-09 |  | NERC Relay Loadability Compliance 2011 | Upgrade relays throughout system | MI |  | 2009-12-04 | BaseRel | Not Shared |  | 2250000 | 2011-12-31 | 2011-12-31 | Planned | 120 |  | A | Y
A in MTEP09 | East | ITC | 2541 | 2008-12-09 |  | Hunters Creek - Robin - Wabash | Install double groundwire peaks and second shield wire. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 2400000 | 2011-07-22 | 2011-07-22 | Under Construction | 120 |  | A | Y
A in MTEP09 | East | ITC | 2545 | 2008-10-31 |  | Marathon/Navarre | New distribution interconnection served from Navarre substation | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 640000 | 2011-09-01 | 2011-09-01 | Planned | 120 |  | A | Y
A in MTEP08 | East | ITC | 1870 | 2008-08-04 |  | Clyde | Distribution Interconnection to add a new 120/41kV transformer at Clyde. Taps the Placid-Durant 120kV circuit | MI |  | 2008-12-04 | Other | Not Shared |  | 2750000 | 2013-06-01 | 2013-06-01 | Planned | 120 |  | A | Y
A in MTEP08 | East | ITC | 1873 | 2008-01-10 |  | Tahoe | Distribution Interconnection to add a new 120/13.2kV transformer at Tahoe. | MI |  | 2008-12-04 | Other | Not Shared |  | 2800000 | 2013-05-31 | 2013-05-31 | Planned | 120 |  | A | Y
A in MTEP06 | East | ITC | 1308 | 2008-10-01 | ITC30 | B3N Interconnection | Returns the Bunce Creek to Scott 220 kV circuit to service, and replaces the Phase Angle Regulator with 2 new phase angle regulating transformers in series | MI |  | 2007-02-15 | Other | Not Shared |  | 25000000 | 2011-09-30 | 2011-09-30 | Planned | 220 |  | A | Y
A in MTEP06 | East | ITC | 1310 | 2008-10-01 | ITC31 | Breaker Replacement Program | Targets the replacement of breakers nearing their end of life where maintenance costs will be just as high as new breakers | MI |  | 2007-02-15 | Other | Not Shared |  | 150000 | 2011-09-30 | 2011-09-30 | Planned | 120 |  | A | Y
A in MTEP10 | East | METC | 2502 | 2009-09-25 |  | McGulpin Shunt Reactor | Install shunt reactor McGulpin | MI |  | 2010-12-02 | BaseRel | Not Shared |  | 3000000 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2903 | 2009-09-14 |  | Battery Replacement 2012 | Replace batteries and chargers | MI |  | 2010-12-02 | Other | Not Shared | Condition | 300000 | 2012-12-31 | 2012-12-31 | Planned |  |  | A | Y
A in MTEP10 | East | METC | 2904 | 2009-09-14 |  | Breaker Replacement Program 2012 | Replace defective, damaged, or over dutied breakers throughout system. | MI |  | 2010-12-02 | Other | Not Shared | Condition | 6000000 | 2012-12-31 | 2012-12-31 | Planned |  |  | A | Y
A in MTEP10 | East | METC | 2905 | 2009-09-14 |  | NERC Relay Loadability Compliance 2012 | Upgrade relay throught system | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 2400000 | 2012-12-31 | 2012-12-31 | Planned |  |  | A | Y
A in MTEP10 | East | METC | 2906 | 2009-09-14 |  | Potential Device Replacement 2012 | Replace aging potential devices | MI |  | 2010-12-02 | Other | Not Shared | Condition | 300000 | 2012-12-31 | 2012-12-31 | Planned |  |  | A | Y
A in MTEP10 | East | METC | 2907 | 2009-09-14 |  | 'Power Plant Control Relocation 2012 | Relocate substation controls currently located in power plants control rooms | MI |  | 2010-12-02 | Other | Not Shared | Condition | 1200000 | 2012-12-31 | 2012-12-31 | Planned |  |  | A | Y
A in MTEP10 | East | METC | 2908 | 2009-09-14 |  | Relay Betterment Program 2012 | Replace aging and electromechanical relays throughout the system. Add OPGW where needed. | MI |  | 2010-12-02 | Other | Not Shared | Condition | 1200000 | 2012-12-31 | 2012-12-31 | Planned |  |  | A | Y
A in MTEP10 | East | METC | 2909 | 2009-09-14 |  | Sag clearance 2012 | Identify and remediate inherent sag limitations on heavily loaded METC trasmission lines throughout the system. | MI |  | 2010-12-02 | Other | Not Shared | clearance | 3600000 | 2012-12-31 | 2012-12-31 | Planned | 345 | 138 | A | Y
A in MTEP10 | East | METC | 2910 | 2009-09-14 |  | Wood Pole Replacement 2012 | Replace deteriorating wood pole | MI |  | 2010-12-02 | Other | Not Shared | Condition | 4800000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2912 | 2009-09-14 |  | Blanket for Customer Interconnections 2011 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2500000 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2913 | 2009-09-14 |  | Blanket for Customer Interconnections 2012 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2500000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2914 | 2009-09-14 |  | Blanket for Customer Interconnections 2013 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2500000 | 2013-12-31 | 2013-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2915 | 2009-09-14 |  | Blanket for Customer Interconnections 2014 | Throughout system | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 2500000 | 2014-12-31 | 2014-12-31 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2916 | 2010-07-21 |  | Livingston - Vanderbilt 138 kV Rebuild | Rebuild 9.7 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. | MI |  | 2010-12-02 | BaseRel | Shared |  | 12734400 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP10 | East | METC | 2917 | 2009-09-14 |  | David Jct - Hubbardson Jct - Bingham Sag Remediation | Improve sag clearance by replacing 16 wood poles with 138 kV FDC steel poles. | MI |  | 2010-12-02 | BaseRel | Not Shared |  | 1216860 | 2011-11-30 | 2011-11-30 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 646 | 2010-04-03 | 86 | Edenville Jct. - Warren 138kV | Replace poles on the Edenville-Warren 138kV line to future-double-circuit, prebuilt to 230kV. | MI |  | 2009-12-04 | Other | Not Shared | Reliability | 12500000 | 2011-12-01 | 2012-12-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 662 | 2009-07-16 | 117 | Weeds Lake | Loop the 345kV Argenta - Robinson Park 345kV circuit into a new 345/138kV EHV substation called Weeds Lake. Build 4 new (approximately 6 miles) 138kV circuits to loop the two Argenta-Milham 138kV lines into the substation. | MI |  | 2009-12-04 | BaseRel | Shared |  | 45026457 | 2013-06-01 | 2013-06-01 | Planned | 345 | 138 | A | Y
A in MTEP09 | East | METC | 1810 | 2009-06-26 |  | Iosco - East Tawas 138kV | Rebuild 12 miles of 138kV to 954 ACSR. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 9818854 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 1833 | 2008-12-09 |  | Sag clearance 2011 | Identify and remediate inherent sag limitations on heavily loaded METC trasmission lines throughout the system. | MI |  | 2009-12-04 | Other | Not Shared | Clearance | 3400000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | METC | 2475 | 2008-10-31 |  | Titus Lake | Distribution interconnection to add a second transformer at Titus Lake. | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 4200000 | 2015-06-01 | 2015-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2478 | 2010-09-28 |  | Capital Ave | New distribution interconnection served from Battle Creek - Verona #2 138kV (Line connection change to Battle Creek to Island Road) | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 178188 | 2012-05-31 | 2012-05-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2481 | 2008-12-09 |  | Forrest Grove | New distribution interconnection served from Campbell-Ransom 138kV circuit. | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 170000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2482 | 2008-10-31 |  | Hawthorne | New distribution interconnection served from Four Mile - Blendon 138kV circuit. | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 170000 | 2013-05-31 | 2013-05-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2483 | 2008-10-31 |  | Maines Road | New distribution interconnection served from Marshall - Blackstone 138kV circuit | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 176386 | 2012-05-31 | 2012-05-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2484 | 2008-10-31 |  | Scenic Lake | New distribution interconnection served from Cornell-Tihart 138kV circuit | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 176386 | 2012-05-31 | 2012-05-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2485 | 2008-12-09 |  | Ironwood | New distribution interconnection served from CE's 138kV spur on the Ransom-Buck Creek 138kV. | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 12000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2486 | 2008-10-31 |  | Haakwood | New distribution interconnection served from Riggsville-Livingston 138kV (on the Rondo-Vanderbilt section) | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 170000 | 2014-05-31 | 2014-05-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2487 | 2008-12-09 |  | Birchwood | New distribution interconnection served from Spaulding-Plaster Creek 138kV (on the Spaulding-Kraft section) | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 170000 | 2012-06-30 | 2012-06-30 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2489 | 2010-04-03 |  | Terminal Equipment upgrade at Tippy | Terminal Equipment upgrade at Tippy on the Tippy-Keystone 138kV line | MI |  | 2009-12-04 | BaseRel | Not Shared |  | 60215 | 2011-09-30 | 2011-09-30 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2492 | 2008-12-09 |  | Battle Creek - Verona 138kV ckt. #2 | Upgrade terminal equipment. | MI |  | 2009-12-04 | BaseRel | Not Shared |  | 200000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2496 | 2008-12-09 |  | Bullock - Tittabawassee 138kV | Upgrade terminal equipment. | MI |  | 2009-12-04 | BaseRel | Not Shared |  | 360000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2498 | 2008-12-09 |  | Breaker Replacement Program 2011 | Replace defective, damaged, or over dutied breakers throughout system. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 5650000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | METC | 2499 | 2008-12-09 |  | Relay Betterment Program 2011 | Replace aging and electromechanical relays throughout the system. Add OPGW where needed. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 1200000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP09 | East | METC | 2501 | 2008-12-09 |  | Northern Reactive | Install 3 capacitors in the northern part of Michigan | MI |  | 2009-12-04 | BaseRel | Not Shared |  | 2700001 | 2012-06-01 | 2012-06-01 | Planned |  |  | A | Y
A in MTEP09 | East | METC | 2507 | 2009-06-26 |  | Alcona - Mio 138kV | Rebuild the line to 954 ACSR future-double-circuit (pre-built to 230kV) | MI |  | 2009-12-04 | Other | Not Shared | Condition | 24500000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2510 | 2008-12-09 |  | Wood Pole Replacement 2011 | Replace deteriorating wood pole | MI |  | 2009-12-04 | Other | Not Shared | Condition | 6000000 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2515 | 2009-06-26 |  | Tihart - Oakland (Genoa) 138kV | Replace all line structures and insulators. | MI |  | 2009-12-04 | Other | Not Shared | Condition | 18871627 | 2011-08-01 | 2011-08-01 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2517 | 2008-10-31 |  | NERC Relay Loadability Compliance 2011 | Upgrade relay throught system | MI |  | 2009-12-04 | BaseRel | Not Shared |  | 2250000 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP09 | East | METC | 2522 | 2010-04-03 |  | Power Plant Control Relocation 2011 | Relocate substation controls currently located in power plants control rooms |  |  | 2009-12-04 | Other | Not Shared | Condition | 1200000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP08 | East | METC | 1448 | 2006-10-25 | 196 | Simpson | Project to connect a distribution transformer at Simpson | MI |  | 2008-12-04 | Other | Not Shared |  | 2200000 | 2016-06-01 | 2016-06-01 | Planned | 138 | 12.5 | A | Y
A in MTEP08 | East | METC | 1655 | 2007-10-26 |  | Breaker Repair or Replace Program | throughout system | MI |  | 2008-12-04 | Other | Not Shared |  | 480000 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP08 | East | METC | 1796 | 2008-08-04 |  | Twining - Almeda 138kV | Rebuild 22 miles of 138kV of 110 Cu to 954 ACSR. Prebuild to 230kV construction. | MI |  | 2008-12-04 | BaseRel | Shared |  | 22819200 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP08 | East | METC | 1814 | 2008-01-10 |  | Tippy - Chase 138kV | Rebuild 30 miles of 138kV 110 CU to 954 ACSR. Prebuild to 230kV construction. | MI |  | 2008-12-04 | BaseRel | Shared |  | 26970000 | 2012-12-31 | 2012-12-31 | Planned | 138 |  | A | Y
A in MTEP08 | East | METC | 1820 | 2008-08-04 |  | METC Communication and Relaying Upgrade | Throughout system | MI |  | 2008-12-04 | Other | Not Shared |  | 10000000 | 2011-12-31 | 2011-12-31 | Planned |  |  | A | Y
A in MTEP08 | East | METC | 1834 | 2008-01-10 |  | Tirrell Road | New Distrbution Interconnection served from Battle Creek - Island Rd. 138kV circuit | MI |  | 2008-12-04 | Other | Not Shared |  | 200000 | 2011-12-15 | 2011-12-15 | Planned | 138 |  | A | Y
A in MTEP08 | East | METC | 1841 | 2008-08-04 |  | Eagles Landing | New Distrbution Interconnection served from Iosco - Karn 138kV circuit | MI |  | 2008-12-04 | Other | Not Shared |  | 178188 | 2012-05-31 | 2012-05-31 | Planned | 138 |  | A | Y
A in MTEP06 | East | METC | 988 | 2010-01-06 | 120 | Simpson - Batavia 138 kV line | Simpson - Batavia 138 kV line - Build 30 miles new 138 kV line, 795 ACSS | MI |  | 2007-02-15 | BaseRel | Shared |  | 37100000 | 2011-12-31 | 2011-12-31 | Planned | 138 |  | A | Y
A in MTEP06 | East | METC | 1408 | 2008-12-09 | 158 | RTU / SCADA Re-direction Program | Install and/or upgrade RTU's and SCADA points throughout system | MI |  | 2007-02-15 | Other | Not Shared |  | 801000 | 2013-06-30 | 2013-06-30 | Under Construction | 345 | 138 | A | Y
A in MTEP06 | East | METC | 1434 | 2006-10-25 | 182 | Five Mile | Install bulk substation served from the Spaulding 138kV ring bus | MI |  | 2007-02-15 | Other | Not Shared |  | 750000 | 2014-06-01 | 2014-06-01 | Planned | 138 |  | A | Y
A in MTEP06 | East | METC | 1445 | 2006-10-25 | 193 | Emmet | Install a second distribution transformer at Emmet | MI |  | 2007-02-15 | Other | Not Shared |  | 2750000 | 2016-12-31 | 2016-12-31 | Planned | 138 |  | A | Y
A in MTEP06 | East | METC | 1447 | 2006-10-25 | 195 | Horseshoe Creek (Deja) | Install bulk substation served from the Eureka-Deja-Vestaburg 138kV Line | MI |  | 2007-02-15 | Other | Not Shared |  | 2200000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | A | Y
A in MTEP10 | East | MPPA | 3074 | 2011-01-10 | 17-3 | TC East - Parsons TLine | New 4.1 mi 69kV transmission line from new TC East Sub to existing Parsons Sub | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 1600000 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | A | NT
A in MTEP10 | East | MPPA, METC | 3073 | 2011-01-10 | 17-2 | TC East Substation | New 138/69kV Substation Interconnection | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 8413791 | 2011-12-31 | 2012-12-31 | Planned | 138 | 69 | A | Y
A in MTEP10 | East | NIPS | 2322 | 2009-09-14 | 71C7407 | Green Acres Sub.- 345-138kV Transformer | Install a 560 MVA 345/138 kV transformer, (1) 345 kV and (1) 138 kV circuit breaker and associated equipment at Green Acres Substation. | IN |  | 2010-12-02 | BaseRel | Shared |  | 7417000 | 2011-06-01 | 2011-06-01 | Planned | 345 | 138 | A | Y
A in MTEP08 | East | NIPS | 1996 | 2009-09-14 | 9326166 | Circuit 6980 - Angola Sub to Sw #644 - Rebuild w 336 KCM ACSR | Rebuild and upgrade 12 miles of Circuit 6980's existing 2/0 Cu to 336.4 kCM ACSR. | IN |  | 2008-12-04 | Other | Not Shared |  | 2465948 | 2012-12-01 | 2012-12-01 | Under Construction | 69 |  | A | Y
A in MTEP08 | East | NIPS | 1997 | 2009-04-01 | X7L6304 | Circuit 6977 - Goshen Jct to Model Sub Tap - Recond. 1.5 Miles | Upgrade (reconductor) 1.5 miles of 69 KV line to 336.4 KCM ACSR. | IN |  | 2008-12-04 | Other | Not Shared |  | 357000 | 2015-12-01 | 2015-12-01 | Planned | 69 |  | A | Y
A in MTEP10 | East | WPSC | 3060 | 2011-01-11 | Morley Cap. Bank | Morley Capacitor Bank | Install a Capacitor Bank tap at the Morley substation | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 260000 | 2020-12-31 | 2020-12-31 | Planned | 69 |  | A | Y
A in MTEP10 | East | WPSC | 3061 | 2009-11-20 | Tremaine Tap | Tremaine | New Distribution Interconnection from the Burnips to Portland circuit | MI |  | 2010-12-02 | Other | Not Shared | Distribution | 200000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | Y
A in MTEP10 | East | WPSC | 3062 | 2009-11-20 | Blendon Xfmr | Blendon Transformer Upgrade | Replace Blendon Transformer with a larger transformer | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 3750000 | 2013-12-31 | 2013-12-31 | Planned | 138 | 69 | A | Y
A in MTEP10 | East | WPSC | 3063 | 2011-03-17 | RW-BB | Redwood to Baseline Rebuild | Rebuild the Redwood to Baseline line section with a larger conductor | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 2500000 | 2011-12-31 | 2011-12-31 | Under Construction | 69 |  | A | Y
A in MTEP10 | East | WPSC | 3068 | 2011-01-11 | S. Boardman Cap. Bank | South Boardman Capacitor Bank | Install a Capacitor Bank at the South Boardman substation | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 260000 | 2014-12-31 | 2014-12-31 | Planned | 69 |  | A | Y
A in MTEP10 | East | WPSC | 3069 | 2011-01-11 | Weidman Cap. Bank | Weidman Capacitor Bank | Install a Capacitor Bank at the Weidman substation | MI |  | 2010-12-02 | Other | Not Shared | Reliability | 260000 | 2020-12-31 | 2020-12-31 | Planned | 69 |  | A | Y
A in MTEP09 | East | WPSC | 2735 | 2010-01-06 | AB-WW | Alba-Westwood Line Rebuild | Alba - Mancelona - Westwood 69 kV line rebuild (11 miles) to 143 MVA | MI |  | 2009-12-04 | Other | Not Shared | Reliability | 4800000 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | A | Y
A in MTEP09 | East | WPSC | 2736 | 2010-01-06 | EB-SB | East Bay-South Boardman Line Rebuild | East Bay - South Boardman Dist - South Boardman 69 kV line rebuild (16 miles) to 143 MVA | MI |  | 2009-12-04 | Other | Not Shared | Reliability | 6500000 | 2014-12-31 | 2014-12-31 | Planned | 69 |  | A | Y
A in MTEP09 | East | WPSC | 2770 | 2009-02-03 |  | Gilmore | New distribution interconnection served from Hersey to Vestaburg circuit. | MI |  | 2009-12-04 | Other | Not Shared | Distribution | 200000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | Y
A in MTEP08 | East | WPSC | 1222 | 2011-06-23 | LC Upgrade | Lake County 69kV Ring Bus and Transformer | Convert 4 breaker bus at Lake County to Ring Bus and add 168MVA transformer | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 6050000 | 2011-12-31 | 2011-12-31 | Under Construction | 138 | 69 | A | Y
A in MTEP08 | East | WPSC | 1274 | 2010-01-06 | BQ-OF | Blendon to Osipoff | Blendon to Osipoff line rebuild | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 7400000 | 2012-12-31 | 2014-12-31 | Planned | 69 |  | A | Y
A in MTEP08 | East | WPSC | 1311 | 2010-01-06 | GN-CH | Copemish to Grawn | Copemish to Grawn line rebuild | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 9100000 | 2012-12-31 | 2014-12-31 | Planned | 69 |  | A | Y
A in MTEP08 | East | WPSC | 1313 | 2010-01-06 | PJ-HY | Plains X to Hersey | Plains X to Hersey line rebuild | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 11450000 | 2012-12-31 | 2015-12-31 | Planned | 69 |  | A | Y
A in MTEP08 | East | WPSC | 1581 | 2010-01-06 | AB-AD | Alba to Advance 69 rebuild | Alba to Advance 69 kV line rebuild | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 7300000 | 2011-12-31 | 2012-12-31 | Planned | 69 |  | A | Y
A in MTEP08 | East | WPSC | 1586 | 2011-03-17 | GY-AD AD-PY PY-OE | Gaylord to Advance 69 kV line rebuild, Advance to Petoskey 69 kV line rebuild, Petoskey to Oden 69 kV line rebuild | Rebuild Overloaded line | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 7200000 | 2015-12-31 | 2015-12-31 | Planned | 69 |  | A | Y
A in MTEP08 | East | WPSC | 1967 | 2009-01-26 | WD-PD | Wayland to Portland | Rebuild Outdated line | MI |  | 2008-12-04 | Other | Not Shared | Reliability | 14542000 | 2020-12-31 | 2020-12-31 | Planned | 69 |  | A | Y
A in MTEP06 | East | WPSC | 1272 | 2010-09-28 | RW 2nd xfmr | Redwood 75MVA Transformer | Add 75MVA Transformer at Redwood Substation a separate line from Redwood Junction will be ran to energize the transformer. | MI |  | 2007-02-15 | Other | Not Shared | Reliability | 3000000 | 2012-12-31 | 2012-12-31 | Planned | 138 | 69 | A | Y
A in MTEP10 | West | ATC LLC | 2451 | 2010-04-30 |  | Brodhead-S Monroe 69kV Rebuild | Rebuild Brodhead- S Monroe 69kV line with T2 477 kcmil ACSR | WI |  | 2010-12-02 | Other | Not Shared | Reliability | 11800000 | 2012-03-01 | 2012-03-01 | Planned | 69 |  | A | Y
A in MTEP10 | West | ATC LLC | 2819 | 2010-09-15 |  | Replace Bluemound 230/138kV transformerT3 | Replace Bluemound 230/138kV transformer T3 with a 400 MVA unit | WI |  | 2010-12-02 | Other | Not Shared | Condition | 8000000 | 2011-12-27 | 2011-12-27 | Planned | 230 | 138 | A | Y
A in MTEP10 | West | ATC LLC | 3122 | 2010-02-01 |  | Reconductor a portion of Dam Heights-Okee Tap 69kV | Reconductor 1.94 mi of 3-0 and 336 ACSR line conductor with T-2 4-0 ACSR keeping the T-2 3-0 ACSR for the DHT-Okee Tap section of line Y-8, replace 26 1919 vintage lattice towers and 4 wood poles | WI |  | 2010-12-02 | Other | Not Shared | Condition | 2177421 | 2012-06-19 | 2012-06-19 | Planned | 69 |  | A | Y
A in MTEP09 | West | ATC LLC | 2452 | 2010-04-30 |  | G706 Glacier Hills Wind Farm | G706 Glacier Hills Wind Farm; taps Friesland-Hamilton 138 kV line | WI |  | 2009-12-04 | GIP | Shared |  |  | 2011-12-31 | 2011-12-31 | Planned | 0.69 |  | A | Y
A in MTEP08 | West | ATC LLC | 356 | 2011-08-24 | F1435 | Rockdale-West Middleton 345 kV | Construct a new 345/138 kV substation at Cardinal (next to the existing West Middleton sub), install a 345/138 kV 500 MVA transformer at Cardinal, construct 47.9 miles overhead 345 kV line from Albion to Cardinal/West Middleton, modifications to the existing West Middleton substation, construct a new Albion 345 kV switching station. Facility costs listed in the facility table are for the southern route. | WI |  | 2008-12-04 | BaseRel | Shared |  | 219124872.29 | 2013-06-01 | 2013-06-01 | Planned | 345 | 138 | A | Y
A in MTEP08 | West | ATC LLC | 574 | 2010-09-15 | F2454 | Monroe County - Council Creek 161 kV line projects | Monroe County - Council Creek 161 kV line, Council Creek 161/138 kV transformer; Council Creek-Petenwell uprate 138 kV | WI |  | 2008-12-04 | Other | Not Shared |  | 34703000 | 2014-06-01 | 2014-06-01 | Planned | 161 | 69 | A | Y
A in MTEP08 | West | ATC LLC | 1683 | 2007-11-07 |  | Rebuild Sunset Point-Pearl Ave 69 kV line | Rebuild 2.37 miles of 69 kV from Sunset Point-Pearl Ave with 477 ACSR | WI |  | 2008-12-04 | Other | Not Shared | Reliability | 4128701.46 | 2012-03-01 | 2012-03-01 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 1018 | 2009-11-19 | 20386 | Little Falls - Pierz conversion to 115 kV | CWP Little Falls-MP Little Falls 115 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 1705513.76 | 2012-11-30 | 2012-11-30 | Planned | 115 |  | A | Y
A in MTEP10 | West | GRE | 2564 | 2009-09-14 | 20225 | Sartell (SEA) 3.0 mile, 115 kV line | Sartell (SEA) 3.0 mile, 115 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 1385861.12 | 2012-10-28 | 2012-10-28 | Planned | 115 |  | A | Y
A in MTEP10 | West | GRE | 2565 | 2009-09-14 | 20279 | Frazer Bay Development | Frazer Bay Development | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 19275099.17 | 2012-11-05 | 2012-11-05 | Planned | 115 | 69 | A | Y
A in MTEP10 | West | GRE | 2566 | 2009-09-14 | 20294 | Potato Lake (IM) 7 mile, 115 kV line | Potato Lake (IM) 7 mile, 115 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 4401144.26 | 2011-10-14 | 2011-10-14 | Under Construction | 115 |  | A | Y
A in MTEP10 | West | GRE | 2567 | 2009-09-14 | 20311 | Northport (BENCO) 1 mile, dbl ckt 115 kV line | Northport (BENCO) 1 mile, dbl ckt 115 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 1149664 | 2012-10-31 | 2012-10-31 | Planned | 115 |  | A | Y
A in MTEP10 | West | GRE | 2570 | 2009-09-14 | 20197 | Ravenna (DEA) 161 kV Substation | Ravenna (DEA) 161 kV Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 821206.11 | 2014-06-02 | 2014-06-02 | Planned | 161 |  | A | Y
A in MTEP10 | West | GRE | 2574 | 2009-09-14 | 20285 | St. Lawrence Substation and Tap - MVEC | St. Lawrence Substation and Tap - MVEC | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 374182.3301 | 2017-05-01 | 2017-05-01 | Planned | 115 |  | A | Y
A in MTEP10 | West | GRE | 2576 | 2009-09-14 | 20310 | Pokegama (LCP) 8.0 mile, 115 kV line | Pokegama (LCP) 8.0 mile, 115 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 4079992.7128 | 2011-11-01 | 2011-11-01 | Under Construction | 115 |  | A | Y
A in MTEP10 | West | GRE | 2577 | 2009-09-14 | 20312 | Elmcrest (CE) 69 kV Substation | Elmcrest (CE) 69 kV Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 140000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2579 | 2010-09-15 | 20273 | Foster Lake (WH) 69 kV Substation | Foster Lake (WH) 69 kV Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 140000 | 2015-05-29 | 2015-05-29 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2589 | 2009-11-19 | 20328 | Barnes Grove (DEA) 2.0 mile, 69 kV line | Barnes Grove (DEA) 2.0 mile, 69 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 115001 | 2014-03-25 | 2014-03-25 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2605 | 2009-09-14 | 20344 | Bunker Lake #2 (CE at GRE) 69 kV Substation | Bunker Lake #2 (CE at GRE) 69 kV Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 208449.71 | 2012-04-30 | 2012-04-30 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2621 | 2009-11-19 | 20371 | Effie 230/69 kV source | Effie 230/69 kV transformer, Effie-Big Fork 69 kV line, Wirt Tap 3-way switch, Jessie Lake 3-way switch, Big Fork 3-way switch | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 10527919 | 2013-11-01 | 2013-11-01 | Planned | 230 | 69 | A | Y
A in MTEP10 | West | GRE | 2624 | 2009-09-14 | 20374 | Hudson 115 kV conversion | 115 kV conversion | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 381006.42 | 2012-02-29 | 2012-02-29 | Under Construction | 115 |  | A | Y
A in MTEP10 | West | GRE | 2630 | 2009-09-14 | 20383 | Resag Big Fork-Wirt Tap-Jessie Lake Retemp | Resag Big Fork-Wirt Tap-Jessie Lake Retemp | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 1289999 | 2013-04-24 | 2013-04-24 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2631 | 2009-09-14 | 20384 | Resag Deer River-Jessie Lake Retemp | Resag Deer River-Jessie Lake Retemp | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 1339996 | 2013-04-24 | 2013-04-24 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2667 | 2009-09-14 | 20429 | Rush City-Adrian Robinson Rush City Dist Retemp | Rush City-Adrian Robinson Rush City Dist Retemp | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 299001.17 | 2011-09-30 | 2011-09-30 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2670 | 2010-09-15 | 20446 | Schuster Lake 115/41.6 Source | Schuster Lake115/41.6 Source | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 4480714.28 | 2020-04-14 | 2020-04-14 | Planned | 115 | 41.6 | A | Y
A in MTEP10 | West | GRE | 2671 | 2009-09-14 | 20447 | Soderville-Ham Lake-Johnsville (6.18 mi.) Retemp | Soderville-Ham Lake-Johnsville (6.18 mi.) Retemp | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 282809 | 2011-12-30 | 2011-12-30 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2672 | 2009-09-14 | 20448 | Rush City - Bear Creek - Effie Transformer Swap | Rush City - Bear Creek - Effie Transformer Swap | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 500000 | 2011-11-01 | 2012-06-01 | Planned | 230 | 69 | A | Y
A in MTEP10 | West | GRE | 2731 | 2010-09-15 | 20553 | Blomkest (KEPCA) 3.0 mile, 69 kV line | Blomkest (KEPCA) 7.0 mile, 69 kV line | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 1140342.35 | 2012-09-03 | 2012-09-03 | Planned | 69 |  | A | Y
A in MTEP10 | West | GRE | 2833 | 2009-09-04 | 20568 | Lake Caroline | Lake Caroline (WH) 69 kV Distribution Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 675000 | 2013-10-21 | 2013-10-21 | Planned | 69 |  | A | NT
A in MTEP10 | West | GRE | 2834 | 2009-09-04 | 20602 | Rice Lake | Rice Lake (MKR) 69 kV Distribution Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 5138000 | 2013-09-10 | 2013-09-10 | Planned | 69 |  | A | NT
A in MTEP10 | West | GRE | 3106 | 2009-12-29 | 20595 | Tamarac MISO Interconnection (G619) | Tamarac-Cormorant Junction | MN |  | 2010-12-02 | GIP | Shared |  | 728000 | 2012-09-03 | 2012-09-03 | Planned | 115 |  | A | Y
A in MTEP09 | West | GRE | 2562 | 2010-04-05 | 20378 | G362 - Pleasant Valley 345/161 KV transformer | G362 Network Upgrades: Pleasant Valley 345/161 kV transformer (GRE part of G362) | MN |  | 2009-12-04 | GIP | Shared |  | 1006364.75 | 2012-03-30 | 2012-03-30 | Planned |  | 161 | A | Y
A in MTEP09 | West | GRE | 2563 | 2010-04-05 | 20555 | Athens to Martin Lake 69kV System Upgrades and Permitting | Athens to Martin Lake 69kV System Upgrades and Permitting | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 6234719.2725 | 2012-11-30 | 2012-11-30 | Planned | 69 |  | A | NT
A in MTEP05 | West | GRE | 599 | 2010-04-05 | 20152 | Crooked Lake - Enterprise Park 115 kV line | Crooked Lake - Enterprise Park 115 kV line | MN |  | 2005-06-16 | Other | Excluded |  | 8616068.62 | 2013-06-01 | 2013-06-01 | Planned | 115 |  | A | Y
A in MTEP08 | West | GRE, OTP | 1033 | 2010-04-05 | 20395 | Silver Lake 230/41.6 kV transformer | Silver Lake 230/41.6 kV transformer | MN |  | 2008-12-04 | Other | Not Shared | Reliability | 3230626 | 2011-10-28 | 2011-10-28 | Under Construction | 230 | 41.6 | A | Y
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | AlexSS-St.Cloud-Monticello | Fargo, ND - St Cloud/Monticello, MN area 345 kV project | Bison - AlexandriaSS - Waite Park - Monticello 345 ckt 1, Sum rate 2085 | MN | ND | 2008-12-04 | BaseRel | Shared |  | 564747000 | 2011-12-15 | 2015-03-31 | Planned | 345 | 115 | A | Y
A in MTEP10 | West | ITCM | 3046 | 2009-09-14 | SW CR 69kV Upgrade | SW Cedar Rapids 69kV System Upgrade (Phase 1) Near ADM | Re-route 69kV lines near the load to connect to the 161/69kV transformer at the Beverly substation. Install two breaker terminals and a main breaker to connect the re-routed lines. This adds significant capacity to the 69kV system with minimal line construction and no new transformer purchases. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 1800000 | 2012-12-31 | 2012-12-31 | Planned | 69 |  | A | Y
A in MTEP10 | West | ITCM | 3047 | 2009-09-14 | IA Falls Ind TRF | IA Falls Industrial TRF | Upgrade the IA Falls Ind 115/69kV TRF with a dual high side (161-115kV)/69kV TRF. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 1980000 | 2011-08-30 | 2011-08-30 | Planned | 161 | 69 | A | Y
A in MTEP10 | West | ITCM | 3048 | 2009-09-14 | Jeff-Perlee | Jefferson Co-Perlee 69kV Rebuild | Rebuild the Jefferson Co-Perlee 69kV line section. | IA |  | 2010-12-02 | Other | Not Shared | Condition | 2700000 | 2013-12-31 | 2013-12-31 | Planned | 69 | 69 | A | Y
A in MTEP10 | West | ITCM | 3049 | 2009-09-14 | Huxley Terminal | Huxley Industrial Park Terminal Addition | Add a 161kV line terminal to tie to the rerouted Boone Jct-Huxley Park Ind 161kV line. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 750000 | 2012-12-31 | 2012-12-31 | Planned | 161 | 161 | A | Y
A in MTEP10 | West | ITCM | 3050 | 2009-09-14 | Alden-Buckeye dist. | Alden-Buckeye dist. Sub tap | Constuct a new 3 mile 69kV tap to the new Alden-Buckeye dist. Sub from the CBPC Alden sub site. | IA |  | 2010-12-02 | Other | Not Shared | Distribution | 1080000 | 2011-12-31 | 2011-12-31 | Planned | 69 | 69 | A | Y
A in MTEP10 | West | ITCM | 3052 | 2009-09-14 | Wash Sub | Washington 69kV Upgrades | Replace 69kV bus, 2 breakers, relays, and improve breaker configuration, add bus tie breaker, and install a new control building. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 2400000 | 2011-12-31 | 2011-12-31 | Planned | 69 | 69 | A | Y
A in MTEP10 | West | ITCM | 3053 | 2010-06-28 | Keokuk-Carbide | Keokuk Hydro-Carbide 69kV Dbl Ckt | Build a new 69kV circuit from Keokuk Hydro-Carbide. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 3240000 | 2013-12-31 | 2013-12-31 | Planned | 69 | 69 | A | Y
A in MTEP10 | West | ITCM | 3054 | 2009-09-14 | Swisher SS | Swisher Breaker Station | Construct a new 3 terminal breaker station. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 2152000 | 2011-12-31 | 2011-12-31 | Planned | 69 | 69 | A | Y
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | Cedar Rapids 34kV Conversion Plan | ITCM, working with IP & L, has formed a plan to better serve Cedar Rapids load with new larger, 2-transformer substations that will allow retirement of the 4kV system along with several other small distribution substations. Most of these new substations will be served from a new 69 kV and 161 kV Cedar Rapids transmission system that will use the existing 34.5 kV system right-of-way. This will allow retirement of several existing 34.5kV lines while shifting distribution load to a higher voltage to allow better normal and contingency performance. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 24760000 | 2011-12-31 | 2014-12-31 | Planned | 161 | 69 | A | Y
A in MTEP10 | West | ITCM | 3056 | 2009-09-14 | Grundy-Hicks 34kV | Grundy Center-Reinbeck-Hicks tap 69kV line. | Construct a 16 mile 69kV line between Grundy Center and the Hicks tap 69kV line. Constructing this line will allow consolidation of the Dike and Morrison substations into a single new distribution substation and will allow retirement of more than 30 miles of 50 year old 34.5kV line. | IA |  | 2010-12-02 | Other | Not Shared | Distribution | 5760000 | 2012-12-31 | 2012-12-31 | Planned | 69 | 69 | A | Y
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | West Branch 34kV Load Shift Projects | Construct 69kV taps for the Moscow & New Liberty dist. Subs | IA |  | 2010-12-02 | Other | Not Shared | Distribution | 2505000 | 2013-12-31 | 2013-12-31 | Planned | 69 | 34 | A | Y
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | Vinton-Hazleton 34kV Conversion Plan | The plan includes rebuilding a line between Dundee and Vinton substations and converting this line to 69 kV operation. In order to operate this line at 69 kV a 161/69 kV transformer will need to be installed at Vinton. Also, an approximatley 6 mile line will be built to connect the Hazleton source to the Dundee - Vinton line. This plan also includes rebuilding a line between Coggon and Hiawatha substations and converting this line to 69 kV operation. A 161/69 kV transformer will need to be installed at Coggon. | IA |  | 2010-12-02 | Other | Not Shared | Distribution | 21988000 | 2011-12-31 | 2013-12-31 | Planned | 161 | 69 | A | Y
A in MTEP10 | West | ITCM | 3059 | 2009-09-14 | WB &WL SS | West Branch & West Liberty Switch Stations | Construct two new 3 terminal 69kV breaker stations at West Branch and at West Liberty. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 3120000 | 2011-12-31 | 2011-12-31 | Planned | 69 | 69 | A | Y
A in MTEP09 | West | ITCM | 2339 | 2008-12-01 | ITCM-08-009 | G612-Marshalltown-Boone 115kV to 161kV | Construct a new Story Co 161kV switching station and rebuild the Marshalltown-Boone 115kV to 161kV. | IA |  | 2009-12-04 | GIP | Shared |  | 13720000 | 2011-09-30 | 2012-05-30 | Planned | 161 |  | A | Y
A in MTEP09 | West | ITCM | 2340 | 2008-12-16 | ITCM-08-006 | Grand Junction-Paton REC tap 34kV Rebuild | Rebuild the 34kV line from Grand Jct-Paton REC tap to 69kV. Retire Dana 34kV/dist sub and construct in & out taps for new Grand Jct North 69kV/dist. Sub. (still operate at 34kV) | IA |  | 2009-12-04 | Other | Not Shared | Condition | 1103527 | 2011-12-31 | 2011-12-31 | Planned | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2341 | 2009-04-01 | ITCM-08-014 | Monticello-Amber Conversion & Lovell REC Rebuild | Rebuild 8.5 miles Monticello-Amber 34kV to 69kV, add 69kV bkr at Sand Springs, Monticello Industrial, & Amber. Operate Sand Springs-Amber at 69kV. Also rebuild 2.21 miles of 34kV to 69kV east of Lovell REC but continue operation of this portion at 34kV in 2009. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 3775000 | 2011-09-01 | 2011-10-30 | Under Construction | 69 |  | A | NT
A in MTEP09 | West | ITCM | 2342 | 2009-09-25 | ITCM-08-019 | Boone-Jewell 34kV Rebuild | Rebuild 25.3 miles of 34kV line from Jewell to approximately 6 miles south of the Ridgeport dist. substation to 69kV standards. This line will continue to be operated at 34kV. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 6685000 | 2011-12-31 | 2011-12-31 | Under Construction | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | West Branch-West Liberty 34kV Rebuild | Rebuild 15.1 miles of 34kV line from West Branch-West Liberty to 69kV standards. This line will continue to be operated at 34kV. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 4146850 | 2011-12-31 | 2011-12-31 | Planned | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2344 | 2009-04-01 | ITCM-08-022 | Wyoming-Massillon 34kV Rebuild | Rebuild 12 miles of 34kV line from Wyoming-Massilon to 69kV standards. This line will continue to be operated at 34kV. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 4020000 | 2012-12-31 | 2012-12-31 | Planned | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | Eldora Area Rebuild & Breaker Station | Rebuild approx 20 miles of 34kV to 69kV from the Hubbard Rural sub to a new 4-terminal Eldora North 69kV switching station and operate at 69kV. The new switching station will tap the CBPC Pleaseant-CBPC Eldora 69kV line. The 4th terminal will be needed in the near future to feed the Eldora North-Union-Conrad 69kV line after substaitons are ready for conversion. This line will be rebuilt to 69kV standard in 2009. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 16511000 | 2012-12-31 | 2012-12-31 | Under Construction | 69 |  | A | NT
A in MTEP09 | West | ITCM | 2348 | 2009-09-25 | ITCM-08-025 | Beaver Rock 69kV Switching Station | Construct a new 3-terminal 69kV switching station along the Beaver Channel-Rock Creek 69kV line. | IA |  | 2009-12-04 | Other | Not Shared | Reliability | 1593178 | 2011-12-31 | 2011-12-31 | Under Construction | 69 |  | A | NT
A in MTEP09 | West | ITCM | 2353 | 2009-09-25 | ITCM-08-031 | Big River 69kV 3-terminal Switching Station | Construct a new 3-terminal 69kV switching station where the Big River REC line taps the Agency-Sawyer 69kV line. | IA |  | 2009-12-04 | Other | Not Shared | Reliability | 1666427 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | A | NT
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | Hazleton-Fairbank REC 69kV line & breaker station | Construt a 69kV Hazleton-Fairbank line and a new 3-terminal 69kV switching station. | IA |  | 2009-12-04 | Other | Not Shared | Distribution | 5731385 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | A | NT
A in MTEP09 | West | ITCM | 2358 | 2008-12-01 | 0011-01 | Hazleton-Blackhawk 161kV Rebuild | Rebuild 12 miles of the Hazleton-Blackhawk 161kV line (ITC owned portion) | IA |  | 2009-12-04 | BaseRel | Shared |  | 5400000 | 2013-12-31 | 2013-12-31 | Planned | 161 |  | A | Y
A in MTEP09 | West | ITCM | 2363 | 2010-06-28 | 0045-01 | Glenworth 161/69kV (Glenville Area) | Construct a new 161/69kV 100 MVA substation tapping the Hayward-Worth County 161 kV line. ITC will construct the 161kV portion including the TRF and low side protection. DPC will construct the 69kV portion. | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 7240605 | 2011-08-30 | 2011-08-30 | Under Construction | 161 | 69 | A | Y
A in MTEP09 | West | ITCM | 2364 | 2009-04-01 | 0046-01 | Thompson 2 mile 69kV dbl ckt | Rebuild 69kV double circuit line near Thompson, IA | IA |  | 2009-12-04 | Other | Not Shared | Reliability | 460000 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | A | NT
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | Anita Area 34kV to 69kV Rebuilds | Rebuild 5 miles from the Anita-Exira REC to 69kV. Also rebuild 4.7 miles of the Anita to th e Anita-Wiota Joint sub. Rebuild 21.9 miles from Thompson- Redfield. These lines will continue to opeate at 34kV. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 7895000 | 2013-12-31 | 2013-12-31 | Planned | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | Fairfax-Williamsburg 34kV to 69kV Rebuilds | Rebuild 26.6 miles of 34kV line from the Fairfax sub to the Williamsburg115kV sub to 69kV. These lines will continue to opeate at 34kV. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 6903000 | 2013-12-31 | 2013-12-31 | Planned | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2370 | 2009-09-25 | ITCM-08-007 | Andrew Tap & Monmouth Rebuilds | Rebuild the 5.75 mile Andrew Tap & 2 miles of line in the Monmouth area. These lines will continue to opeate at 34kV. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 1869250 | 2011-12-31 | 2011-12-31 | Planned | 34 |  | A | NT
A in MTEP09 | West | ITCM | 2371 | 2009-09-25 | ITCM-08-041 | New Marengo 69kV Switching Station | Construct a new 3-terminal 69kV switching station at the existing Marengo 34kV sub. | IA |  | 2009-12-04 | Other | Not Shared | Condition | 1900000 | 2013-12-31 | 2013-12-31 | Planned | 69 |  | A | NT
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | Hazleton - Salem 345 kV line with a 2nd Salem 345/161 kV 448 MVA transformer. | Build a new Hazleton - Salem 345 kV line. Expand the Hazleton 345kV bus to a 5 position ring and expand the Salem 345kV ring to allow for a 2nd Salem 345/161 kV 448 MVA transformer. (option 1) The route will follow the existing Hazleton-Dundee-Liberty-Lore 161kV route. | IA |  | 2008-12-04 | Other | Not Shared |  | 119010000 | 2012-12-31 | 2012-12-31 | Planned | 345 | 161 | A | Y
A in MTEP08 | West | ITCM | 1618 | 2009-09-25 | 446HRLK | Hrn Lk-Lkfld 161kV Ckt 1 Rbld | Rebuild Heron Lake-Lakefield 161kV line, sum rate 446 MVA | MN |  | 2008-12-04 | BaseRel | Shared |  | 14000000 | 2013-06-01 | 2013-06-01 | Planned | 161 |  | A | Y
A in MTEP08 | West | ITCM | 1619 | 2009-09-25 | 333906GMnd | Grnd Mnd 161-69kV 2nd Xfmr & 161kV loop | Install a 2nd Grand Mound 161-69kV Xfmr (75 MVA) & build a 2.0 miles of new line from the Grand Mound sub to tap the E. Calamus-Maquoketa line (approx. 87% from Maq-E.Cal). The E. Calamus-new tap portion of line will be retired. Existing E.Cal-Maq bkr will feed to GMnd and a new GMnd bkr will feed to Maq. The three terminal line at E.Calamus will be eliminated. | IA |  | 2008-12-04 | Other | Not Shared | Reliability |  | 2011-12-31 | 2011-12-31 | Planned | 161 |  | A | Y
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | Marshalltown-Franklin 115kV conversion to 161kV. | Rebuild Marshalltown-Wellsburg-Eldora-Iowa Falls Industrial-Iowa Falls-Franklin 115kV to 161kV. This will also convert the Wellsburg, Eldora, Iowa Falls Industrial, and Iowa Falls substations to 161kV operation on the high side. The 161-115kV source at Franklin will be eliminated. | IA |  | 2008-12-04 | Other | Not Shared |  | 21580000 | 2011-08-30 | 2013-12-31 | Planned | 161 | 34 | A | Y
A in MTEP08 | West | ITCM | 1645 | 2009-09-25 | LeonCap | Leon 7.2 MVAR Cap Bank | Install a 69kV 7.2 MVAR cap bank at the Leon substation. | IA |  | 2008-12-04 | Other | Not Shared | Reliability | 2511808 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | A | NT
A in MTEP08 | West | ITCM | 1744 | 2009-09-25 | GM-MAQ | Maquoketa-Grand Mound 161kV Reconductor | Reconductor 161kV from Maquoketa to Grand Mound (old East Calamus-Maquoketa 161kV line) | IA |  | 2008-12-04 | BaseRel | Not Shared |  | 10150000 | 2016-12-31 | 2016-12-31 | Planned | 161 |  | A | Y
A in MTEP08 | West | ITCM | 1747 | 2009-09-25 | WORTH | Elk 161/69kV upgrades | Upgrade both Elk 161/69kV transformers and add a 161kV BKR between the new units. A 161kV breaker will be added looking toward Brewster | MN |  | 2008-12-04 | Other | Not Shared | Reliability | 6998396 | 2011-05-31 | 2011-12-31 | Under Construction | 161 | 69 | A | Y
A in MTEP08 | West | ITCM | 2108 | 2009-09-25 | G358 | G358-Fairbault County | Network upgrades for tariff service request | MN |  | 2008-12-04 | GIP | Shared |  | 4216848 | 2011-10-31 | 2011-10-31 | Planned | 161 | 34.5 | A | Y
A in MTEP06 | West | ITCM | 1289 | 2009-04-01 | 11 | Marshalltown - Toledo - Belle Plaine - Stoney Point 115 kV line rebuild | Marshalltown - Toledo - Belle Plaine - Stoney Point 115 kV line will be rebuilt/upgraded between 2008 and 2011 | IA |  | 2007-02-15 | Other | Not Shared |  | 13653000 | 2012-03-30 | 2013-12-31 | Planned | 161 |  | A | Y
A in MTEP06 | West | ITCM | 1342 | 2009-04-01 | 3 | Lewis Fields 161 kV substation which taps the SwampFX - Coggon 115 kV line | Build a new 161 kV substation Lewis Fields to be tapped to the 115 kV line Swamp Fox - Coggon at 5% distance via a new 161/115 kV transformer. Also build a new 161 kV line from Hiawatha to Lewis Fields | IA |  | 2007-02-15 | BaseRel | Not Shared |  | 21051600 | 2014-12-31 | 2014-12-31 | Planned | 161 | 115 | A | Y
A in MTEP06 | West | ITCM | 1344 | 2009-09-25 | 5 | Build a new 345 kV Morgan Valley (Beverly) substation which taps the Arnold -Tiffin 345 kV line | Build a new 345 kV Morgan Valley (Beverly) Tap substation and tapped to 345 kV line Arnold -Tiffin at 40% distance away from Arnold. Add a new 335 MVA 345/161 kV transformer and build a new 161 kV line connecting the new substation to Beverly 161 kV bus. Tap Arnold-Fairfax 161kV line for in and out feeds from Morgan Valley | IA |  | 2007-02-15 | Other | Not Shared |  | 14580000 | 2014-12-31 | 2014-12-31 | Planned | 345 | 161 | A | Y
A in MTEP09 | West | MDU | 1355 | 2006-10-15 |  | Heskett - Additional 230/115 kV Switchyard and 115 kV Capacitor | Heskett - Additional 230/115 kV Switchyard 230 115 Switchyard in parallel w/ existing Heskett switchyard and Cap Bank | ND |  | 2009-12-04 | BaseRel | Shared |  | 11000000 | 2011-09-30 | 2014-12-31 | Planned | 230 | 115 | A | Y
A in MTEP10 | west | MP | 2547 | 2009-12-08 | Essar | Essar | Essar project adds a 95 MW new mine and taconite plant load in fall 2011 with 50 MW DRI facility fall of 2012 total demand to 145 MW. Future load additions could increase total demand to 300 MW | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 34100000 | 2012-06-30 | 2014-07-30 | Planned | 230 | 14 | A | Y
A in MTEP10 | West | MP | 2761 | 2009-11-13 | Dunka Rd | Polymet | add new 138/14 kV substaion off MP 138 KV Line #1 | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 3000000 | 2012-12-30 | 2012-12-30 | Planned | 115 | 14 | A | Y
A in MTEP10 | West | MP | 2762 | 2009-11-13 | Airpark | Airpark | New 115/34.5 and 115/14 kV Substation | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 4105000 | 2012-12-16 | 2013-06-30 | Under Construction | 115 | 14 | A | Y
A in MTEP10 | West | MP | 3091 | 2009-12-08 | 28L reroute | 28L reroute | MP’s 115 kV Line #28 (28L) must be moved as it crosses the area that Essar will be mining. | MN |  | 2010-12-02 | Other | Not Shared | Relocation | 3190000 | 2012-05-30 | 2012-05-30 | planned | 115 |  | A | Y
A in MTEP09 | West | MP | 2552 | 2009-11-13 | Skibo | Skibo | Skibo-Hoyt Lakes 138 ckt 1, Sum rate 202 | MN |  | 2009-12-04 | BaseRel | Not Shared |  | 2540000 | 2012-12-01 | 2012-12-01 | Proposed | 138 |  | A | Y
A in MTEP09 | West | MP | 2759 | 2009-11-13 | Laskin | Laskin | Move Virginia 115/46 kV Transformer to Laskin | MN |  | 2009-12-04 | Other | Not Shared | Distribution | 500000 | 2012-06-01 | 2012-06-01 | Planned | 115 | 46 | A | Y
A in MTEP09 | West | MP | 2763 | 2009-11-13 | LSPI | LSPI 34.5 | Add 115/34.5 kV Transformer and line exit to LSPI 115/14 kV Sub | MN |  | 2009-12-04 | Other | Not Shared | Distribution | 600000 | 2011-08-30 | 2011-08-30 | Under Construction | 115 | 34.5 | A | Y
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | G519 - Mesaba | Network Upgrades associated with 600 MW coal gasification generating facility at the propsoed Mesaba generating station. There is a G477 alternate site which is not described here. | MN |  | 2007-12-13 | GIP | Shared |  | 76319541 | 2012-07-01 | 2012-07-01 | Planned | 230 | 115 | A | Y
A in MTEP05 | West | MP, GRE | 600 | 2010-04-05 | 20113 | Baxter - Southdale 115 kV line | Southdale-Scearcyville 115 kV line | MN |  | 2005-06-16 | Other | Excluded |  | 8045969.38 | 2012-02-28 | 2012-06-01 | Under Construction | 115 |  | A | Y
A in MTEP06 | West | MPC, XEL, OTP, MP | 279 | 2008-10-01 | Bemidji-Grand Rapids | Bemidji-Grand Rapids 230 kV Line | Boswell - Wilton 230 ckt 1, Sum rate 495, Addition of a 187 MVA 230/115 kV transformer at Cass Lake | MN |  | 2007-02-15 | BaseRel | Shared |  | 98530747 | 2012-12-31 | 2012-12-31 | Planned | 230 |  | A | Y
A in MTEP10 | West | MPW | 2934 | 2010-09-21 | MPW-SS | Replace South 161/69 kV Transformer | Replace the existing 161/69 kV, 75 MVA transformer at South Sub with at least a 134 MVA transformer by 2011 (633301-633501). Also the 161 kV bus at South Sub will become a ring bus, splitting the three terminal 161 kV line into two sections between 633209 MPW Unit 9 – 633301 MPW South Sub and 633301 MPW South Sub – 636670 MEC Sub 18. | IA |  | 2010-12-02 | Other | Not Shared | Reliability | 5400000 | 2014-06-01 | 2014-06-01 | Planned | 161 | 69 | A | Y
A in MTEP10 | West | NWE | 3092 | 2009-11-16 | 2012-02 | Webb Lake 69KV line | Rebuild 34.5KV line to Webb Lake at 69KV with horizontal post construction and #4/0 ACSR | WI |  | 2010-12-02 | Other | Not shared | Condition | 425000 | 2011-06-01 | 2011-06-01 | Planned | 69 |  | A | Y
A in MTEP08 | West | NWE | 2011 | 2009-11-16 | 2009-03 | Frederic-Lewis 34.5KV Rebuild | Rebuild the 34.5Kv system between Frederic and Lewis sub at 69KV with 477ASCR and horizontal post construction. | WI |  | 2008-12-04 | Other | Not Shared |  | 350000 | 2011-06-01 | 2011-06-01 | Planned | 69 |  | A | Y
A in MTEP08 | West | NWE | 2012 | 2009-11-16 | 2010-01 | Falun-Penta 34.5KV Rebuild | Rebuild the 34.5Kv system between Falun and Penta sub at 69KV with 477ASCR and horizontal post construction. | WI |  | 2008-12-04 | Other | Not Shared |  | 538000 | 2011-09-01 | 2011-09-01 | Under Construction | 69 |  | A | Y
A in MTEP08 | West | NWE | 2013 | 2009-11-16 | 2010-02 | Penta-Siren Tap 34.5KV Rebuild | Rebuild the 34.5Kv system between Penta sub and Siren Tap at 69KV with 477ASCR and horizontal post construction. | WI |  | 2008-12-04 | Other | Not Shared |  | 175000 | 2011-06-01 | 2011-06-01 | Planned | 69 |  | A | Y
A in MTEP08 | West | NWE | 2016 | 2009-11-16 | 2011-02 | Frederic-Coffee Cup 69KV reconductor | Reconductor 69KV line with 477ACSR | WI |  | 2008-12-04 | Other | Not Shared |  | 100000 | 2012-01-01 | 2012-01-01 | Planned | 69 |  | A | Y
A in MTEP08 | West | NWE | 2018 | 2009-11-16 | 2012-01 | Balsam Lake-Centuria 69KV line | Build new 69KV line to Centuria and build Distribution Sub | WI |  | 2008-12-04 | Other | Not Shared |  | 1200000 | 2011-06-01 | 2011-06-01 | Planned | 69 | 12.47 | A | Y
A in MTEP10 | West | OTP | 3156 | 2010-04-05 | Cass Lake -Nary-Helga -Bemidji 115 | Cass Lake -Nary-Helga -Bemidji 115 |  | MN |  | 2010-12-02 | BaseRel | Shared |  | 10399000 | 2012-12-31 | 2013-12-31 | Planned | 230 | 115 | A | Y
A in MTEP09 | West | OTP | 2751 | 2009-11-18 |  | New Perham 115/12.5 kV Substation | Build New 115/12.5 kV Substation at Perham to Serve as a Back-up Source for Outage of Primary Source | MN |  | 2009-12-04 | Other | Not Shared | Distribution | 400000 | 2013-12-31 | 2013-12-31 | Planned | 115 | 12.5 | A | Y
A in MTEP10 | West | OTP, MPC | 2826 | 2010-04-05 | OTP1 | Enbridge Load Expansion Support | Install Capacitor Bank on 115 kV at Clearbrook, MN. One 34 MVAR. Install Capacitor Bank on 115 kV at Karlstad. One 14 MVAR. Install Capacitor Bank on 115 kV at Thief River Falls. One 15 MVAR. | ND |  | 2010-12-02 | BaseRel | Not Shared |  | 1900000 | 2012-12-31 | 2015-12-31 | Planned | 115 |  | A | Y
A in MTEP10 | West | SMP | 2166 | 2011-02-25 | StPet-UP | City of St Peter, MN load serving upgrades | Adding approx 7.0 mimles of new 69kV transmission line and a new load serving substation (Estimated in service June 2011) | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 6000000 | 2011-12-01 | 2011-12-01 | Under Construction | 69 | 69 | A | NT
A in MTEP10 | West | SMP | 2167 | 2011-02-25 | Red-UP | City of Redwood Falls, MN load serving upgrades | Adding approx 5.2 miles of new 115kV transmission line and a new load serving substation (Estimated in service Dec 2011) | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 4000000 | 2011-12-01 | 2011-12-01 | Planned | 115 | 115 | A | NT
A in MTEP10 | West | SMP | 2171 | 2009-11-13 | Mora-WE | Mora Land Fill Gas Generator | Addition of 3 MW landfill gas generation and construction of approx 7.0 miles of 12.47kV distrbution line. | MN |  | 2010-12-02 | TDSP | Direct Assigned |  | 3700000 | 2011-08-01 | 2011-08-01 | Under Construction | 12.47 |  | A | Y
A in MTEP10 | West | XEL | 2767 | 2009-12-09 |  | Fenton 115/69 kV Interconnection | This project is to install a new 115/69 kV transformer at Fenton substation. Break the existing 69 kV line between Chandler Tap and Lake Wilson to create an in and out to the Fenton substation. | MN |  | 2010-12-02 | Other | Not Shared | Reliability | 3710000 | 2012-01-01 | 2012-01-01 | Planned | 115 | 69 | A | Y
A in MTEP10 | West | XEL | 3097 | 2011-01-11 |  | Monroe County 2nd Transformer | Install second 161/69 kV 70 MVA transformer at Monroe County substation | WI |  | 2010-12-02 | Other | Not Shared | Reliability | 3680000 | 2012-06-01 | 2012-06-01 | Planned | 161 | 69 | A | Y
A in MTEP10 | West | XEL | 3100 | 2009-11-19 |  | Westgate 115/69 kV TR upgrade | Upgrade Westgate 115/69 kV transformer #2 to 70 MVA | MN |  | 2010-12-02 | Other | Not Shared | Distribution | 2070000 | 2012-06-01 | 2012-06-01 | Planned | 115 | 69 | A | Y
A in MTEP09 | West | XEL | 2156 | 2008-04-07 | N Mankato | North Mankato 115 kV project | 1) New 345/115 kV TR at the proposed Helena 345 kV switching station. 2) New 115 kV line from Helena - St. Thomas. 3) New 115/69 kV substation near St. Thomas. 4) New 69 kV switchig station at Lesueur Tap. | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 17450000 | 2011-06-01 | 2011-06-01 | Planned | 345 | 69 | A | Y
A in MTEP09 | West | XEL | 2157 | 2008-04-07 |  | Douglas Co 2nd TR | 2nd Douglas Co 115/69 kV transfromer | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 4435000 | 2011-11-01 | 2011-11-01 | Planned | 115 | 69 | A | NT
A in MTEP09 | West | XEL | 2158 | 2008-04-07 |  | Upgrade Sauk Center - Osakis 69 kV line | Upgrade Sauk Center - Osakis 69 kV line to a lower impedance. | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 4514000 | 2011-09-30 | 2011-09-30 | Planned | 69 |  | A | NT
A in MTEP09 | West | XEL | 2160 | 2008-04-07 |  | Park Falls TR upgrade | Upgrade the Park Falls 115/34.5 kV TR to 47 MVA | WI |  | 2009-12-04 | Other | Not Shared | Reliability | 3355800 | 2012-06-01 | 2012-06-01 | Planned | 115 | 34.5 | A | NT
A in MTEP09 | West | XEL | 2178 | 2008-07-15 | RIGO | G362 Pleasant Valley XEL | G362 Network upgrades: New 161 kV line from Pleasant Valley - Byron 161 kV line | MN |  | 2009-12-04 | GIP | Shared |  | 10007181 | 2011-12-01 | 2012-06-01 | Planned | 161 |  | A | Y
A in MTEP09 | West | XEL | 2307 | 2008-10-01 |  | St. Cloud Loop | (1) New 4 mile 115 kV line from St. Cloud tap tap to Mayhew Lake substation.(2) Convert Benton Co - St. Cloud double circuit to bifurcated line and reterminarte into Mayhew Lake substation (3) Convert St. Cloud tap to Granite City into bifurcated line (this results in single 115 kV circuit from St. Cloud to Granite City). | MN |  | 2009-12-04 | BaseRel | Shared |  | 6100000 | 2012-06-01 | 2012-06-01 | Planned | 115 |  | A | Y
A in MTEP09 | West | XEL | 2308 | 2008-10-01 |  | Grove Lake - Glenwood line rebuild | This project is to rebuild 13 miles of 69 kV line from Grove Lake switching station to Glenwood to 477 ACSR | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 16350812 | 2011-09-01 | 2011-09-01 | Planned | 69 |  | A | NT
A in MTEP09 | West | XEL | 2309 | 2009-05-11 |  | Maple Lake - Watkins line rebuild | This project is to rebuild 20 miles of 69 kV line from Maple Lake to Watkins in west Central Minnesota | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 2487000 | 2012-06-01 | 2012-06-01 | Planned | 69 |  | A | NT
A in MTEP09 | West | XEL | 2772 | 2009-02-10 | South Minneapolis | South Minneapolis | New 115 kV distribution substation with four terminations tapping the Elliot Park - Southtown line, 1.25 new miles of double circuit 795 SAC to a new 115 kV distribution sustation | MN |  | 2009-12-04 | Other | Not Shared | Distribution | 26890000 | 2012-06-01 | 2012-06-01 | Planned | 115 | 13.8 | A | Y
A in MTEP08 | West | XEL | 675 | 2008-06-30 |  | Rebuild Westgate to Scott County 69 kV to 115 kV | Upgrade 20.1 miles Westgate-Deephaven-Excelsior-Scott County 69kV to 115 kV using 795 ACSS conductor, Upgrade 2 miles Westgate-Eden Prairie 115kV #1 and #2 to 400MVA (PrjID 606), Substation work at Deephaven, Excelsior and Scott County. | MN |  | 2008-12-04 | Other | Not Shared |  | 14000000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | A | Y
A in MTEP08 | West | XEL | 1487 | 2006-10-15 |  | Somerset - Stanton 69 kV line 84 MVA | Construct 7 miles of 69 kV line using 477 SSAC conductor traveling north along 210th Avenue, interconnecting with a new stanton 69 kV substion on the Clear Lake - New Richmond 69 kV line and the New Summerset substation on the DPC Roberts - St. Criox Falls 69 kV line | WI |  | 2008-12-04 | Other | Not Shared | Reliability | 9247500 | 2011-12-31 | 2011-12-31 | Planned | 69 |  | A | NT
A in MTEP08 | West | XEL | 1549 | 2007-04-10 | Eau Claire - Hydro Lane 161 kV Conversion | Eau Claire - Hydro Lane 161 kV Conversion | 1.)Eau Claire 161 kV circuit breaker. 2.Bring Wheaton-Presto Tap 161 kV line into Eau Claire substation. 3.) Reconductor Wheaton to Eau Claire 161 kV line to 795 ACS. 4.) Construct second circuit from Wheaton Tap to Wheaton substation. 5.New 50th Avenue substation near where Red Cedar to Wissota 161 kV line intersects 69 kV corridor from Eau Claire to Chippewa Falls. Construct a 4 breaker 161 kV ring bus, add two 161-69 kV transformers with at least 60 MVA capacity. Construct a strait bus 69 kV with a bus tie breaker between the transformers. 6.) Where the 161 kV line from Eau Claire to Presto crosses the double-circuit 69 kV line to Hallie, tap the 161 kV line and convert the 69 kV lines to one 161 kV line with 795 ASCC conductor up to the new 50th Ave substation. 7.)Convert Hallie Substation from 69 kV to 161 kV operation. | WI |  | 2008-12-04 | Other | Not Shared | Reliability | 3070000 | 2011-09-01 | 2011-12-01 | Planned | 161 |  | A | Y
A in MTEP08 | West | XEL | 1957 | 2008-01-10 | ECP2 | New 161/69 kV Sub SW of Eau Claire where Alma – Elk Mound 161 kV intersects Shawtown – Naples 69 kV line. Rebuild 69 kV London/Madison to new substation. New 69 kV from new substation - DPC Union Sub. New 69 kV to DPC Brunswick Sub | New 161/69 kV Substation southwest of Eau Claire where Alma – Elk Mound 161 kV line intersects with Shawtown – Naples 69 kV line. Rebuild 69 kV line from London/Madison Tap to new substation. Construct 69 kV line from new substation to DPC Union Substation. Construct 69 kV line from new substation to DPC Brunswick Substation | WI |  | 2008-12-04 | Other | Not Shared | Reliability | 7080000 | 2012-06-01 | 2012-06-01 | Planned | 161 | 69 | A | Y
A in MTEP08 | West | XEL | 1958 | 2008-01-10 | NWWLS | Stone Lake-Edgewater 161 kV line. A new radial 161 kV line and substation in Sawyer County, Wisconsin | Expand 161 kV ring bus at Stone Lake to accept new line termination. Construct 161 kV line from Stone Lake to Couderay Substation. Install 161/69 kV transformer at Couderay Substation. Install the following substation equipment at Couderay: -161 kV MOD -69 kV low-side transformer breaker -69 kV line breaker | WI |  | 2008-12-04 | Other | Not Shared | Reliability | 26185641 | 2012-12-01 | 2012-12-01 | Planned | 161 |  | A | Y
A in MTEP06 | West | XEL | 1458 | 2009-05-11 | G349 | G349, 37774-01. Upgrades for G349 | G349 Upgrades: Yankee substation, Brookings Co 345/115 substation, Hazel Run 53 Mvar capacitor, Brookings-Yankee 115 kV line | MN |  | 2007-02-15 | GIP | Shared |  | 2202000 | 2011-11-30 | 2011-11-30 | Planned | 34.5 |  | A | Y
A in MTEP09 | West | XEL, GRE | 1952 | 2008-01-10 |  | Plato capacitor bank | 'This project is to add a 10 MVAR cap bank at Plato. This project is required to convert the existing 69 kv line from Young America - Glencoe to 115 kV (part of Glencoe - West Waconia 115 kV line project). | MN |  | 2009-12-04 | Other | Not Shared | Reliability | 700000 | 2011-12-01 | 2011-12-01 | Planned | 69 |  | A | NT
A in MTEP08 | West | XEL, SMP, Non-MISO | 1024 | 2007-05-22 | SE TC-Roch-N. Lacrosse | SE Twin Cities - Rochester, MN - LaCrosse, WI 345 kV project | Construct Hampton Corner-North Rochester-Chester-North LaCrosse 345 kV line, North Rochester - N. Hills 161 kV line, North Rochester-Chester 161 kV line, Hampton Corner 345/161 transformer, North Rochester 354/161 transformer, North LaCrosse 345/161 transformer | MN | WI | 2008-12-04 | BaseRel | Shared |  | 444999999 | 2012-12-15 | 2015-09-30 | Planned | 345 | 161 | A | Y
B | Central | AmerenIL | 1234 | 2008-02-14 |  | Havana, South-Mason City, West 138 kV | Increase ground clearance on 18.4 miles | IL |  |  | BaseRel |  |  | 642300 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | B | Y
B | Central | AmerenIL | 1533 | 2008-02-14 |  | Washington Street-S. Bloomington - Upgrade Terminal Equipment | Replace terminal equipment at S. Bloomington | IL |  |  | BaseRel |  |  | 137000 | 2013-12-01 | 2013-12-01 | Proposed | 138 |  | B | Y
B | Central | AmerenIL | 1537 | 2007-04-02 |  | Mt. Vernon, West-S. Centralia - Upgrade Terminal Equipment | Replace terminal equipment at S. Centralia | IL |  |  | BaseRel |  |  | 200000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | B | Y
B | Central | AmerenIL | 2114 | 2008-02-22 | IP03 | IP03 | Network upgrades for tariff service request | IL |  |  | GIP | In Suspension |  | 2082000 | 2009-09-30 | 2013-12-01 | Planned | 138 |  | B | Y
B | Central | AmerenIL | 2117 | 2008-12-10 | IP08 | IP08 | Network upgrades for tariff service request | IL |  |  | GIP | In Suspension |  | 1891464 | 2014-06-01 | 2014-06-01 | Planned | 138 |  | B | Y
B | Central | AmerenIL | 2118 | 2008-12-10 | IP04, IP08 | IP04, IP08 | Network upgrades: Line #1382 & #1384: Project of replacing approximately 47.1 circuit miles of existing three phase, single conductor, 477 MCM 30/7 ASCR with three phase 556.5 MCM 26/7 ACSS conductor. Approximately 121 existing wood H-frame type structures will be replaced with new wood H-frame type structures to gain additional ground clearance. | IL |  |  | GIP | In Suspension |  |  | 2014-06-01 | 2014-06-01 | Planned | 138 |  | B | Y
B | Central | AmerenIL | 2280 | 2008-08-29 |  | LaSalle-Oglesby Main 138 kV Line 1496 | Reconductor 2.16 miles of 477 kcmil ACSR and 336 kcmil ACSR to 1200 A summer emergency capability | IL |  |  | BaseRel | Not Shared |  | 900000 | 2013-06-01 | 2013-06-01 | Planned | 138 |  | B | Y
B | Central | AmerenMO | 2774 | 2009-12-10 | G578 | Adair Wind Farm | Connect Wind Farm at Adair Substation | MO |  |  | GIP | In Suspension |  |  | 2020-11-01 | 2020-11-01 | Proposed | 161 |  | B | Y
B | Central | DEM | 1521 | 2007-03-02 | 802G6746 | Bloomington 13836 Switches | Replace the Bloomington 13836 600A breaker disconnect switches with 2000A switches. New limit 800A Wave Trap. | IN |  |  | BaseRel | Not Shared |  | 233455 | 2016-06-01 | 2016-06-01 | Planned | 138 |  | B | Y
B | Central | DEM | 3381 | 2010-09-15 | AMOH0361 | Meldahl Dam Generator 345kV Interconnect | Install interconnection substation for Meldahl Dam generator. Install 3-breaker 345kV ring bus, 345-138kV - 120 MVA transformer, loop Feeder 4545 through new substation. Connect independent generator per MISO requirements. | OH |  |  | GIP | Not Shared |  | 8949798 | 2013-12-31 | 2013-12-31 | Planned | 345 | 138 | B | Y
B | Central | DEM, IPL | 1558 | 2011-01-11 | DEI 3 | Close Wheatland Breaker | Close the breaker at IPL's Wheatland - make upgrade to Petersburg - Francisco and the Petersburg - Thompson 345 kV to address 1st contingency limitations | IN |  |  | Other |  |  | 11435000 | 2013-05-01 | 2013-05-01 | Proposed | 345 |  | B | Y
B | Central | IPL, DEM | 1557 | 2009-08-28 | FG14 | Bloomington to Pritchard to Franklin to Hanna 345 kV line | Tap the Hanna - Stout 345 and Hanna - Francs 345 kV circuits into one new 345 kV Switching Station at the Franklin twp site and build station at Pritchard. Also adds 345 kV single circuit from Bloomington - Pritchard - Frankin Twp station. | IN |  |  | RegBen |  |  | 41750000 | 2014-01-01 | 2014-01-01 | Proposed | 345 |  | B | Y
B | East | ITC | 1850 | 2008-12-09 |  | Hancock 230/120kV Transformer | Cut the Wixom-Quaker 230kV circuit into Hancock Station, install a 230/120kV transformer. | MI |  |  | BaseRel | Shared |  | 9000000 | 2013-12-31 | 2013-12-31 | Proposed | 230 | 120 | B | Y
B | East | METC | 2809 | 2009-06-26 | 87 | Garfield-Hemphill 138kV | Replace 9.1 miles of 336 ACSR with 1431 ACSR | MI |  |  | Other | Excluded |  | 11740000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | B | Y
B | East | METC | 2822 | 2009-07-24 | new | Edenville Jct. - Warren 138kV | Reconductor the Edenville-Warren 138kV line to 954 ACSR | MI |  |  | Other | Not Shared |  | 7000000 | 2016-12-01 | 2016-12-01 | Proposed | 138 |  | B | Y
B | East | NIPS | 3154 | 2010-04-04 | 71C7559 | Sheffield Substation - 13877 Reactors | Add 0.795 Ohm reactor on BP Whiting to Sheffield circuit | IN |  |  | Other | Not Shared |  | 807141 | 2012-12-01 | 2012-12-01 | Proposed | 138 |  | B | Y
B | West | ATC LLC | 544 | 2010-09-15 | p2-104, F2650 | Bluemound 3x75 Cap Banks | Add 3x75 Cap Banks to 2 Bluemound buses | WI |  |  | Other | Not Shared |  | 3463000 | 2015-06-01 | 2015-06-01 | Conceptual | 138 |  | B | Y
B | West | ATC LLC | 1269 | 2010-09-15 | PR04353 or PR03222 | Arcadian transformer replacement | Replace Arcadian 345/138kV transformer #3 with a 500MVA transformer. | WI |  |  |  | Not Shared |  | 3500000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 | 138 | B | Y
B | West | ATC LLC | 1270 | 2011-04-19 | PR04508 | Rebuild Arcadian - Waukesha 138kV lines | Rebuild the two Arcadian - Waukesha 138kV lines | WI |  |  | Other | Not Shared |  | 14586895 | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | B | Y
B | West | ATC LLC | 1284 | 2010-09-15 | 5, F2095 canceled? | Tie the 138kV radial line Racine - Somers - Albers to the 138kV substation at Albers. Also upgrade the 138kV radial line to 345/477 summer normal/emergency ratings. | Tie the 138kV radial line Racine - Somers - Albers to the 138kV substation at Albers. Also upgrade the 138kV radial line to 345/477 summer normal/emergency ratings. | WI |  |  | BaseRel |  |  |  | 2050-06-01 | 2050-06-01 | Conceptual | 138 |  | B | Y
B | West | ATC LLC | 1624 | 2010-09-15 | PR03203 | Uprate X-67 Portage-Trienda 138 kv line | Increase clearance and uprate SS equipment | WI |  |  |  | Not Shared |  |  | 2022-06-01 | 2022-06-01 | Conceptual | 138 |  | B | Y
B | West | ATC LLC | 1687 | 2010-09-15 | F1867 | Metomen 138-69 kV Transformer Replacement | Replace the Metomen 138-69 kV transformer to achieve a higher emergency rating | WI |  |  | Other | Not Shared |  | 4700000 | 2017-06-01 | 2017-06-01 | Planned | 138 | 69 | B | Y
B | West | ATC LLC | 1946 | 2010-09-15 |  | 2nd Spring Green 138-69 kV Transformer | Install a 2nd Spring Green 138-69 kV Transformer with a 100 MVA summer normal rating | WI |  |  | Other | Not Shared |  | 1400000 | 2018-06-01 | 2018-06-01 | Conceptual | 138 | 69 | B | Y
B | West | ATC LLC | 2044 | 2010-09-15 |  | Uprate Castle Rock-McKenna 69kV | Increase line clearance to 200 deg F SN/SE | WI |  |  | Other | Not Shared |  | 1093828 | 2017-06-01 | 2017-06-01 | Conceptual | 69 |  | B | Y
B | West | ATC LLC | 2454 | 2009-11-19 | G590 | G590 Stony Brook | G590 G-T Interconnection From Techumseh Rd 138 kV bus. Upgrade Kaukauna Central tap - Tayco 138 kV line. | WI |  |  | GIP | In Suspension |  | 1610720 | 2012-05-01 | 2012-05-01 | Planned | 138 |  | B | Y
B | West | ATC LLC | 3089 | 2009-10-08 |  | Nine Springs Pflaum Area Project | Uprate Fitchburg-Nine Springs and Royster-Pflaum lines to 275 deg F SE clearance and move AGA load onto Femrite-Royster line and install 2-16.33Mvar cap banks at Nine Springs | WI | [5 empty] | 4400000 | 2013-01-31 | 2013-01-31 | Proposed | 69 |  | B | Y
B | West | ATC LLC | 3118 | 2010-01-15 | 3118 | North Lake Geneva-South Lake Geneva 138kV | North Lake Geneva-South Lake Geneva 138kV line | WI | [5 empty] | 16401632 | 2016-06-01 | 2016-06-01 | Proposed | 138 | 69 | B | Y
B | West | GRE | 2098 | 2008-02-22 | G390 | G390, A252, A253 | Network upgrades for tariff service request for G390, A252, A253 | MN |  |  | GIP | In Suspension |  | 6272080 | 2013-04-01 | 2013-04-01 | Proposed | 230 |  | B | Y
B | West | ITCM | 1147 | 2009-09-25 | G298 | G298, 37061-02 | Net: The Transmission Owner shall install a new 161kV line breaker on the Triboji- Wisdom Line and a new 161kV transformer breaker located on the existing #1 Triboji 161/69kV transformer and are shown in Exhibit A2.. Int: Generator shall construct a 161/34kV substation consisting of 161kV breaker, 161/34kV transformer, 34kV breakers and a 161kV line from (Bob what is name of Customer sub?) to the dead-end tower at the IPL Triboji substation. | IA |  |  | GIP | In Suspension |  | 2300000 | 2011-12-31 | 2011-12-31 | Planned | 161 |  | B | Y
B | West | ITCM | 1741 | 2011-02-15 |  | G517: Dotson - Storden - Heron Lake 161kV | Network upgrades for G517. Build a new Heron Lake - Cottonwood Co 161 kV line and a new Cottonwood Co 161 kV switch station. Build Cottonwood Co to Dotson 161kV line. | MN |  |  | GIP | Shared |  | 36719820 | 2012-12-31 | 2012-12-31 | Planned | 161 |  | B | Y
B | West | MDU | 1148 | 2005-11-18 | G297 | G297, 37664-01 | Net: At the Glenham Jct Substation, two 115 kV line potential sources and sync-check relaying on breakers 7047 and 7050. · At the Bowdle Jct Substation, five 41.6 kV line potential sources and sync-check relaying on breakers 500, 510, 5049, 5050 and 6470 . Int: | SD |  |  | GIP | In Suspension |  |  | 2012-12-31 | 2012-12-31 | Planned | 115 | 1 | B | Y
B | West | MDU | 1153 | 2005-11-18 | G311 | G311, 37699-01 | Net: The Transmission Owner shall install a larger 115/34.5kV substation transformer, and relaying associated with the new transformer. Add 34.5kV PTs, 34.5kV station service transformer, SCADA RTU, 115kV CVTs and 115kV line relaying at Gascoyne. Add sync-check relaying on breaker 2132 at the Hettinger Jct Substation. Int: Generator shall cause to be constructed the following interconnection facilities at Transmission Owner's Gascoyne Jct Substation: 2-circuit breaker disconnect switches, 1- “intertie circuit breaker” and associated 34.5kV line and intertie protective relaying, meters, 34.5kV potential and current transformers, arresters, the associated high voltage bus work, grounding, foundations, conduit and control wiring. | ND |  |  | GIP | In Suspension |  |  | 2012-09-01 | 2012-09-01 | Planned | 115 | 1 | B | Y
B | West | MDU | 3083 | 2009-09-15 | Dickinson Loop | Dickinson 115 kV Loop | Complete 115 kV loop & new 115/41.6 subsation in Dickinson area | ND |  |  | TBD |  |  | 11150000 | 2014-10-01 | 2014-10-01 | Planned | 115 | 41.6 | B | Y
B | West | MEC | 2937 | 2009-09-14 | G0103 | Sub 39 Add 2nd 345-161 kV Xfmr | Add a second 345-161 kV xfmr. Expand 345 kV and 161 kV buses. | IL |  |  | BaseRel | Shared |  | 14500000 | 2014-06-01 | 2014-06-01 | Proposed | 345 | 161 | B | Y
B | West | MEC | 2938 | 2009-09-14 | G0104 | Uprate Sub 39 - Cordova 345 kV Line | Change out structures to increase rating. | IL |  |  | BaseRel | Shared |  | 400000 | 2014-06-01 | 2014-06-01 | Proposed | 345 |  | B | Y
B | West | MEC | 2939 | 2010-09-01 | G0307 | Raun-Sioux City 345 kV Line | Construct a 23 mile 345 kV line between the Raun and Sioux City Substations | IA |  |  | BaseRel | Shared |  | 28400000 | 2016-06-01 | 2016-06-01 | Proposed | 345 |  | B | Y
B | West | MP | 1292 | 2011-09-06 | 14 | Raise tower height on ETCO-Forbes 115 kV line | Raise tower height on ETCO-Forbes 115 kV line so the 336 ACSR conductor rating can reach 122/134 MVA | MN |  |  | BaseRel | Not Shared |  | 400000 | 2012-12-01 | 2012-12-01 | Planned | 115 |  | B | Y
B | West | OTP | 549 | 2009-11-18 | p2-108 | Jamestown Reactor Addition | Jamestown 115 kV 25 MVAR reactor | ND |  |  | BaseRel | Not Shared |  | 250000 | 2015-12-01 | 2015-12-01 | Proposed | 115 |  | B | Y
B | West | OTP | 585 | 2009-11-18 | 585 | Pelican Rapids 115 kV Line Uprate | Pelican Rapids - Pelican Rapids Turkey Plant 115 kV line | MN |  |  | Other | Not Shared | Reliability | 858869 | 2013-12-31 | 2013-12-31 | Planned | 115 |  | B | Y
B | West | OTP | 2824 | 2011-09-06 | OTP1 | Hensel Capacitor Bank | Install Capacitor Bank on 115 kV at Hensel, ND. Two 15 MVAR. | ND |  |  | Other | Not Shared | Reliability | 750000 | 2014-12-31 | 2014-12-31 | Proposed | 115 | 41.6 | B | Y
B | West | XEL | 2107 | 2008-02-22 | G520 | G520 | Network upgrades: Install new 3-position 115 kV substations (tapping Lake Yankton - Lyon County 115 kV line) with breakers, switches, buswork, steel, foundations, control house and associated equipment. Install new loop in-and-out tap, 3.5 miles of double circuit, 115 kV transmission line. | MN |  |  | GIP | In Suspension |  | 5930926 | 2009-04-02 | 2009-04-02 | Planned | 115 | 34.5 | B | Y
B | West | XEL | 2115 | 2008-02-22 | G491 | G491 | G491: One new 120 MVA, 118-36.2 kV transformer, three new 115 kV breakers and associated disconnect switches, one new 34.5 kV transformer low side main breaker and associated disconnect switches, control house expansion, structural steel and foundations associated with this new equipment, control and protection equipment associated with these new installations | MN |  |  | GIP | In Suspension |  | 4363152 | 2010-09-01 | 2010-09-01 | Planned | 115 |  | B | Y
B | West | XEL | 3099 | 2009-11-19 |  | Franklin TR upgrade | Upgrade Franklin 115/69 kV Xfrmr 1 and 2 to 70 MVA as part of the CapX underlying system upgrade | MN |  |  | Other | Not Shared | Reliability | 4800000 | 2013-06-01 | 2013-06-01 | Planned | 115 | 69 | B | Y
B in MTEP10 | Central | AmerenIL | 2964 | 2010-12-06 |  | Secure Energy Connection | Secure Energy - Provide connection to Secure Energy coal gasification plant with 5 PCB 138 kV ring bus substation. Plant would connect in the Decatur area to ADM North-North 27th Street 138 kV Line 1604 between ADM North and Caterpillar Substations. | IL |  |  | Other | Not Shared |  | 5966000 | 2011-06-01 | 2011-06-01 | Proposed | 138 | 1 | B | Y
B in MTEP10 | Central | AmerenIL | 2978 | 2009-12-23 |  | ESK Capacitor Bank | ESK Customer Substation - Install 32 Mvar, 138 kV capacitor bank to improve customer load power factor. | IL |  |  | BaseRel | Not Shared |  | 1521000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | B | Y
B in MTEP10 | Central | AmerenMO | 2970 | 2010-12-06 |  | Apache Flats - Scruggs Delivery Point | Apache Flats 161 kV Substation - Install 1-161 kV, 2000 A PCB and necessary metering and relaying to provide a delivery point for Associated Electric's Scruggs 161-69 kV Substation. | MO |  |  | Other | Not Shared |  | 1035000 | 2012-06-01 | 2012-06-01 | Planned | 161 |  | B | Y
B in MTEP10 | Central | IPL | 3212 | 2010-08-19 |  | Wheatland - Breed 345kV rating upgrade and close Wheatland 345 kV tie breaker | Increase rating to 1386MVA on line Wheatland - Breed 345kV. Close Wheatland 345 kV Tie breaker | IN | [5 empty] | 12000000 | 2015-01-01 | 2015-01-01 | Proposed | 345 |  | B | Y
B in MTEP10 | East | ITC | 1856 | 2009-09-14 |  | Belle River - Greenwood - Pontiac 345kV cut into Jewell | Cut the Pontiac section of the Belle River-Greenwood-Pontiac 345kV circuit into and out of Jewell station. Utilize an existing unused side of 345kV tower for one of the circuits into Jewell, and relocate the Jewell-Spokane 230kV circuit | MI |  |  | BaseRel | Shared |  | 5200000 | 2015-12-31 | 2015-12-31 | Proposed | 345 |  | B | Y
B in MTEP10 | East | ITC | 2932 | 2009-09-14 |  | St Antoine-Essex #2 120 kV | Construct 2nd underground cable from St Antoine to Essex (5.1 miles). | MI |  |  | BaseRel | Shared |  | 54800000 | 2015-06-01 | 2015-06-01 | Proposed | 120 |  | B | Y
B in MTEP10 | East | METC | 3210 | 2010-07-21 |  | Vanderbilt - Riggsville 138 kV Rebuild | Rebuild 30.3 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. | MI | [5 empty] | 33254000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | B | Y
B in MTEP10 | West | MPW | 2935 | 2010-09-21 | MPW-WR | Reconductor 69 kV lines South - Wiggins - Power Plant (Lines 81 & 82) | The 2008 updated schedule changed the schedule for the 69 kV transmission line upgrades. MPW is looking at upgrading the 69 kV transmission lines from 633501 South Sub to 633511 Wiggins Road (Line 82) and from 633511 Wiggins Road to our 633408 Power Plant (Line 81) from 58 MW to at least 89 MW (636 ACSR) by 2014. | IA |  |  | Other | Not Shared | Reliability | 300000 | 2017-06-01 | 2017-06-01 | Proposed | 69 |  | B | Y
B in MTEP10 | West | XEL | 3121 | 2010-01-27 |  | Lake Marion - Burnsville upgrade | Upgrade 13 miles of 115 kV line between Lake Marion and Burnesville to 2-795 ACSR conductor | MN |  |  | BaseRel | Shared |  | 6200000 | 2016-06-01 | 2016-06-01 | Planned | 115 |  | B | Y
B in MTEP10 | West, Central, East | Midwest ISO | 3200 | 2010-07-13 | RGOS 765 | RGOS 765 kV Strategy. In AMIL,AMMO,MEC,XEL,OTP,ALTE,GRE,WEC,MDU,MGE,ALTW,DPC,DEM,IPL,ITCT,SIGE,FE,WPS,Non-MISO | Build transmission throughout the Midwest ISO system that helps the facilitation of the collection and delivery of renewable energy to meet the current mandate needs. This strategy focuses on the introduction of 765 kV transmission throughout the Midwest ISO footprint. Further development and identification of timing needs will be dependent on further regional analysis and candidate MVP evaluation. | IA | WI |  | MVP |  |  | 12581351093.76 | 2025-01-01 | 2025-01-01 | Conceptual | 765 | 115 | B | Y
B in MTEP10 | West, Central, East | Midwest ISO | 3202 | 2010-07-13 | RGOS Native | RGOS Native Voltage Strategy. In AMIL,AMMO,MEC,XEL,OTP,ALTE,GRE,WEC,MDU,MGE,ALTW,DPC,DEM,IPL,ITCT,SIGE,FE,WPS | Build transmission throughout the Midwest ISO system that helps the facilitation of the collection and delivery of renewable energy to meet the current mandate needs. This strategy focuses on the development of transmission voltages that are already native to the areas. Further development and identification of timing needs will be dependent on further regional analysis and candidate MVP evaluation. | IA | WI |  | MVP |  |  | 10423998000 | 2025-01-01 | 2025-01-01 | Conceptual | 765 | 115 | B | Y
B in MTEP11 | Central | AmerenIL | 2967 | 2011-04-22 |  | Grand Tower Capacitor Bank | Grand Tower Plant - Install 2-stage 80 Mvar (2 x 40 Mvar) 138 kV capacitor bank. 2-138 kV PCB's needed. | IL |  |  | BaseRel | Not Shared |  | 2715000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | B | Y
B in MTEP11 | Central | AmerenIL | 2977 | 2011-04-22 |  | LaSalle Substation Relocation | LaSalle 138-34.5 kV Substation - Relocate Substation to avoid flooding and to permit remediation of manufactured gas plant site. | IL |  |  | Other | Not Shared |  | 1347000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | B | Y
B in MTEP11 | Central | AmerenIL | 2982 | 2011-04-22 |  | Washington Street-S. Bloomington Line 1326 - Upgrade Terminal Equipment | Washington Street-S. Bloomington 138 kV Line 1326 - Replace terminal equipment (wavetrap, 3-CT's and bus conductor) at S. Bloomington with equipment capable of carrying minimum 2000 A under summer emergency conditions. | IL |  |  | BaseRel | Not Shared |  | 137000 | 2013-12-01 | 2013-12-01 | Proposed | 138 |  | B | Y
B in MTEP11 | Central | AmerenIL | 3009 | 2011-04-22 | AMRN12 | Newton-Hutsonville-Merom 345 kV Line | Newton-Hutsonville 345 kV line – New 40 mi. 3000 A summer emergency capability line. Hutsonville-Merom 345 kV line - New 12 mi. 3000 A summer emergency capability line. 345/138 kV 560 MVA transformer @ Hutsonville | IL | [5 empty] | 110000000 | 2018-06-01 | 2018-06-01 | Proposed | 345 | 138 | B | Y
B in MTEP11 | Central | AmerenIL | 3010 | 2011-04-22 | AMRN13 | Baldwin-Grand Tower-N.W. Cape 345 kV Line | New 69 mile, single-circuit line (possible double circuit), 3000 A SE capability (Baldwin-Grand Tower - 45 miles; Grand Tower-N.W. Cape - 24 miles). Grand Tower 345/138 kV Substation - 1-560 MVA transformer, 345 kV Ring bus | IL | [5 empty] | 151000000 | 2025-12-01 | 2025-12-01 | Proposed | 345 | 138 | B | Y
B in MTEP11 | Central | AmerenMO | 2971 | 2011-04-22 | AMRN5 | Rolla Alftermann Substation | Rolla Alfermann Substation - Tap Clark-Osage-2 and Rivermines-Maries-1 138 kV lines to establish 138 kVsupplies to new 138-34.5 kV Alfermann Substation, owned by City of Rolla. Ameren to construct tapping structures. 2-138 kV, 1200 A disconnect switches | MO |  |  | Other | Not Shared |  | 963000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | B | Y
B in MTEP11 | Central | AmerenMO | 2973 | 2011-04-22 |  | Howard Bend Substation Connection | Howard Bend 138-12 kV Substation - Provide 138 kV ring bus connection from Mason-Carrollton-8 138 kV line to new Howard Bend Substation. Install 1-138 kV, 2000 A PCB at Carrollton Substation as a bus-tie. | MO |  |  | Other | Not Shared |  | 1371000 | 2016-12-01 | 2016-12-01 | Proposed | 138 |  | B | Y
B in MTEP11 | Central | AmerenMO | 2979 | 2011-04-22 |  | Enon 345 kV Breaker Addition | Enon 345/161 kV Substation - Install 2-345 kV PCB's on incoming 345 kV lines. | MO |  |  | BaseRel | Not Shared |  | 1876000 | 2013-06-01 | 2013-06-01 | Proposed | 345 |  | B | Y
B in MTEP11 | Central | AmerenMO | 2988 | 2011-04-22 |  | Warrenton-Lincoln Bulk 161 kV Line | Warrenton-Lincoln Bulk Substation 161 kV - Establish a second 161 kV supply to Lincoln Bulk Substation from Warrenton Substation. 10 miles of new 161 kV line, 2-161 kV, 2000 A PCBs at Warrenton Substation. | MO |  |  | BaseRel | Shared |  | 12000000 | 2016-06-01 | 2016-06-01 | Proposed | 161 |  | B | Y
B in MTEP11 | East | ITC | 3282 | 2010-09-15 | 8 | Southfield - Sunset 120 kV Rebuild | Rebuild 6.4 mile 120 kV Line | Mi |  |  | BaseRel | Shared |  | 7100000 | 2013-12-31 | 2013-12-31 | Planned | 120 |  | C>B | Y
B in MTEP11 | East | METC | 1803 | 2011-03-28 |  | Plum-Stover 138 kV Rebuild | Rebuild the 8.8 mile 138 kV line to 954 ACSR (Pre-build to 230 kV construction). | MI |  |  | BaseRel | Shared |  | 10900000 | 2013-12-31 | 2013-12-31 | Planned | 138 |  | C>B | Y
B in MTEP11 | East | METC | 1815 | 2011-03-28 |  | Chase - Mecosta 138kV Rebuild | Rebuild 7.2 miles of 138kV 110 and 115 CU to 954 ACSR. Prebuild to 230kV construction. | MI |  |  | BaseRel | Shared |  | 8900000 | 2014-12-31 | 2014-12-31 | Planned | 138 |  | C>B | Y
B in MTEP11 | West | ATC LLC | 2799 | 2010-09-15 |  | Kinross Load Interconnection | Construct a 3 mile line to connect the Kinross load | MI | [5 empty] | 3882248 | 2013-07-01 | 2013-07-01 | Conceptual | 69 |  | C>B | Y
B in MTEP11 | West | ATC LLC | 3119 | 2010-09-15 | 3119 | Uprate 6923 Pine River-9mile 69kV | Increase ground clearance for 6923 Pine River-9Mile 69kV line to 167 deg f clearance | MI | [5 empty] | 2000000 | 2016-06-01 | 2016-06-01 | Proposed | 69 |  | C>B | Y
B in MTEP11 | West | ATC LLC | 3209 | 2010-09-15 |  | Replace Edgewater 138/69kV Trs | Replace the Edgewater 138-69 kV Trs with 60 MVA units Replace the 4/0 Cu strain bus sections 1 & 2 with conductor capable of 75 MVA SE Remove 69 kV by-pass switches 1666A, 359A, 460A, and 368A Replace the following 69 kV disconnect switches with new GOAB switches 359L, 359B, 368L and 368B Add line side surge arresters to 69 kV lines Y-31, Y-55, and Y-142 Upgrade and/or replace relaying and protection systems Install new GCBs to the low side (69KV) positions of T31 and T32. Replace T31 and T32 transformer 69 kV disconnect switches 315A and 337A. | WI | [5 empty] | 5409471 | 2013-10-25 | 2013-10-25 | Proposed | 138 | 69 | C>B | Y
B in MTEP11 | West | ATC LLC | 3490 | 2011-03-22 | PR04027 | Rebuild Y-20 Doylestown-Rio Pumping Station | Asset Management project to Rebuild Y-20 Doylestown to Rio Pumping Station | WI | [5 empty] | 7400000 | 2013-04-15 | 2013-04-15 | Planned | 69 |  | C>B | Y
B in MTEP11 | West | ATC LLC | 3514 | 2011-06-07 |  | 96th St Breaker and a half bus reconfiguration | Create 96ST 6-rung breaker and a half for zoo interchange relocation project | WI | [5 empty] | 28000000 | 2013-09-01 | 2013-09-01 | Proposed | 138 |  | C>B | Y
B in MTEP11 | West | ATC LLC | 3519 | 2011-07-12 |  | RiverBend T-D Load interconnection | Construct a 138 kV loop through River Bend distribution Substation on line 731. | WI |  |  | Other | Not Shared | Distribution | 3016359 | 2012-12-31 | 2012-12-31 | Proposed | 138 | 24.9 | C>B | Y
B in MTEP11 | West | MEC | 3214 | 2010-09-07 | G1405 | Sub 17 and Sub 39 Replace Relays 161-17-39-1 | Replace relaying and remove wave trap | IL |  |  | Other | Not Shared | Condition | 225000 | 2015-12-01 | 2015-12-01 | Proposed | 161 |  | C>B | Y
B in MTEP11 | West | MEC | 3215 | 2010-09-07 | T6242 | Sub 49 161 kV Capacitor | Add 50 MVAr 161 kV capacitor | IL |  |  | BaseRel | Not Shared |  | 840000 | 2014-06-01 | 2014-06-01 | Proposed | 161 |  | C>B | Y
B in MTEP11 | West | MEC | 3216 | 2011-02-15 | G1352 | Plymouth-Sioux City 161 kV Line | Construct a 2 mile 161 kV line between the Plymouth and Sioux City Substations and associated substation equipment additions. | IA |  |  | BaseRel | Not Shared |  | 2400000 | 2014-06-01 | 2014-06-01 | Planned | 161 |  | C>B | Y
B in MTEP11 | West | MEC | 3266 | 2010-09-07 | T6164 | Sub 56-89 161 Line Uprate | Increase 161 kV line rating. | IA |  |  | BaseRel | TBD |  | 680000 | 2016-06-01 | 2016-06-01 | Proposed | 161 |  | C>B | Y
B in MTEP11 | West | OTP | 3431 | 2010-09-28 | OTP1 | Hankinson 230/41.6 kV Transformer Addition | Add a second 230/41.6 kV transformer at Hankinson Substation which will include the addition of 2 new 230 kV breakers. | ND | [5 empty] | 835000 | 2012-10-01 | 2012-10-01 | Planned | 230 | 41.6 | C>B | Y
B in MTEP11 | West | OTP | 3462 | 2011-01-11 | OTP1 | Project G-968 100 MW Wind Farm near Viking MN | Add 3 breaker 115 kV ring bus | MN | [5 empty] | 2800000 | 2012-10-30 | 2012-10-30 | Proposed | 115 | 115 | C>B | Y
B in MTEP11 | West | OTP | 3464 | 2011-01-11 | OTP1 | Project G-873 20 MW Wind Farm on Donaldson 41.6 kV Line | Add 3 Way Switch on 41.6 kV line between Donaldson 115 kV substation to Donaldson distribution sub. | MN |  |  | GIP | Not Shared |  | 160000 | 2012-12-01 | 2012-12-01 | Proposed | 41.6 |  | B | Y
B in MTEP11 | West | OTP | 3465 | 2011-01-11 | OTP1 | Project G-875 80 MW Wind Farm at Donaldson 115/41.6 kV Substation | Add 3 new 115 kV Breakers & expand substation to accommodate wind farm. | MN |  |  | GIP | Not Shared |  | 1500000 | 2012-12-31 | 2012-12-31 | Proposed | 115 | 41.6 | B | Y
B in MTEP11 | West, Central, East | AmerenMO, AMIL, MEC, XEL | 3201 | 2011-04-22 | RGOS DC | RGOS Identified DC transmission | Build transmission throughout the Midwest ISO system that helps the facilitation of the collection and delivery of renewable energy to meet the current mandate needs. This strategy focuses on the introduction of HVDC transmission throughout the Midwest ISO footprint. Further development and identification of timing needs will be dependent on further regional analysis and candidate MVP evaluation. | IA | SD |  | MVP |  |  | 5401519473.6 | 2025-01-01 | 2025-01-01 | Conceptual | 800 |  | B | Y
C | West | ATC LLC | 3506 | 2011-04-20 | PR04371 | Vinburn T-D Interconnection | Construct a 69 kV loop through Vinburn distribution Substation on line Y104. This project also includes rerouting the Hampden tap into Vinburn Substation. | WI | [5 empty] | 3362287 | 2012-12-31 | 2012-12-31 | Proposed | 69 |  | C | Y
C | West | ATC LLC | 3507 | 2011-04-20 | PR04556 | Shoto-Manrap Uprate | This project is a thermal uprate of C-55 (MANRAP - SHOTO 69KV) | WI | [5 empty] | 319044 | 2012-03-01 | 2012-03-01 | Proposed | 69 |  | C | Y
C | West | ATC LLC | 3508 | 2011-08-24 |  | Revere-Northeast Uprate | This project is a thermal uprate of C-103 (Revere - Northeast 69KV) | WI | [5 empty] | 171475 | 2012-01-01 | 2012-01-01 | Proposed | 69 |  | C | Y
C | West | ATC LLC | 3515 | 2011-06-07 | PR04627 | Granville Economic Project | Uprate 3443 Granville-Tosa 138kV & 3453 Granville-Butler 138kV | WI | [5 empty] | 1136322 | 2011-12-31 | 2011-12-31 | Proposed | 138 |  | C | Y
C | West | GRE | 3470 | 2011-01-11 |  | MISO G667 |  | MN | [5 empty] | 118182 | 2011-12-01 | 2011-12-01 | Planned |  |  | C | Y
C | Central | AmerenIL | 2283 | 2008-12-10 |  | South Bloomington 138-34.5 kV Substation | Install 2 new 2000 A, 138 kV Bus-Tie breakers | IL |  |  | Other |  |  | 1030000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2289 | 2008-08-29 |  | Benton-W. Frankfort 138 kV Line | Reconductor 9.62 miles of 350 kcmil Cu to carry 1200 A under summer emergency conditions | IL |  |  | BaseRel |  |  | 1871000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2290 | 2009-12-23 |  | Joppa 345 kV Switching Station 2nd. Xfmr | Add 2nd. 345/161 kV, 560 MVA Transformer | IL |  |  | BaseRel | Not Shared |  | 4000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 | 161 | C | Y
C | Central | AmerenIL | 2293 | 2008-08-29 |  | N. LaSalle-LaSalle Jct. 138 kV Line 1556A | Reconductor 9.68 miles of 477 kcmil ACSR to 1600 A summer emergency capability | IL | [5 empty] | 2515000 | 41791 | 41791 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2294 | 2009-09-22 |  | Stallings 345/138 kV Sub - 138 kV Bus-Tie CT Replacement | Reconnect or replace 1200 A CT in the 138 kV Bus-Tie Position 1302 to 2000 A capability. | IL |  |  | BaseRel |  |  |  | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2295 | 2008-08-29 |  | W. Mt. Vernon-E. W. Frankfort 345 kV | Upgrade terminal equipment to 3000 A continuous capability | IL |  |  | Other |  |  | 1366000 | 2015-06-01 | 2015-06-01 | Proposed | 345 |  | C | Y
C | Central | AmerenIL | 2299 | 2008-08-29 |  | Fargo 138-69 kV Substation | Install 138 kV Capacitor Bank | IL |  |  | BaseRel |  |  | 1500000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2300 | 2009-12-23 |  | Hennepin Plant - 138 kV Bus-Tie Breakers | Install 2-3000 A, 138 kV Breakers as Bus-Ties in the Hennepin North and South Buses. Swap connection to Transformer TT2 with breaker position 1556 or 6101. | IL |  |  | BaseRel | Shared |  | 9124000 | 2019-06-01 | 2019-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2301 | 2008-08-29 |  | Hennepin-Oglesby 138 kV Line 1556 | Reconductor 8.37 miles of 477 kcmil ACSR to 1600 A summer emergency capability | IL |  |  | BaseRel |  |  | 4215000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2302 | 2008-08-29 |  | Madison Industrial-Madison State Street 138 kV | Reconductor 2.35 miles of 795 kcmil SAC conductor to 1200 A summer emergency capability | IL |  |  | BaseRel |  |  | 710000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2305 | 2008-08-29 |  | Monmouth Substation 138 kV Capacitor Bank | Install 30 Mvar, 138 kV capacitor bank | IL |  |  | BaseRel |  |  | 1022000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3024 | 2010-12-06 |  | Bunsonville 2nd. 345/138 kV Transformer | Bunsonville 345/138 kV Substation - Install 2nd. 560 MVA Transformer. | IL | [5 empty] | 5000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 | 138 | C | Y
C | Central | AmerenIL | 3336 | 2010-09-15 |  | Gilman-Watseka Reconductoring | Reconductor to 1600 A summer emergency capability | IL | [5 empty] | 4763000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3338 | 2010-12-06 |  | Lanesville Transformer Replacement | Replace existing transformer with 560 MVA unit | IL | [5 empty] | 4000000 | 2013-06-01 | 2013-06-01 | Proposed | 345 | 138 | C | Y
C | Central | AmerenIL | 3339 | 2010-09-15 |  | Pana, North-Taylorville, South Reconductoring | Reconductor to 1600 A summer emergency capability. Upgrade terminal equipment to match. | IL | [5 empty] | 4073000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3340 | 2010-09-15 |  | Pawnee, West-Taylorville, South Terminal Equipment | Replace bus conductor at both terminals to 1200 A summer emergency capability | IL | [5 empty] | 100000 | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3341 | 2010-09-15 |  | Diamond Star-West Washington Street Reconductoring | Reconductor 336 kcmil ACSR conductor to 1200 A summer emergency capability | IL | [5 empty] | 375000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3342 | 2010-09-15 |  | Diamond Star-McClean County Sw. Station - Increase Ground Clearance | Increase ground clearance on 2.4 miles of 477 kcmil ACSR conductor | IL | [5 empty] | 240000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3343 | 2010-09-15 |  | Increase Ground Clearance - Raab Rd.-White Oak Tap | Increase ground clearance on 3.92 miles of 477 kcmil ACSR conductor | IL | [5 empty] | 400000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3344 | 2010-09-15 |  | Increase Ground Clearance - El Paso Tap-Minonk | Increase ground clearance on 13.88 miles of 477 kcmil ACSR conductor | IL | [5 empty] | 1300000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3345 | 2010-09-15 |  | Increase Ground Clearance - R.S. Wallace-E. Peoria | Increase ground clearance on 0.6 mile of 477 kcmil ACSR conductor. | IL | [5 empty] | 60000 | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3346 | 2010-09-15 |  | Reconductor Mason-Holland | Reconductor 0.05 mile 795 kcmil ACSR to 1200 A summer emergency capability | IL | [5 empty] | 25000 | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3347 | 2010-09-15 |  | Reconductor Mason-San Jose Rail | Reconductor 0.05 mile 795 kcmil ACSR to 1200 A summer emergency capability | IL | [5 empty] | 25000 | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3351 | 2010-09-15 |  | Wood River 138 kV Bus-Tie Breakers | Install 2-2000 A, 138 kV bus-tie breakers | IL | [5 empty] | 2000000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3352 | 2010-09-15 |  | West Tilton 138 kV Capacitor Bank | Install 40 Mvar, 138 kV capacitor bank. | IL | [5 empty] | 1500000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3353 | 2010-09-15 |  | Edwards-Keystone 138 kV - Breaker Replacement at Keystone | Replace 138 kV, 1200 A breaker and terminal equipment at Keystone terminal to 2000 A capability | IL | [5 empty] | 1100000 | 2012-06-01 | 2012-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3354 | 2010-09-15 |  | Edwards-Caterpillar Sub 1 - Increase Ground Clearance | Increase ground clearand on 795 kcmil ACSR and 927 ACAR conductor | IL | [5 empty] | 950000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3362 | 2010-09-15 |  | H100 Generator connection - Sidney-Rantoul Jct. | Install a 3-position ring bus to facilitate connection of wind farm (H100) to the Sidney-Rantoul Jct. 138 kV line. | IL | [5 empty] | 3240000 | 2013-09-30 | 2013-09-30 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3369 | 2010-09-15 |  | Quincy, East Sub. - Replace Transformer #3 | Replace 138-34.5 kV Transformer Bank #3 with a 112 MVA unit. Replace 600 A, 138 kV disconnect switch with minimum 800 A capability | IL | [5 empty] | 100000 | 2012-06-01 | 2012-06-01 | Planned | 138 |  | C | Y
C | Central | AmerenMO | 2296 | 2009-12-23 |  | Belleau 345/138 kV Substation - 2nd. Xfmr | Install 2nd. 560 MVA, 345/138 kV Transformer | MO |  |  | BaseRel | Not Shared |  | 8335000 | 2013-06-01 | 2013-06-01 | Proposed | 345 | 138 | C | Y
C | Central | AmerenMO | 2297 | 2009-12-10 |  | Belleau 345/138 kV Substation - Install 138 kV capacitor bank | Install 138 kV, 120 Mvar capacitor bank (as 2-60 Mvar stages) At Belleau Substation | MO |  |  | Other |  |  | 3071000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 2975 | 2010-12-06 |  | Dupo Ferry-Selma-1 - Connection to Wings Enterprises | Dupo Ferry-Selma-1 138 kV Line - Install 3 position 138 kV ring bus and extend 138 kV line to serve a customer substation (Wings Enterprises). 3-138 kV, 1200A PCB's | MO | [5 empty] | 1141000 | 2012-12-01 | 2012-12-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 3356 | 2010-09-15 |  | Tegeler-Osage Disconnect Switch Replacement | Replace 138 kV disconnect switch at Freeburg with new 1200 A switch | MO | [5 empty] | 200000 | 2012-12-01 | 2012-12-01 | Planned | 138 |  | C | Y
C | Central | AmerenMO | 3364 | 2010-12-06 | AMRN22 | Prairie Dell Substation | Install 138 kV breakers, build 3.1 miles of new 138 kV double circuit line, reuse a total of 9.6 miles of 34.5 kV line at 138 kV to establish supplies to Prairie Dell Substation | MO | [5 empty] | 11100000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 3365 | 2010-09-15 |  | Delbridge Substation High-Side Transfer | Install 2000 A breaker and 2-2000 A 138 kV motor operated disconnect switches | MO | [5 empty] | 2221000 | 2011-12-01 | 2011-12-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 3366 | 2010-12-06 |  | Wallen Creek Substation High-Side Transfer | Install 2000 A breaker and 2-2000 A 138 kV motor operated disconnect switches | MO | [5 empty] | 2221000 | 2011-12-01 | 2011-12-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 3367 | 2010-12-06 |  | Pershall Substation | Install 4-2000 A breaker ring bus and connect to Berkeley-Sioux-1 138 kV to establish 138 kV connections for Pershall 138-12.47 kV Sub | MO | [5 empty] | 4631000 | 2013-09-01 | 2013-09-01 | Proposed | 138 |  | C | Y
C | Central | AMRN | 3197 | 2010-06-30 | 1 | Oak Grove - Kewanee 161 kV | Build new 161 kV circuit from Oak Grove to Kewanee | IL |  |  | MVP |  |  | 61000000 | 2014-05-01 | 2017-06-01 | Proposed | 161 | 138 | C | Y
C | Central | AMRN | 3198 | 2010-06-30 | 2 | Oak Grove - Kewanee 345 kV | Build new 345 kV circuit from Oak Grove to Kewanee | IL |  |  | MVP |  |  | 86000000 | 2014-05-01 | 2017-06-01 | Proposed | 345 | 138 | C | Y
C | Central | DEM | 2795 | 2009-03-10 | Pioneer LLC | Pioneer 765 | New 765 kV line from Rockport (AEP) to Greentown (DEM) | IN | [5 empty] | 1000000000 | 2015-05-01 | 2015-05-01 | Proposed | 765 |  | C | Y
C | Central | DEM | 2862 | 2009-09-14 | AMIN0131 | Staunton to Lonestar Jct 138kV - 13802 ckt. Uprate | Uprate Staunton to Greencastle Jct to Lonestar Jct 13802 circuit 336ACSR for 100C cond temp operation (Lone Star Jct switches may also need upgraded to 1200A) | IN | [5 empty] | 350000 | 2016-06-01 | 2016-06-01 | Planned | 138 |  | C | Y
C | Central | IPL, HE | 2901 | 2009-09-14 | 1557 | Hanna - Bloomington 345 kV Line Economic Project Portfolio | Add a new 345 kV line from IPL Hanna - IPL Franklin Township - HE Bloomington Substation, Close the Duke Wheatland Substation Tie Breakers and Upgrade the rating of the 345 kV line from IPL Petersburg - Duke Wheatland - AEP Breed to 1386 MVA. Closing the Duke Wheatland bus tie breakers connects the IPL Petersburg-Duke Wheatland-AEP Breed line into the Duke Wheatland 345 kV substation. | IN | [5 empty] | 70900000 |  |  | Proposed | 345 |  | C | Y
C | West | ATC LLC | 1689 | 2010-09-15 | PR03927 | Ripon Capacitor Banks | Upgrade 4.1 MVAR capacitor bank to 8.2 MVAR and install a new 8.2 MVAR capacitor bank at Ripon 69 kV substation | WI |  |  |  | Not Shared |  | 895300 | 2015-06-01 | 2015-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1700 | 2010-09-15 |  | Ripon-Metomen 69 kV line | Construct a 69 kV line from SW Ripon to the Ripon-Metomen 69 kV line | WI |  |  |  | Not Shared |  |  | 2015-09-30 | 2015-09-30 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 2779 | 2010-09-15 |  | New Chandler-18th Road 138 kV line + 18th Road 138/69 kV SS and xfmr | Build a new 6-mile 138 kV line from Chandler to 18th Road, add a new 138/69 kV SS and 138/69 kV 150 MVA xfmr at 18th Road | MI | WI |  | TBD | TBD |  | 22000000 | 2014-06-01 | 2014-06-01 | Proposed | 138 | 69 | C | Y
C | West | ATC LLC | 3096 | 2010-09-15 |  | Uprate Inland line Munising-Blaney Park 69kV | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance | MI | [5 empty] | 21003000 | 2014-06-01 | 2014-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3125 | 2010-09-15 |  | Install a 345/138kV Tr at Arnold | Tap the Plains-Dead River 345kV line into the Arnold 138kV substation and add a 345/138kV transformer | MI | [5 empty] | 16000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 | 138 | C | Y
C | West | ATC LLC | 3158 | 2010-09-15 |  | Petenwell 138/69kV Transformer Replacement | Petenwell 138/69kV Transformer Replacement | WI | [5 empty] | 3246000 | 2015-06-01 | 2015-06-01 | proposed | 138 | 69 | C | Y
C | West | ATC LLC | 3159 | 2010-09-15 |  | West Middleton-Timberlane-Stage Coach Uprate | West Middleton-Timberlane-Stage Coach 69kV line Uprate | WI | [5 empty] | 1808043 | 2015-06-01 | 2015-06-01 | Conceptual | 69 |  | C | Y
C | West | GRE | 2569 | 2010-09-15 | 20138 | Shoal Lake (Lawrence Lake) 115 kV line | Shoal Lake (Lawrence Lake) 115 kV line | MN |  |  | Other | Not Shared | Distribution | 6450514.76 | 2013-12-02 | 2013-12-02 | Planned | 115 |  | C | Y
C | West | GRE | 2600 | 2010-09-15 | 20339 | Big Sandy (LCP) 4.0 mile, 69 kV line | Big Sandy (LCP) 4.0 mile, 69 kV line | MN |  |  | Other | Not Shared | Distribution | 5149000 | 2015-10-30 | 2015-10-30 | Planned | 69 |  | C | Y
C | West | GRE | 2632 | 2010-09-15 | 20385 | Onigum 115 kV Conversion | Onigum 115 kV Conversion | MN | [5 empty] | 5300000 | 2013-12-01 | 2013-12-01 | Proposed | 115 |  | C | Y
C | West | GRE | 3393 | 2010-09-15 | 200332 | Peterson 115 kV Distribution | Convert Peterson Substation from 24 kV to 115 kV operation | MN |  |  | Other | Not Shared | Reliability | 742690 | 2013-11-01 | 2013-11-01 | Planned | 115 |  | C | Y
C | West | OTP, XEL, GRE, MP, MHEB | 3085 | 2009-09-15 | MISO TSR | Dorsey - Maple River - Helena 500kV | Dorsey - Maple River 50% series compensated 500kV line with one 500/345kV 1,200 MVA transformer at Maple River. Maple River - Helena 50% series compensated 500kV line with two 1,200MVA transformers at Helena. | MN |  |  | TDSP | Direct Assigned |  | 1180000000 | 2017-06-01 | 2017-06-01 | Proposed | 500 | 345 | C | Y
C | West | ITCM | 1746 | 2010-07-16 |  | Lakefield-Adams 161kV Rebuild | Rebuild Lakefield-Fox Lake-Rutland-Winnebago-Hayward-Adams 161kV line to double ckt 345 & 161kV. Allow for a 345kV line position for future use. | MN |  |  | BaseRel |  |  | 97580000 | 2011-12-31 | 2015-12-31 | Proposed | 161 |  | C | Y
C | West | OTP, XEL | 3204 | 2011-06-23 |  | Sheyenne - Audubon 230 kV line | Sheyenne - Audubon 230 kV line | MN | ND |  |  |  |  | 6000000 | 2015-12-31 | 2015-12-31 | Planned | 230 |  | C | Y
C | West | ATC LLC | 3510 | 2011-05-16 |  | Mukwonago-St Martins 138 kV Rebuild | Rebuild Mukwonago-Edgewood-St. Martins 138 kV Line, includes replacing jumpers at Edgewood and Mukwonago | WI | [5 empty] | 19200000 | 2017-06-01 | 2017-06-01 | Proposed | 138 |  | C | Y
C | West | ATC LLC | 3511 | 2011-05-16 | F3185, PR04111 | Edgewater-Saukville 345 kV Uprate | AM project to uprate Edgewater to Saukville line clearance issues | WI | [5 empty] | 1798252 | 2011-11-14 | 2011-11-14 | Proposed | 345 |  | C | Y
C | Central | AmerenIL | 1536 | 2007-04-02 |  | Latham-Mason City - Reconductor | Reconductor from Latham Tap to Kickapoo Tap | IL | [5 empty] | 4670000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 1538 | 2010-12-06 |  | Pana, North-Ramsey, East - Rebuild Line | Reconductor 18.43 miles of line to 2000 A summer emergency capability. | IL | [5 empty] | 5500000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 1539 | 2007-04-02 |  | Roxford Substation - Install 345 kV PCB | Install 345 kV PCB on Roxford-Stallings line position | IL | [5 empty] | 1000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 |  | C | Y
C | Central | AmerenIL | 1540 | 2008-12-10 |  | Sidney-Windsor - Reconductor | Reconductor 13.1 miles to 1600 A Summer Emergency Capability | IL | [5 empty] | 3900000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2232 | 2009-09-22 | 57 | MTEP08 Reference Future EHV Overlay - East Moline to Kewanee | Build 345 kV circuit from East Moline to Kewanee in Illinois | IL | [5 empty] | 44000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenIL | 2233 | 2009-09-22 | 58 | MTEP08 Reference Future EHV Overlay - Kewanee to Tazewell | Build 345 kV circuit from Kewanee to Tazewell in Illinois | IL | [5 empty] | 85000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 2242 | 2009-05-06 | 67 | MTEP08 Reference Future EHV Overlay - Norris City to Albion | Build 345 kV circuit from Norris City to Albion in Illinois | IL | [5 empty] | 50000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 2983 | 2009-09-14 |  | Mt. Carmel Capacitor Banks | Mt. Carmel - Install capacitor bank(s). | IL | [5 empty] | 1500000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2985 | 2009-12-10 |  | Monmouth Blvd. Capacitor Bank | Monmouth Blvd 138/69 kV Substation - Install 138 kV 30 Mvar capacitor bank and circuit breaker. | IL | [5 empty] | 1500000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2994 | 2009-12-10 |  | Gillespie Macoupin Substaiton - 2nd. Transformer | Gillespie Macoupin 138-34.5 kV Substation - Tap Wood River-North Staunton 138 kV Line 1436 and make a 138 kV 'in-out' arrangement at the substation with installation of the 2nd. 138-34.5 kV transformer. 2-2000 A, 138 kV PCB's needed. | IL | [5 empty] | 2000000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2995 | 2009-12-10 |  | Brokaw Substation Bus Conductor Replacment | Brokaw 345/138 kV Substation - Replace 477 kcmil ACSR Bus Conductor in Brokaw-Normal East 138 kV Line 1578 position with conductor capable of carrying 1200 A continuously. | IL | [5 empty] | 100000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 2999 | 2009-12-10 |  | LaSalle-Oglesby Main Line 1496 Reconductoring | LaSalle-Oglesby Main 138 kV Line 1496 - Reconductor 2.16 miles of 477 kcmil ACSR and 336 kcmil ACSR with conductor capable of carrying 1200 A under summer emergency conditions. | IL | [5 empty] | 650000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3001 | 2010-12-06 | AMRN10 | Mascoutah Area 345/138 kV Substation | Mascoutah Area 345/138 kV Substation - Install a new 345/138 kV Substation. Supply from the Baldwin-Prairie State 345 kV line. 1-560 MVA 345/138 kV transformer, 3-345 kV PCB's, 1-138 kV PCB. | IL | [5 empty] | 9000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 | 138 | C | Y
C | Central | AmerenIL | 3002 | 2009-12-10 |  | N. Decatur-Clinton Rt. 54 Line 1313 Reconductoring | N. Decatur-Clinton Rt. 54 138 kV Line 1313 - Reconductor 5.41 miles of 336 kcmil ACSR conductor in the N. Decatur-County Hwy. 20 line section with conductor capable of carrying 1200 A under summer emergency conditions. | IL | [5 empty] | 1650000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3004 | 2009-12-10 |  | Gilman Capacitor Bank | Gilman 138-69 kV Substation - Install 138 kV capacitor bank and PCB | IL | [5 empty] | 1500000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3005 | 2009-12-10 |  | S. Belleville-Tilden Terminal Equipment | S. Belleville-Tilden 138 kV Line 1526 - Replace 1200 A terminal equipment (PCB, CT's, and bus conductor) at S. Belleville Substation with equipment capable of carrying 2000 A continuously. | IL | [5 empty] | 1100000 | 2015-12-01 | 2015-12-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3006 | 2009-12-10 |  | Vermilion-Champaign Reconductoring | Vermilion-Champaign 138 kV Line 1396 - Reconductor 26.8 miles of 477 kcmil ACSR with minimum 1200 A SE capability. | IL | [5 empty] | 8100000 | 2016-06-01 | 2016-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenIL | 3011 | 2009-12-10 |  | Joppa-Mound City 161 kV Line Reconductoring | Joppa-Mound City 161 kV Line - Reconductor 23.4 mi. 556 ACSR with conductor capable of carrying 1200 A under summer emergency conditions. | IL | [5 empty] | 7100000 | 2017-06-01 | 2017-06-01 | Conceptual | 161 |  | C | Y
C | Central | AmerenIL | 3012 | 2009-12-10 |  | Normal East Substation Terminal Upgrade | Normal East 138/34 kV Substation - Upgrade 600 A terminal equipment to minimum 1200 A SE capability in the Brokaw-Normal East 138 kV line terminal. | IL | [5 empty] | 100000 | 2017-06-01 | 2017-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3013 | 2009-12-10 |  | Turkey Hill-Cahokia Reinsulation to 345 kV | Turkey Hill-Cahokia 345 kV - Reinsulate the existing Turkey Hill-Cahokia 138 kV Line 1492 (approx. 19 miles) to 345 kV service. | IL | [5 empty] | 1000000 | 2017-06-01 | 2017-06-01 | Proposed | 345 |  | C | Y
C | Central | AmerenIL | 3014 | 2009-12-10 |  | Cape-Joppa 161 kV Line Reconductoring | Cape-Joppa 161 kV Line - Reconductor line (40.27 miles) to 1600 A Summer Emergency Capability. | IL | [5 empty] | 12100000 | 2018-06-01 | 2018-06-01 | Proposed | 161 |  | C | Y
C | Central | AmerenIL | 3015 | 2009-12-10 |  | Grand Tower-E.W Frankfort 345 kV Line | Grand Tower-E.W. Frankfort 345 kV - New 41 mile, 345 kV, 3000 A line. 345 kV PCBs: 2-Grand Tower; 2- E.W. Frankfort | IL | [5 empty] | 82000000 | 2018-06-01 | 2018-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 3016 | 2009-12-10 |  | Galesburg Substation Transformer Addition | Galesburg 345/138 kV Substation - 1-560 MVA 345/138 kV transformer, 3-345 kV PCBs, 1-138 kV PCB | IL | [5 empty] | 18480000 | 2019-11-15 | 2019-11-15 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenIL | 3018 | 2009-09-14 |  | Tazewell-Tremont 138 kV Line | Tazewell-Tremont 138 kV Line - Physically inspect 3 miles of existing deenergized 477 kcmil ACSR line near Tremont Tap (Havana-Danvers 138 kV Line 1352). Construct 3 miles of new 138 kV line with 1200 A summer emergency capability to extend line to Tazew | IL | [5 empty] | 2922000 | 2018-06-01 | 2018-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenIL | 3019 | 2009-09-14 |  | Oglesby 345/138 kV Transformer Addition | Oglesby 345/138 kV Substation - 1-560 MVA 345/138 kV transformer, 1-138 kV PCB | IL | [5 empty] | 6000000 | 2018-06-01 | 2018-06-01 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenIL | 3021 | 2009-09-14 |  | Mound City-Charleston 161 kV Line | Mound City-Charleston 161 kV Line - New 20 mile, 1200 A summer emergency capability line. 3-161 kV PCBs: 2-Mound City, 1-Charleston. | IL | [5 empty] | 23000000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 |  | C | Y
C | Central | AmerenIL | 3023 | 2009-09-14 |  | E. Collinsville-Porter Road 138 kV Reconductoring | E. Collinsville-Porter Road 138 kV Line 1432 - Reconductor 5.15 miles of 477 kcmil ACSR with conductor capable of carrying 2000 A under summer emergency conditions. | IL | [5 empty] | 1600000 | 2018-06-01 | 2018-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenIL | 3026 | 2009-09-14 |  | Havana Plant-138 kV Connection for R.A.T. | Havana Plant 138 kV Switchyard - Add 138 kV Connection for new Reserve Auxiliary Transformer needed to supply new pollution control load. | IL | [5 empty] | 100000 | 2019-06-01 | 2019-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenIL | 3029 | 2010-12-06 | AMRN16 | Gibson City Plant - Increase Outlet Line Capacity | Gibson City Plant 138 kV Outlet - Increase capability of Gibson City-Brokaw and Gibson City-Paxton 138 kV lines. | IL | [5 empty] | 6750000 | 2019-06-01 | 2019-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenIL | 3033 | 2010-12-06 | AMRN18 | Dupo Area 345/138 kV Substation | Dupo Area 345/138 kV Substation - 1-560 MVA Transformer, 8-138 kV PCBs. New 8 mi. 3000 A 345 kV line from Cahokia Substation, 2-345 kV PCBs @ Cahokia, and 138 kV Outlet to Cahokia-Meramec circuits near Lemay Taps. New Dupo-Dupo Ferry 138 kV 2000 A line. | IL | [5 empty] | 22192000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenIL | 3035 | 2009-09-14 |  | Kinmundy-Salem, West 138 kV - Increase Ground Clearance | Kinmundy-Salem, West 138 kV line - Increase clearances to ground. | IL | [5 empty] | 1100000 | 2019-06-01 | 2019-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenIL | 3036 | 2009-09-14 |  | Latham Substation 2nd. 345/138 kV Transformer | Latham 345/138 kV Substation - Install 2nd. 345/138 kV, 448 MVA Transformer. 1-345 kV PCB, 1-138 kV PCB. | IL | [5 empty] | 5000000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenIL | 3037 | 2009-09-14 |  | Rush Island-Dupo 345 kV Line | Rush Island-Dupo 345 kV Line - New 27 mile, 3000 A summer emergency capability line. Design for double-circuit. 2-345 kV PCBs: 1-Rush Island, 1-Dupo. | IL | [5 empty] | 49000000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 3039 | 2009-09-14 |  | Grand Tower-Joppa 345 kV Line | Grand Tower-Joppa 345 kV Line - New 50 mile 345 kV, 3000 A line. 345 kV PCBs: 2-Grand Tower; 1-Joppa. | IL | [5 empty] | 100000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 3040 | 2009-09-14 |  | Tazewell-S. Bloomington 345 kV Line | Tazewell-South Bloomington 345 kV Line - New 35 mile, 345 kV, 3000 A line. 345 kV PCBs: 2 at Tazewell, 3 at South Bloomington switching station. | IL | [5 empty] | 87500000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 3043 | 2009-09-14 |  | LaSalle-Oglesby 345 kV Line | LaSalle-Oglesby 345 kV Line - New 22 mi. 3000 A summer emergency capability line; 1-345 kV PCB at LaSalle, 1-138 kV PCB at Oglesby. | IL | [5 empty] | 44000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 3044 | 2009-09-14 |  | Roxford-Pawnee 345 kV Line | Roxford-Pawnee 345 kV Line - New 60 mile, 3000 A summer emergency capability line. 3-345 kV PCBs (1-Roxford, 2-Pawnee). Install WAMS - PMU at Pawnee on new line terminal. | IL | [5 empty] | 120000000 | 2021-06-01 | 2021-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenIL | 3175 | 2010-05-05 |  | Palmyra Tap-Pawnee 765 kV Line | New 117 mile 765 kV, approx. 4000 A line | IL | [5 empty] | 347557224 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenIL | 3176 | 2010-05-05 |  | Pawnee-Breed 765 kV Line | New 140 mile 765 kV, approx. 4000 A line | IL | [5 empty] | 404702844 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenIL | 3177 | 2010-05-05 |  | Pawnee 765/345 kV Substation | New 2250 MVA, 765/345 kV Substation | IL | [5 empty] | 28200000 | 2020-06-01 | 2020-06-01 | Conceptual | 765 | 345 | C | Y
C | Central | AmerenIL | 3178 | 2010-05-05 |  | Pawnee-Powerton 765 kV Line | New 79 mile 765 kV, approx. 4000 A line | IL | [5 empty] | 224509670 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenIL | 3183 | 2010-05-05 |  | Grand Tower 765/345 kV Substation | New 2250 MVA, 765/345 kV Substation | IL | [5 empty] | 28200000 | 2020-06-01 | 2020-06-01 | Conceptual | 765 | 345 | C | Y
C | Central | AmerenIL | 3184 | 2010-05-05 |  | Grand Tower-Rockport 765 kV Line | New 172 mile 765 kV, approx. 4000 A line | IL | [5 empty] | 494506712 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenIL | 3349 | 2010-09-15 |  | East Galesburg Breaker Replacement | Replace breaker at East Galesburg with 1200 A breaker. Replace terminal equipment to 1200 A capability. | IL | [5 empty] | 1000000 | 2020-06-01 | 2020-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenIL | 3350 | 2010-09-15 |  | East Kewanee-Princeton Tap of Hennepin-East Kewanee Reconductor | Reconductor 477 kcmil ACSR conductor to 1200 A summer emergency capability. Replace terminal equipment at East Kewanee to 1200 A capability. | IL | [5 empty] | 2656000 | 2012-12-01 | 2012-12-01 | Planned | 138 |  | C | Y
C | Central | AmerenIL, Non-MISO | 2197 | 2008-08-05 | 20 | MTEP08 Reference Future EHV Overlay - St. Francois to Rockport | Builds 765 kV circuit from St. Francois Station in Missouri to Rockport Station in Indiana (Located in 3 States: 15% in MO, 56% in IL, 29% in IN | IL | IN,MO |  |  |  |  | 599000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenIL, Non-MISO | 2215 | 2008-08-05 | 40 | MTEP08 Reference Future EHV Overlay - Coffeen to Sullivan | Build 765 kV circuit from Coffeen Station in Illinois to Sullivan Station in Indiana | IL | IN |  |  |  |  | 322000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenMO | 2122 | 2008-02-14 |  | Belleau - GM - 3 to AECI Enon Substation 161 kV line | Belleau - GM - 3 to AECI Enon Substation 161 kV line | MO | [5 empty] | 1896500 | 2011-11-17 | 2011-11-17 | Planned | 161 |  | C | Y
C | Central | AmerenMO | 2292 | 2009-12-23 |  | Kelso 345/161 kV Substation | Replace 336 MVA, 345/161 kV Transformer with 450 MVA Transformer | MO |  |  | BaseRel |  |  | 6134000 | 2016-06-01 | 2016-06-01 | Proposed | 345 | 161 | C | Y
C | Central | AmerenMO | 2987 | 2009-09-14 |  | Taum Sauk Capacitor Banks | Taum Sauk 138 kV Capacitor Banks - 2-30 Mvar banks; 2-138 kV synchronous PCBs. | MO | [5 empty] | 1500000 | 2014-06-01 | 2014-06-01 | Conceptual | 138 |  | C | Y
C | Central | AmerenMO | 2990 | 2009-09-14 | AMRN8 | Conway-Tyson-3 and -4 Increase Ground Clearance | Conway-Tyson-3 and -4 138 kV - Increase ground clearance on Tyson-Orchard Gardens sections (7 miles) | MO | [5 empty] | 700000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 2991 | 2009-12-23 |  | Mason Transformer Replacement | Mason 345/138 kV Substation - Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | MO | [5 empty] | 5000000 | 2014-06-01 | 2014-06-01 | Proposed | 345 | 138 | C | Y
C | Central | AmerenMO | 2993 | 2009-12-23 |  | Dupo Ferry-Buck Knob Reconductoring | Dupo Ferry-Buck Knob 138 kV Line - Replace 22 mi. of 2-300 ACSR with maximum size conductor existing towers will support. | MO | [5 empty] | 6600000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 2996 | 2009-09-14 |  | Montgomery-Spencer Creek - Increase Ground Clearance | Montgomery-Spencer Creek 345 kV - Increase ground clearance on 28 miles of 795 kcmil ACSR conductor and upgrade terminal equipment at Montgomery Substation. | MO | [5 empty] | 9500000 | 2015-06-01 | 2015-06-01 | Proposed | 345 |  | C | Y
C | Central | AmerenMO | 2998 | 2009-09-14 |  | Overton 2nd. Transformer | Overton 345/161 kV Substation - 2nd Transformer - 450 MVA; 1-161 kV PCB, 2-345 kV PCBs, 345 kV Ring Bus | MO | [5 empty] | 5000000 | 2015-06-01 | 2015-06-01 | Conceptual | 345 | 161 | C | Y
C | Central | AmerenMO | 3000 | 2009-09-14 |  | Miller Substation Transformer Addition | Miller 138/161 kV Substation - Install a new 300 MVA 138/161 kV transformer to convert Miller-Zion line to 161 kV operation and increase voltage support to Jefferson City, Missouri area. | MO | [5 empty] | 5000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 | 161 | C | Y
C | Central | AmerenMO | 3007 | 2010-12-06 | AMRN11 | Camden-Ullman 138 kV Line | Camden-Ulman 138 kV Line - Construct approximately 16 miles of 138 kV line between Camden Substation and Ulman (switching station connecting to Maries-Osage-1 138 kV line), with 1600 A summer emergency capability. Install 300 MVA, 161/138 kV transformer | MO | [5 empty] | 29000000 | 2016-06-01 | 2016-06-01 | Proposed | 161 | 138 | C | Y
C | Central | AmerenMO | 3008 | 2009-09-14 |  | Overton Capacitor Bank | Overton 161 kV Capacitor Bank - 1-90 Mvar capacitor bank, 1-161 kV synchronous PCB, 1-161 kV reactor. | MO | [5 empty] | 1500000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 |  | C | Y
C | Central | AmerenMO | 3020 | 2009-09-14 |  | Overton-Columbia Terminal Upgrade | Overton-Huntsdale-Columbia 161 kV - Replace 800 A CT at Overton Terminal with 1200 A unit. | MO | [5 empty] | 50000 | 2018-06-01 | 2018-06-01 | Proposed | 161 |  | C | Y
C | Central | AmerenMO | 3025 | 2010-12-06 |  | Rivermines-N. Farmington - Second 138 kV Line | Rivermines-N. Farmington 138 kV Line - Construct a second 5.5 mile 138 kV line. | MO | [5 empty] | 7500000 | 2019-06-01 | 2019-06-01 | Proposed | 138 |  | C | Y
C | Central | AmerenMO | 3027 | 2009-09-14 | AMRN14 | Campbell Substation 2nd. 345/138 kV Transformer | Campbell 345/138 kV Substation - 2nd 560 MVA transformer; New 12.8 mi. Roxford-Campbell 345 kV 3000 A summer emergency capability line; 2-345 kV PCBs (1-Campbell, 1-Roxford); 1-138 kV PCB @ Campbell. | MO |  |  |  | Shared |  | 6000000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenMO | 3028 | 2009-09-14 | AMRN15 | Campbell-Euclid-Page 138 kV Line Rebuild | Campbell-Euclid-Page 138 kV Line - Rebuild 5.25 mi. double-circuit 138 kV 2000 A SE capability. 3-138 kV PCBs (2-Campbell, 1-Page). Operate Euclid 138 kV Bus-Tie normally closed. | MO | [5 empty] | 21300000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3030 | 2009-09-14 |  | Labadie-Mason 345 kV Line #3 | Labadie-Mason 345 kV Line #3 - New 25 mi. 3000 A summer emergency capability line designed for double-circuit. 345 kV PCBs: 1-Labadie, 1- Mason. Install WAMS - PMU at Labadie on new line terminal | IL | MO |  |  |  |  | 44250000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3031 | 2009-09-14 | AMRN17 | Page Area 345/138 kV Substation | Page Area 345/138 kV Substation - 2-560 MVA transformers. 9-138 kV PCBs: 2-transformer, 1-bus-tie, 6-line (2-Warson, 2-Page, 2-Hunter). | MO | [5 empty] | 11000000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 | 138 | C | Y
C | Central | AmerenMO | 3032 | 2009-12-23 |  | Campbell-Page-Mason 345 kV Line | Campbell-Page-Mason 345 kV Line - New 16.5 mi. 3000 A summer emergency capability line, plus reutilization of 14.5 miles of existing Page-Sioux-4 at 345 kV. | MO | [5 empty] | 35750000 | 2019-06-01 | 2019-06-01 | Proposed | 345 |  | C | Y
C | Central | AmerenMO | 3034 | 2009-09-14 |  | Loose Creek-Kingdom City 345 kV Line | Loose Creek-Kingdom City 345 kV Line - New 25 mile 345 kV, 3000 A line. 2-345 kV PCBs at Loose Creek, 2-345 kV PCBs at Kingdom City.. | MO | [5 empty] | 52000000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3038 | 2009-12-23 |  | Loose Creek-Barnett-Windsor-Pleasant Hill 345 kV Line | Loose Creek-Barnett-Windsor-Pleasant Hill 345 kV Line - New 138 mile 345 kV, 3000 A line. 560 MVA, 345/161 kV transformer at Barnett Substation. 345 kV PCBs: 2 at Loose Creek, 2 at Barnett, 2 at Windsor, 2 at Pleasant Hill. | MO | [5 empty] | 249000000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3042 | 2009-09-14 |  | Palmyra-Thomas Hill-Fairport 345 kV Line | Palmyra-Thomas Hill-Fairport - New 122 mile 345 kV, 3000 A line. 345 kV PCBs: 2 at Palmyra, 2 at Thomas Hill, 2 at Fairport. | MO | [5 empty] | 220000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3045 | 2009-09-14 |  | St. Francois-Fletcher 345 kV Line | St. Francois-Fletcher 345 kV Line - New 48 mi. 3000 A SE capability. 345 kV terminals at St. Francois & Fletcher. Install WAMS - PMU at St. Francois on new line terminal. | MO | [5 empty] | 86000000 | 2021-06-01 | 2021-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3171 | 2010-05-05 |  | West Adair-Fairport 345 kV Line | New 113 mile 345 kV, 3000 A line | MO | [5 empty] | 171818625 | 2018-06-01 | 2018-06-01 | Conceptual | 345 |  | C | Y
C | Central | AmerenMO | 3173 | 2010-05-05 |  | Fairport-Palmyra Tap 765 kV Line | New 176 mile 765 kV, approx. 4000 A line | MO | [5 empty] | 500335836 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenMO | 3174 | 2010-05-05 |  | Palmyra Tap 765/345 kV Substation | New 2250 MVA, 765/345 kV Substation | MO | [5 empty] | 28200000 | 2020-06-01 | 2020-06-01 | Conceptual | 765 | 345 | C | Y
C | Central | AmerenMO | 3179 | 2010-05-05 |  | Palmyra Tap-Montgomery 765 kV Line | New 68 mile 765 kV, approx. 4000 A line | MO | [5 empty] | 192436860 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenMO | 3180 | 2010-05-05 |  | Montgomery 765/345 kV Substation | New 2250 MVA, 765/345 kV Substation | MO | [5 empty] | 28200000 | 2020-06-01 | 2020-06-01 | Conceptual | 765 | 345 | C | Y
C | Central | AmerenMO | 3181 | 2010-05-05 |  | Montgomery-St. Francois 765 kV Line | New 104 mile 765 kV, approx. 4000 A line | MO | [5 empty] | 295069852 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenMO | 3182 | 2010-05-05 |  | St. Francois-Grand Tower 765 kV Line | New 63 mile 765 kV, approx. 4000 A line | MO | [5 empty] | 193607736 | 2020-06-01 | 2020-06-01 | Conceptual | 765 |  | C | Y
C | Central | AmerenMO | 3187 | 2010-06-16 |  | St. Francois 765/345 kV Substation | New 2250 MVA, 765/345 kV Substation | MO | [5 empty] | 28200000 | 2020-06-01 | 2020-06-01 | Conceptual | 765 | 345 | C | Y
C | Central | AmerenMO, AmerenIL | 2195 | 2008-08-05 | 18 | MTEP08 Reference Future EHV Overlay - Montgomery to Coffeen | Builds 765 kV circuit from Montgomery Station in Missouri to Coffeen Station in Illinois | MO | IL |  |  |  |  | 343000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | Central | BREC | 3435 | 2010-11-15 | LRP1 | Rome Junction to West Owensboro 69 kV reconductor. | Reconductor 5.8 miles of 3/0 and 267 MCM ACSR with 336 MCM ACSS | KY | [5 empty] | 440000 | 2017-12-31 | 2017-12-31 | Proposed | 69 |  | C | Y
C | Central | BREC | 3436 | 2010-11-15 | LRP2 | Wilson to Sacremento 69 kV line addition | New 11 mile line and line terminal at Wilson | KY | [5 empty] | 2100000 | 2018-12-31 | 2018-12-31 | Proposed | 69 |  | C | Y
C | Central | BREC | 3437 | 2010-11-15 | LRP3 | Thruston Junction to East Owensboro reconductor. | Reconductor .4 miles of 3/0 ACSR with 336 MCM ACSR | KY | [5 empty] | 40000 | 2018-12-31 | 2018-12-31 | Proposed | 69 |  | C | Y
C | Central | BREC | 3438 | 2010-11-15 | LRP4 | Daviess County to Philpot Tap reconductor. | Reconductor 7.7 miles of 267 MCM ACSR with 336 MCM ACSS | KY | [5 empty] | 580000 | 2018-12-31 | 2018-12-31 | Proposed | 69 |  | C | Y
C | Central | BREC | 3439 | 2010-11-15 | LRP5 | Ensor 161/69 kV Substation | Construct new 161/69 kV substation with 56 MVA transfomer. | KY | [5 empty] | 6200000 | 2022-12-31 | 2022-12-31 | Proposed | 161 | 69 | C | Y
C | Central | BREC | 3440 | 2010-11-15 | LRP6 | Reid EHV 161/69 kV transformer | Add a 56 MVA transformer to the existing Reid EHV substation. | KY | [5 empty] | 5000000 | 2024-12-31 | 2024-12-31 | Proposed | 161 | 69 | C | Y
C | Central | BREC | 3441 | 2010-11-15 | LRP7 | Olivet Church Road to Olivet Church Road Tap 69 kV reconductor. | Reconductor 1.4 miles of 4/0 ACSR with 336 MCM ACSS | KY | [5 empty] | 150000 | 2020-12-31 | 2020-12-31 | Proposed | 69 |  | C | Y
C | Central | BREC | 3442 | 2010-11-15 | LRP8 | White Oak transformer addition | Add a second 56 MVA transformer to the White Oak 161/69 kV substation. | KY | [5 empty] | 1900000 | 2024-12-31 | 2024-12-31 | Proposed | 161 | 69 | C | Y
C | Central | BREC | 3443 | 2010-11-15 | LRP9 | Hardinsburg 161/69 transformer replacements | Replace both 50 MVA 161/69 kV transformers with 100 MVA transformers. | KY | [5 empty] | 4000000 | 2017-12-31 | 2017-12-31 | Proposed | 161 | 69 | C | Y
C | Central | BREC | 3444 | 2010-11-15 | LRP10 | Meade County 161/69 transformer addition | Add a third 56 MVA transformer to the existing Meade County substation. | KY | [5 empty] | 700000 | 2020-12-31 | 2020-12-31 | Proposed | 161 | 69 | C | Y
C | Central | BREC | 3445 | 2010-11-15 | LRP11 | Brandenburg 69 kV capacitor addition | Add a 6 MVAR capacitor in the Brandenburg/Battletown area. | KY | [5 empty] | 300000 | 2020-12-31 | 2020-12-31 | Proposed | 69 |  | C | Y
C | Central | BREC | 3446 | 2010-11-15 | LRP12 | Hardinsburg No. 1 to Harned 69 kV reconductor. | Reconductor 2 miles of 3/0 ACSR with 336 MCM ACSS | KY | [5 empty] | 170000 | 2022-12-31 | 2022-12-31 | Proposed | 69 |  | C | Y
C | Central | DEM | 840 | 2009-09-17 | AMIN0075 | Rushville 69kV Cap | Add 14.4 MVAR 69kV capacitor at Rushville. | IN |  |  | Other | Not Shared |  | 510845.03 | 2016-06-01 | 2016-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 1249 | 2009-09-17 | 602G6621 | Frankfort 230 36MVAR 69kV capacitor | Install 36 MVAR 69kV capacitor | IN |  |  | Other | Not Shared |  | 632358 | 2016-12-31 | 2016-12-31 | Planned | 69 |  | C | NT
C | Central | DEM | 1264 | 2011-03-25 | 702G6714 | Speed | Replace existing 345/138 transformer at Speed with a new transformer rated at 3,000A or higher. | IN |  |  | BaseRel | Shared |  | 7541500 | 2022-06-01 | 2022-06-01 | Alternative | 345 | 138 | C | Y
C | Central | DEM | 1518 | 2011-01-11 | 202D7784 | Curliss 138/69 | Install new Curliss 138-69 kV sub in the 5884 ckt, 150 MVA xfmr, Install one 69 kV circuit. Convert Glen Este and Batavia dist subs from 34 to 69kV primary voltage. | OH |  |  | Other | Not Shared |  | 9818000 | 2016-06-01 | 2016-06-01 | Proposed | 138 | 69 | C | Y
C | Central | DEM | 1571 | 2011-01-11 | AMIN0060 | Rockville (IPL) to Avon East new 138KV line | Construct 4.3 miles / 954ACSR of 138kv line from IPL Rockville to Avon East | IN |  |  | Other |  |  | 2980000 | 2015-06-01 | 2015-06-01 | Alternative | 138 |  | C | Y
C | Central | DEM | 1900 | 2009-09-17 | AMIN0220 | Avon Industrial Park 138 (or 69)-12kV new dist sub | Avon Industrial Park (aka Central Logistics) - Construct 69/138-12kV - 22.4 MVA sub and 2.6 mile - 69kV radial line from roughly the Avon South sub - unknown if this will be a 69 or 138 kv sub | IN |  |  | Other |  |  | 923000 | 2015-06-01 | 2015-06-01 | Proposed | 138 | 12 | C | NT
C | Central | DEM | 1904 | 2009-01-05 | AMIN0065 | Batesville to Hillenbrand 69kV uprate | Uprate 69kV Batesville to Hillenbrand to 100C – 4/0acsr – 2.1 miles – 69107 ckt | IN |  |  | Other | Not Shared |  | 115960.76 | 2015-06-01 | 2015-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2124 | 2009-09-17 | 804J3044 | Brooklyn to HE Brooklyn 69kV Reconductor | Brooklyn Sub to HE Brooklyn Sub reconductor 1.28 miles of 6940 line 4/0 Cu with 954ACSR@100C | IN |  |  | Other | Not Shared |  | 320000 | 2020-06-01 | 2020-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2125 | 2009-09-17 | 802J3045 | Centerton 138/69kV Bk 1 replacement | Upgrade/replace existing 75MVA 138/69kV bank with 120MVA bank | IN |  |  | Other |  |  | 3091000 | 2020-06-01 | 2020-06-01 | Planned | 138 | 69 | C | NT
C | Central | DEM | 2129 | 2009-09-17 | 604J3046 | Plainfield S. to HE Mooresville Jct 69kV reconductor | Plainfield South to HE Mooresville Jct 69kV reconductor 4/0Cu with 954ACSR - 2.03 miles | IN |  |  | Other | Not Shared |  | 980000 | 2020-06-01 | 2020-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2135 | 2008-04-07 | 602J3057 | Franklin 230 Sub 69kV Cap | Franklin 230 Sub 69kV Cap - Install 36MVAR 69kV bus capacitor bank | IN |  |  | Other | Not Shared |  | 400000 | 2014-06-15 | 2014-06-15 | Planned | 69 |  | C | NT
C | Central | DEM | 2139 | 2008-04-07 | 602J3054 | Greenwood West Sub 69kV #2 switch upgrade | Greenwood West Sub - upgrade (or replace, if required) 69kV Loadbreak switch #2 for 1200amp capacity in the 6999 ckt. | IN |  |  | Other | Not Shared |  | 50000 | 2016-06-30 | 2016-06-30 | Planned | 69 |  | C | NT
C | Central | DEM | 2140 | 2009-09-17 | AMIN0063 | Greenwood West to Lenore Jct 69kV reconductor | Greenwood West to Lenore Jct reconductor 69kV - 6949 ckt. with 477ACSR @ 100C conductor | IN |  |  | Other |  |  | 1377500 | 2015-06-30 | 2015-06-30 | Planned | 69 |  | C | NT
C | Central | DEM | 2144 | 2008-04-07 | 604J3062 | Franklin 230 to Earlywood 69kv Reconductor | Franklin 230kV sub to Earlywood sub reconductor 1.06 mile - 69kV - 69165 line with 954ACSR@100C | IN |  |  | Other | Not Shared |  | 424000 | 2015-06-30 | 2015-06-30 | Planned | 69 |  | C | NT
C | Central | DEM | 2145 | 2011-03-25 | 602J3065 | Franklin 230/69 Bks 1&2 Replacement | Franklin 230 sub - Replace 230/69kV banks 1&2 each with a 200MVA LTC transformer | IN |  |  | Other |  |  | 4800000 | 2020-06-01 | 2020-06-01 | Planned | 230 | 69 | C | Y
C | Central | DEM | 2146 | 2008-04-07 | 604J3063 | HE Honey Creek Jct to Frances Creek Jct 69kv reconductor | HE Honey Creek Jct to Frances Creek Jct. reconductor 69kV - 1.12 mile line section of the 69102 ckt. with 954ACSR 100C conductor. | IN |  |  | Other | Not Shared |  | 420000 | 2015-06-30 | 2015-06-30 | Planned | 69 |  | C | NT
C | Central | DEM | 2147 | 2008-04-07 | 604J3060 | Whiteland to Madison J 69kv reconductor | Whiteland Sub to Greenwood North Tap to Madison Ave Jct reconductor 3.44 mile 69kV - 6997 line with 954ACSR 100C conductor. | IN |  |  | Other |  |  | 1376000 | 2015-06-30 | 2015-06-30 | Planned | 69 |  | C | NT
C | Central | DEM | 2247 | 2008-08-05 | 75 | MTEP08 Reference Future EHV Overlay - 'Gwynn 765/345 Autotransformation | Add Gwynn 765/345 kV autotransformer in Indiana | IN | [5 empty] | 20000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | Central | DEM | 2328 | 2009-09-17 | 704J3100 | Speed to HE Bethany 69kV - 6955 Reconductor Ph2 | Speed to HE Bethany 69kV - 6955 Reconductor Ph2 - Replace 1.6 miles of 4/0 ACSR with 477 ACSR (new limiter 600A switches) | IN |  |  | Other | Not Shared |  | 480000 | 2015-06-01 | 2015-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2329 | 2009-09-17 | 704J3098 | Clarksville to Indiana Arsenal 69kv - 6955 ckt. reconductor | Clarksville to Indiana Arsenal 69kv - 6955 ckt. reconductor 1.1 miles of 4/0acsr with 477ACSR at 100C (this is Phase 2 remainder of 4/0ACSR in this line section) | IN |  |  | Other | Not Shared |  | 330000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2330 | 2009-09-17 | 704J3095 | New Albany to HE Georgetown 69kv - 6970 ckt. Reconductor | New Albany to HE Georgetown 69kv - 6970 ckt. Reconductor 1.24 miles of 4/0acsr with 477acsr@100C | IN |  |  | Other | Not Shared |  | 666000 | 2014-06-01 | 2014-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2864 | 2009-09-17 | AMIN0144 | Centeron to Martinsville 69kV - 69163 ckt. Reconductor | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | IN | [5 empty] | 1110000 | 2020-06-01 | 2020-06-01 | Planned | 69 |  | C | NT
C | Central | DEM | 2868 | 2009-09-14 | X04C7993 | Fairfax to Senco 69kV - F868 Reconductor | F868 - Reconductor Fairfax to Senco - Replace 4/0 ACSR with 954 ACSR - Approx 4.6 miles | OH | [5 empty] | 1711992 | 2014-06-01 | 2014-06-01 | Proposed | 69 |  | C | NT
C | Central | DEM | 2873 | 2009-09-14 | AMIN0216 | Danville E. 69kV looped feed | Construct new Danville East substation near HRH hospital - single 22.4MVA transformer - 6945 ckt to be looped through | IN | [5 empty] | 500000 | 2018-06-01 | 2018-06-01 | Proposed | 69 | 12 | C | NT
C | Central | DEM | 3382 | 2010-10-12 | AMIN0341 | Vincennes Vigo St. 138kV Dist Sub | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV | IN | [5 empty] | 1800000 | 2017-12-31 | 2017-12-31 | Planned | 138 | 12 | C | Y
C | Central | DEM, IPL | 2783 | 2010-05-08 |  | Wheatland - Bloomington 345 kV line | Build new 345 kV circuits from Wheatland Power Facility to Bloomington substation | IN | [5 empty] | 105000000 | 2012-05-01 | 2012-05-01 | Proposed | 345 |  | C | Y
C | Central | DEM, Non-MISO | 2203 | 2008-08-05 | 27 | MTEP08 Reference Future EHV Overlay - Greentown to Blue Creek | Build 765 kV circuit from Greentown Station to Blue Creek Station in Indiana | IN | [5 empty] | 191000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | Central | DEM, Non-MISO | 2213 | 2008-08-05 | 38 | MTEP08 Reference Future EHV Overlay - Ghent to Buffinton | Build 345 kV circuit from Ghent Station to Buffington Station in Kentucky | KY | [5 empty] | 47000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | Central | IPL | 2246 | 2008-08-05 | 74 | MTEP08 Reference Future EHV Overlay - Pete 765/345 Autotransformation | Add Pete 765/345 kV autotransformer in Indiana | IN | [5 empty] | 20000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | Central | IPL | 2897 | 2009-09-14 | 2052 | Petersburg - Frances Creek - Hanna 345 kV line rating upgrade | Increase line rating from 956 to 1195 MVA | IN |  |  | BaseRel | Not Shared |  | 2500000 | 2013-06-01 | 2013-06-01 | Proposed | 345 |  | C | Y
C | Central | IPL | 2898 | 2009-09-14 | New1 | Hanna - Southeast 138 kV line rating upgrade | Increase line rating from 287 to 574 MVA. Remove operating guide # 2007-S-012-C Hanna-Southeast-138-IPL. | IN |  |  | BaseRel | Not Shared |  | 4000000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | Central | IPL | 2899 | 2009-09-14 | New2 | Guion - Whitestown 345 kV line rating upgrade | Increase line rating from 956 to 1195 MVA | IN |  |  | BaseRel | Not Shared |  | 1000000 | 2015-06-01 | 2015-06-01 | Proposed | 345 |  | C | Y
C | Central | ITCM, Non MISO | 2198 | 2008-08-05 | 22 | MTEP08 Reference Future EHV Overlay - Rockcreek to Pontiac | Builds 765 kV circuit from Rock Creek Station in Iowa to Pontiac Station in Illinois | IA | IL |  |  |  |  | 378000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | Central | MEC, AmerenMo | 2194 | 2008-08-05 | 17 | MTEP08 Reference Future EHV Overlay - Toledo to Montgomery | Builds 765 kV circuit from Toledo Station in Iowa to Montgomery Station in Missouri | IA | MO |  |  |  |  | 871000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | Central | Non-MISO | 2199 | 2008-08-05 | 23 | MTEP08 Reference Future EHV Overlay - Pontiac to Dequine | Builds 765 kV circuit from Pontiac Station in Illinois to Dequine Station in Indiana | IL | IN |  |  |  |  | 265000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | Central | Non-MISO | 2200 | 2008-08-05 | 24 | MTEP08 Reference Future EHV Overlay - Dequine to "Chicago" | Build 765 kV circuit from Dequine Station to New South Chicago Station in Indiana | IN | [5 empty] | 161000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | East | ATC LLC, ITC | 2208 | 2008-08-05 | 33 | MTEP08 Reference Future EHV Overlay - Dead River to Livingston | Build 345 kV circuit from Dead River Station to Livingston Station in Michigan | MI | [5 empty] | 329000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | East | ITC | 694 | 2010-01-06 | ITC9 | Saratoga Station | Saratoga 345/120 kV switching station | MI | [6 empty] | 2018-12-31 | 2018-12-31 | Proposed | 345 | 120 | C | Y
C | East | ITC | 908 | 2010-01-06 | ii | Lulu Station | Tap the Majestic to Lemoyne and Milan to Allen Junction to Monroe 3-4 345 kV circuits into a new 345 kV Switching Station at the Lulu site. Project also adds three miles 345 kV double circuit tower from Monroe to cut the Lulu-Leymoyne circuit into Monroe, moving the Leymone 345 kV interconnection with First Energy to the Monroe 3-4 345 kV bus | MI | [6 empty] | 2018-06-01 | 2018-06-01 | Proposed | 345 |  | C | Y
C | East | ITC | 1012 | 2008-01-10 | zz | Wayne - Newburg Split | Establish new Wayne-Newburgh 120 kV circuit 3 using currently paralleled wire from existing Wayne-Newburgh circuit 2 | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 1295 | 2010-01-06 |  | Quaker to Southfield #2 120 kV | Rebuild the existing Quaker - Drexel - Southfield line to double-circuit and construct a new Quaker - Southfield #2 120 kV line (7.5 miles total). | MI | [6 empty] | 2016-06-30 | 2016-06-30 | Proposed | 120 |  | C | Y
C | East | ITC | 1382 | 2006-10-24 | The 765 | Michigan 765 kV Backbone | Project constructs a 765 kV circuit from AEP's Cook station to a new 765 kV station at the Kenowa 345 kV (METC) station including one 765/345 kV transformer at Kenowa. A new 765 kV circuit from the Kenowa station to a new 765 kV station at the Denver location including a 765/138 kV transformer. A new 765 kV circuit from the Denver station to a new 765 kV station at the Sprague Creek location including a 765/345 kV transformer at Sprague Creek. A new 765 kV circuit from the Sprague Creek station to a new 765 kV station at the Bridgewater site including two 765/345 kV transformers. A new 765 kV circuit from Bridgewater to a new 765 kV station near the Indiana - Ohio border tapping the Dumont to Marysville 765 kV circuit. A new 765 kV circuit from the Bridgewater station to AEP's South Canton 765 kV station. The project will also tap the Blackfoot to Madrid 345 kV circuit at the new Sprague Creek 345 kV station and create two Blackfoot to Sprague Creek 345 kV circuits and one Madrid to Sprague Creek 345 kV circuit. And tap the Majestic to Lulu and Majestic to Milan 345 kV circuits at the new Bridgewater 345 kV station and create two Majestic to Bridgewater 345 kV circuits and a Bridgewater to Milan 345 kV circuit and a Bridgewater to Lulu 345 kV circuit. Other options are also being considered including HVDC. | MI | IN,OH |  |  |  |  | 2500000000 | 2016-12-31 | 2016-12-31 | Proposed | 765 | 138 | C | Y
C | East | ITC | 1550 | 2008-12-09 | ITC32 | Hager - Sunset 120 kV | Transposes the existing cabled line entrance of the Hager-Sunset 120 kV Line with the overhead line entrance of the Sunset-Southfield 120 kV line to increase the thermal rating of Hager-Sunset. | MI | [6 empty] | 2015-05-31 | 2015-05-31 | Proposed | 120 |  | C | Y
C | East | ITC | 1854 | 2010-01-06 |  | Trenton Channel - Riverview 120kV | Install a new 120 kV circuit from Trenton Channel to Riverview utilizing the existing de-energized Trenton Channel to Jefferson circuit to get from Trenton Channel to Jefferson, or rebuild it if required, and then from Jefferson to Riverview either install a new 120 kV single circuit tower line or replace the existing double circuit towers with triple circuit towers. Also reconductor/rebuild Trenton Channel to Jefferson 120 kV #4 circuit (3.53 miles). | MI | [6 empty] | 2018-06-01 | 2018-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 1858 | 2008-01-10 |  | Wayne 345 kV Overloaded S.E. Replacement | Replace various pieces of station equipment that are overloaded at Wayne station under normal conditions and for various contingencies. | MI | [6 empty] | 41426 | 41426 | Proposed | 345 |  | C | Y
C | East | ITC | 2205 | 2008-08-05 | 29 | MTEP08 Reference Future EHV Overlay - Evans to Spreague | Build 765 kV circuit from Evans Station to Spreague Station in Michigan | MI | [5 empty] | 304000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | East | ITC | 2206 | 2008-08-05 | 31 | MTEP08 Reference Future EHV Overlay - Spreague to Bridgewater | Build 765 kV circuit from Spreague Station to Bridgewater Station in Michigan | MI | [5 empty] | 135000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | East | ITC | 2933 | 2009-09-14 |  | Superior - Wayne 120 kV Rebuild | Rebuild the 10.5 miles of the Superior to Wayne 120 kV circuit from 477 ACSR to 954 ACSR on new structures. | MI |  |  | BaseRel | Shared |  | 8800000 | 2013-06-01 | 2013-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3129 | 2010-01-06 |  | Belle River - Bunce Creek 230 kV | Construct a new 230 kV line between Belle River and Bunce Creek substations. This project includes a 345/230 kV transformer at Belle River and 230/120 kV transformer at Bunce Creek (13.5 miles total). | MI | [6 empty] | 2017-06-01 | 2017-06-01 | Proposed | 345 | 230 | C | Y
C | East | ITC | 3130 | 2010-01-06 |  | Thumb Area 120 kV Capacitors | Install a 50 MVAR capacitor at the Stratford and Wabash 120 kV stations. | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3140 | 2010-01-06 |  | Belle River - St. Clair #2 345 kV | Build a second 345 kV circuit from Belle River to St. Clair (1.12 miles total). | MI | [6 empty] | 2017-06-01 | 2017-06-01 | Proposed | 345 |  | C | Y
C | East | ITC | 3141 | 2010-01-06 |  | Redrun - Chestnut #2 120 kV & L-N-NW - Lincoln 120 kV | Build a new 120 kV line between Redrun and Chestnut (5 miles total) | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3142 | 2010-01-06 |  | L-N-NW - Lincoln 120 kV | Rebuild 2.95 miles of 477 ACSR to 954 ACSR on the L-N-NW - Lincoln 120 kV line | MI | [6 empty] | 2016-06-01 | 2016-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3143 | 2010-01-06 |  | Northwest - Southfield 120 kV | Rebuild 0.13 mile of 477 ACSR to 1431 ACSR and replace the line entrance at Northwest substation. | MI | [6 empty] | 2019-06-01 | 2019-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3147 | 2010-01-06 |  | Phoenix 120 kV Capacitor | Install a 75 MVAR 120 kV capacitor at Phoenix. | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3148 | 2010-01-06 |  | Riverview - I-N-RV 120 kV | Replace wavetrap at Riverview. | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 120 |  | C | Y
C | East | ITC | 3496 | 2011-03-28 |  | NERC Alert Facility Ratings for 2012 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI | [6 empty] | 2012-12-31 | 2012-12-31 | Planned |  |  | C | Y
C | East | ITC | 3497 | 2011-03-28 |  | NERC Alert Facility Ratings for 2013 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI | [6 empty] | 2013-12-31 | 2013-12-31 | Planned |  |  | C | Y
C | East | ITC | 3498 | 2011-03-28 |  | NERC Alert Facility Ratings for 2014 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI | [6 empty] | 2014-12-31 | 2014-12-31 | Planned |  |  | C | Y
C | East | ITC, Non-MISO | 2204 | 2008-08-05 | 28 | MTEP08 Reference Future EHV Overlay - Cook to Evans | Build 765 kV circuit from Cook Station to Evans Station in Michigan | MI | [5 empty] | 319000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | East | ITC, Non-MISO | 2207 | 2008-08-05 | 32 | MTEP08 Reference Future EHV Overlay - Bridgewater to Blue Creek | Build 765 kV circuit from Bridgewater Station in Michigan to Blue Creek Station in Indiana (1% in Indiana, 26% in OH, 73% in MI) | MI | [5 empty] | 447000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | East | ITC, Non-MISO | 2209 | 2008-08-05 | 34 | MTEP08 Reference Future EHV Overlay - Bridgewater to South Canton | Build 765 kV circuit from Bridgewater Station in Michigan to South Canton Station in Ohio | MI | OH |  |  |  |  | 538000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | East | METC | 642 | 2005-07-27 | 57 | Argenta - Hazelwood(Sag) 138 ckt # 1 | Argenta - Hazelwood(Sag) 138 ckt # 1 | MI |  |  |  | Excluded |  | 50000 | 2017-06-01 | 2017-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 987 | 2005-07-27 | 118 | Emmet - Stover 138 kV Line | Build 30 miles new 138 kV line, 795 ACSS | MI | [5 empty] | 10250000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1432 | 2010-01-06 | 180 | Withey Lake-Twining 138kV line | Rebuild 0.2 miles of Withey Lake-Twining 138kV line | MI | [5 empty] | 100000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1573 | 2008-10-01 | 198 | Donaldson Creek 138kV Capacitor | Install minimum 23.3 MVAR 138kV capacitor | MI | [6 empty] | 2011-06-01 | 2011-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1657 | 2007-10-26 |  | Terminal Equipment Upgrade | throughout system | MI | [8 empty] | Proposed |  |  | C | Y
C | East | METC | 1795 | 2008-01-10 |  | David Jct. - Bingham 138kV | Rebuild 19 miles of 138kV 336.4 ACSR to 954 ACSR. | MI |  |  | BaseRel | TBD |  | 11700000 | 2012-06-01 | 2012-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1800 | 2008-01-10 |  | Argenta-Riverview 138kV | Fix Sag limit, Retap or upgrade 1200A CT's at both ends, Upgrade 1200A Breaker 377 and 1200A Switch 377 at Riverview | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1804 | 2010-01-06 |  | Marquette - Easton Jct. 138kV | Upgrade relaying at Marquette | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1805 | 2010-01-06 |  | Livingston-Emmet-Oden 138kV | Rebuild the Livingston-Emmet and Emmet-Oden 138kV circuits with 954 ACSR DCT, creating two circuits from both Livingston-Emmet and Emmet-Oden. Total line rebuild is 33 miles | MI | [6 empty] | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1807 | 2010-01-06 |  | Murphy - Bullock 230kV | Swap the existing Bullock-Gleaner and Tittabawassee-Begole 138 kV lines, and open the Begole-Tittabawassee 138 kV line, and build 3.2 miles of new DCT into Richland, creating Bullock -Richland, Richland-Begole, and Tittabawassee-Gleaner 138 kV lines. Convert 8.3 miles of the new Bullock to Richland 138 kV line to 230 kV 954 ACSR. Install a new 345/230 kV transformer at Richland and a new 230/138 kV transformer at Bullock. | MI | [6 empty] | 2016-06-01 | 2016-06-01 | Proposed | 345 | 138 | C | Y
C | East | METC | 1808 | 2008-01-10 |  | Four Mile - Cowan Lake Jct. | Rebuild 15.5 miles of 336/477 to 954 ACSR. | MI | [6 empty] | 2017-06-01 | 2017-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1811 | 2008-01-10 |  | Keystone - Gray Rd. 138kV | Construct a new 9 mile 138kV 954 ACSR circuit from Keystone to Gray Road. | MI | [6 empty] | 2018-06-01 | 2018-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1816 | 2010-01-06 |  | Mecosta - Croton 138kV | Rebuild 22 miles of 138kV 110 CU to 954 ACSR. Prebuild to 230kV construction. | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 1831 | 2010-01-06 |  | Northern Michigan 230 kV Loop | Cut in the existing Hampton -Tittabawassee 345 kV and Thetford -- Tittabawassee 2 345 kV circuits to a new 345 kV station, Crane Rd. Construct a 230 kV loop from Crane Rd to Twining to Mio to Livingston to Plum to Keystone to Tippy to a new station, Sunoco, which is formed by reconfiguring the Ludington -- Kenowa 1 345 kV circuit into it. Install 345/230 kV transformers at Crane Rd, Mio, Livingston, Keystone, and Sunoco, and 230/138 kV transformers at Twining, Mio, Livingston, Plum, Keystone, and Tippy. The total 230 kV circuit mileage would be approximately 330 miles and roughly 320 miles would be along the existing ROW. | MI | [6 empty] | 2019-06-01 | 2019-06-01 | Proposed | 345 | 138 | C | Y
C | East | METC | 2490 | 2010-01-06 |  | North Belding - Vergennes 138kV | Upgrade terminal equipment. | MI |  |  | BaseRel | Not Shared |  | 550000 | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 2810 | 2009-06-26 |  | Delhi - Canal Jct 138kV | Rebuild 7.5 miles of 138kV line to 954 ACSR | MI | [5 empty] | 5500000 | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 2811 | 2010-10-20 |  | East Tawas - Karn 138kV | Rebuild 56 miles of 138kV to 954 ACSR. Does not include the 12.3 miles of rebuild from 2011 MTEP project Cottage Grove - East Tawas 138kV rebuild. | MI | [5 empty] | 51000000 | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3103 | 2009-08-28 |  | Gallagher 345 kV additional breakers | Add two 345kV breakers and convert the Gallagher 345 kV side to a three breaker ring | MI |  |  | BaseRel | Not Shared |  | 5000000 | 2014-12-31 | 2014-12-31 | Proposed | 345 |  | C | Y
C | East | METC | 3128 | 2010-01-06 |  | Emmet - Riggsville and Livingston - Riggsville #2 138 kV Lines | Construct a new 138 kV circuit from Emmet to Riggsville (25 miles total), 954 ACSR and install Livingston to Riggsville 138 kV circuit #2 (40 miles total) | MI | [6 empty] | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3131 | 2010-01-06 |  | Bil-Mar Jct.- Port Sheldon Jct. 138 kV Sag Remediation | Improve sag clearance | MI | [6 empty] | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3132 | 2010-01-06 |  | Tallmadge - Tyler 138 kV Sag Remediation | Improve sag clearance | MI | [6 empty] | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3133 | 2010-01-06 |  | Claremont - Cornell 138 kV #2 | Rebuild/Reconductor the Bell Rd to N. Corunna and the Cornell to N. Corunna sections of 115 CU (4.34 miles). | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3134 | 2010-01-06 |  | Weadock Station 138 kV | Terminal Equipment upgrade at Weadock | MI | [6 empty] | 2012-06-01 | 2012-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3135 | 2010-01-06 |  | Airport - Alpena #2 138 kV | Rebuild the existing Airport - Alpena circuit on DCT's while creating a second circuit from Airport to Alpena. | MI | [6 empty] | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3136 | 2010-01-06 |  | Alpena - Iosco 138 kV | Rebuild 20 miles from Alpena to Spruce Rd and replace limiting station equipment. | MI | [6 empty] | 2017-06-01 | 2017-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3137 | 2010-01-06 |  | Bard Road - Warren 138 kV | Rebuild 20 miles from Bard Rd to Warren and replace limiting station equipment. | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3138 | 2010-01-06 |  | Mio-Gaylord 138 kV | Terminal Equipment upgrade at Mio | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3144 | 2010-01-06 |  | Argenta - Morrow 138 kV | Terminal Equipment upgrade at Morrow | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3145 | 2010-01-06 |  | Blackstone - Leoni 138 kV #1, #2 and #3 | Replace the 636 ACSR trainers at Blackstone substation. Upgrade the relaying at Leoni and Blackstone. | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3146 | 2010-01-06 |  | Battle Creek - Verona # 2 138 kV | Replace the 795 ACSR trainer at Verona substation. | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3149 | 2010-01-06 |  | Four Mile Station 138 kV | Replace the 2-4/0 Cu trainer at Four Mile. | MI | [6 empty] | 2013-06-01 | 2013-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3150 | 2010-01-06 |  | North Belding - Bricker Jct 138 kV | Replace the 336.4 ACSR trainer at North Belding. | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3151 | 2010-01-06 |  | Spaulding - Pettis Jct. 138 kV | Replace the 795 ACSR trainer at Spaulding. | MI | [6 empty] | 2014-06-01 | 2014-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3152 | 2010-01-06 |  | Riggsville to McGulpin 138 kV | Replace 266.8 ACSR trainer at McGulpin and 336.4 ACSR trainer at Riggsville. | MI | [6 empty] | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3153 | 2010-01-06 |  | Oden to McGulpin 138 kV | Replace 336.4 ACSR trainer at McGulpin. | MI | [6 empty] | 2016-06-01 | 2016-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3300 | 2010-10-20 | 14 | Stover - Livingston Rebuild | Rebuild 22.2 miles 138 kV line | MI | [6 empty] | 2015-06-01 | 2015-06-01 | Proposed | 138 |  | C | Y
C | East | METC | 3492 | 2011-03-28 |  | NERC Alert Facility Ratings for 2012 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI | [6 empty] | 2012-12-31 | 2012-12-31 | Planned |  |  | C | Y
C | East | METC | 3493 | 2011-03-28 |  | NERC Alert Facility Ratings for 2013 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI | [6 empty] | 2013-12-31 | 2013-12-31 | Planned |  |  | C | Y
C | East | METC | 3494 | 2011-03-28 |  | NERC Alert Facility Ratings for 2014 | Verify and remediate facilities as required due to the industry-wide NERC alert | MI | [6 empty] | 2014-12-31 | 2014-12-31 | Planned |  |  | C | Y
C | East | MPPA | 2079 | 2009-09-14 | 17-4 | SA Switches | Replacing 600 Amp switches with 1200 Amp switches at the South Airport Sub. | MI | [5 empty] | 200000 | 2015-07-01 | 2015-07-01 | Planned | 69 |  | C | NT
C | East | MPPA | 2080 | 2009-09-14 | 17-5 | BWX Switches | Replacing 600 Amp switches with 1200 Amp switches at the Barlow Junction. | MI | [5 empty] | 200000 | 2019-07-01 | 2019-07-01 | Planned | 69 |  | C | NT
C | East | MPPA | 2081 | 2009-09-14 | 17-6 | CDX Switches | Replacing 600 Amp switches with 1200 Amp switches at the Cass Road Junction. | MI | [5 empty] | 200000 | 2019-07-01 | 2019-07-01 | Planned | 69 |  | C | NT
C | East | NIPS | 1973 | 2010-04-04 | X7L6803 | Leesburg to Northeast -- Upgrade Capacity | Increase circuit capacity between Leesburg and Northeast (8.5 mi.). Upgrade to 954 KCM ACSR. | IN |  |  | BaseRel | Not Shared |  | 5279000 | 2017-12-01 | 2017-12-01 | Conceptual | 138 |  | C | Y
C | East | NIPS | 1979 | 2009-09-14 | 71C6817 | Maple Sub - 69 kV Switched Capacitors | Add two steps of 8.1 MVAR capacitors on the Maple Substation 69 kV bus. | IN |  |  | Other | Not Shared |  | 1080000 | 2014-12-01 | 2014-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 1980 | 2009-09-14 | 71C7203 | Babcock Sub - 69 kV Switched Capacitors | Add two to three steps of 9.0 MVAR capacitors on the Babcock Substation 69 kV bus. . | IN |  |  | Other | Not Shared |  | 1052000 | 2013-12-01 | 2013-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 1981 | 2009-09-14 | 71C7204 | Kreitzburg Sub - 69 kV Switched Capacitors | Add two steps of 9.0 MVAR capacitors on the Kreitzburg Substation 69 kV bus. . | IN |  |  | Other | Not Shared |  | 1052000 | 2013-12-01 | 2013-12-01 | Proposed | 69 |  | C | Y
C | East | NIPS | 1983 | 2009-09-14 | 71C7206 | Dekalb Sub - Upgrade 138/69 Transformer | Replace the existing No.1 138/69 KV 56 MVA transformer with a 138/69 kV 112 MVA transformer. | IN |  |  | BaseRel | Not Shared |  | 1700000 | 2016-12-01 | 2016-12-01 | Conceptual | 138 | 69 | C | Y
C | East | NIPS | 1984 | 2010-04-04 | 71C7209 | South Knox - New 138/69 kV Substation | South Knox- New 138-69 KV, 1-168 MVA Transformer Substation | IN |  |  | BaseRel | Not Shared |  | 12568000 | 2017-12-01 | 2017-12-01 | Conceptual | 138 | 69 | C | Y
C | East | NIPS | 1985 | 2010-09-15 | 9320340 | Circuit 6959 Wolcotville to S. Milford Reconductor | Reconductor 5.4 miles of Circuit 6959's existing 2/0 Cu to 336.4 kCM ACSR. | IN |  |  | Other | Not Shared |  | 1671000 | 2017-12-01 | 2017-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 1989 | 2010-09-15 | 9325469 | Upgrade Circuit 6959 - S Milford to Helmer Tap | Reconductor 4.73 miles of Circuit 6959's existing 2/0 Cu to 336.4 kCM ACSR. | IN |  |  | Other | Not Shared |  | 1037000 | 2017-12-01 | 2017-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 1990 | 2010-09-15 | 9325471 | Upgrade Circuit 6986 - Dekalb to Angola Substation | Rebuild 16.5 miles of Circuit 6986's existing 2/0 Cu line to 336.4 kCM ACSR. | IN |  |  | Other | Not Shared |  | 9253000 | 2016-12-01 | 2016-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 1993 | 2009-09-14 | 9325543 | South Valparaiso - New 138/69 kV Substation | South Valparaiso - New 138/69 Substation, (3) 69 kV line extensions | IN |  |  | BaseRel | Not Shared |  | 4917000 | 2017-12-01 | 2017-12-01 | Conceptual | 138 | 69 | C | Y
C | East | NIPS | 1994 | 2009-09-14 | 9326151 | Circuit 6977 - Midway to Bristol Subs - Recond 4.1 miles | Upgrade (reconductor) 4.1 miles of 69 KV line to 336.4 KCM ACSR between Midway and Bristol Substations. | IN |  |  | Other | Not Shared |  | 656000 | 2011-12-01 | 2011-12-01 | Planned | 69 |  | C | Y
C | East | NIPS | 1998 | 2009-09-14 | X7L6606 | Circuits 6962 & 6937 - Lawton to E. Winamac - Rebuild 4.5 Miles | Rebuild existing double circuit 69 kV line between East Winamac and Lawton. Rebuild with new poles and conductors for 4.5 miles. | IN |  |  | Other | Not Shared |  | 1339000 | 2013-12-01 | 2013-12-01 | Proposed | 69 |  | C | Y
C | East | NIPS | 2000 | 2009-09-14 | X7L6802 | Circuit 6977 - Goshen Jct to Model Sub Tap | Upgrade (reconductor) .5 miles of 69 KV line to 336.4 KCM ACSR. | IN |  |  | Other | Not Shared |  | 52000 | 2014-12-01 | 2014-12-01 | Planned | 69 |  | C | Y
C | East | NIPS | 2003 | 2009-09-14 | X7L6811 | Circuit 6937 Sw 854 to Bruce Lake Sub - Rebuild | Rebuild existing 69 kV line between Bruce Lake Substation and Switch 854. | IN |  |  | Other | Not Shared |  | 957800 | 2014-12-01 | 2014-12-01 | Proposed | 69 |  | C | Y
C | East | NIPS | 2244 | 2008-08-05 | 71 | MTEP08 Reference Future EHV Overlay - should be Stillwell to Burr Oak | Build 345 kV circuit from Stillwell to Burr Oak station in Indiana | IN | [5 empty] | 28000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | East | NIPS | 2319 | 2009-09-14 | 71C7404 | South Chalmers MO 62 load breaks and switch replacement. | Upgrade Switch and install Load breaks | IN |  |  | Other | Not Shared |  | 25000 | 2013-05-01 | 2013-05-01 | Proposed | 69 |  | C | Y
C | East | NIPS | 2320 | 2010-09-15 | X7L6608 | Circuits 13874-Pole Replacement | Circuit 13874 - Replace 58 wood poles up to 70 poles if needed upon inspection, inspect and replace static wire as needed. First half of a two part project which will complete work begun in 2008. | IN |  |  | Other | Not Shared |  | 600000 | 2010-12-01 | 2010-12-01 | Planned | 138 |  | C | Y
C | East | NIPS | 2321 | 2009-09-14 | 71C6336 | Miller Sub - Add 138KV Capacitors - 100.0 MVAR | Add one step of 100 MVAR capacitors on the Miller Substation 138 kV bus. Engineering only in 2010. | IN |  |  | BaseRel | Not Shared |  | 974838 | 2017-09-01 | 2017-09-01 | Conceptual | 138 |  | C | Y
C | East | NIPS | 2323 | 2009-09-14 | 9326172 | Hiple Sub to Northport Sub - New 138 kV Line | Add new 138 kV terminals at Hiple and Northport Substations, and construct a new 10 mile 954 KCM ACSR 138 kV line between these two substations. Engineering only on 2008. | IN |  |  | Other | Not Shared |  | 5770000 | 2016-12-01 | 2016-12-01 | Conceptual | 138 |  | C | Y
C | East | NIPS | 2324 | 2009-09-14 | 71C7213 | East Plymouth - New 345-138 Substation | Add East Plymouth 345/138 kV, 1-560 MVA Transformer Sub - New | IN |  |  | BaseRel | Shared |  | 18884017 | 2016-05-01 | 2016-05-01 | Conceptual | 345 | 138 | C | Y
C | East | NIPS | 2792 | 2010-09-15 | X7L7502-71C6811-71C7517 | Northwest circuit reconfiguration | Phase I: Reconfigure 138 kV circuits at Mitchell switchyard to address SF-6 breaker maintenance. Reconfigure Chicago Avenue 138 kV line terminals. Phase II: Split existing Dune Acres Substation 138 kV bus into two sections to form a double bus. Add (2) new POT's and additional system protection (differential relaying) to provide adequate protection for a normally split 138 kV bus. | IN |  |  | Other | Not Shared |  | 2771000 | 2012-12-01 | 2012-12-01 | Conceptual | 138 |  | C | Y
C | East | NIPS | 3399 | 2010-09-15 | X7L7705 | Circuit 6964 rebuild | Rebuild/ Reconductor 6964 from Kentland Sub to Goodland Sub to Pine Creek Sub. | IN | [5 empty] | 5567000 | 2010-12-01 | 2010-12-01 | Proposed | 69 |  | C | Y
C | East | NIPS | 3400 | 2010-09-15 | X7L7703 | Extend 6951 to Palmira Substation | Extend 6951 to Palmira Substation | IN | [5 empty] | 123000 | 2012-12-01 | 2012-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 3401 | 2010-09-15 | X7L7704 | Circuit 6913 Rebuild Reconductor | Circuit 6913 Rebuild Reconductor | IN | [5 empty] | 2131000 | 2013-12-01 | 2013-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 3402 | 2010-09-15 | X7L7706 | Circuit 6981 Rebuild Reconductor | Circuit 6981 Rebuild Reconductor | IN | [5 empty] | 5563000 | 2013-12-01 | 2013-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 3403 | 2010-09-15 | X7L7707 | Circuit 6987 Rebuild Reconductor | Circuit 6987 Rebuild Reconductor | IN | [5 empty] | 1383000 | 2012-12-01 | 2012-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 3404 | 2010-09-15 | X7L7708 | Circuit 6998, Switch 151 to Warsaw Sub Reconductor Rebuild | Circuit 6998, Switch 151 to Warsaw Sub Reconductor Rebuild | IN | [5 empty] | 461000 | 2015-12-01 | 2015-12-01 | Conceptual | 69 |  | C | Y
C | East | NIPS | 3405 | 2010-09-15 | X7L7709 | Circuit 69-107 Reconductor | Circuit 69-107 Reconductor | IN | [5 empty] | 360000 | 2015-12-01 | 2015-12-01 | Conceptual | 69 |  | C | Y
C | West | AmerenIL, ATC LLC, GRE, ITCM, TP, XEL | 2773 | 2010-05-08 | GPE | Green Power Express 765kV | Construct a 765kV network including 11 new 765/345kV substations (13 new 765/345kV TRFs) and approximately 3000 miles of new 765kV line. Proposed substation locations include 2 in North Dakota, 1 in South Dakota, 4 in Minnesota, and 3 in Iowa. This 765kV network wil tie to the existing 765kV substations in Plano, IL and Sullivan, IN. | IA | WI |  |  |  |  | 11510000000 | 2020-12-31 | 2020-12-31 | Conceptual | 765 | 345 | C | Y
C | West | ATC LLC | 89 | 2011-01-05 | 67 | Mill Road 345/138 kV substation and transformer | Mill Road transformer - 345/138 ckt , Sum rate 500 | WI | [5 empty] | 29200000 | 2050-06-01 | 2050-06-01 | Conceptual | 345 | 138 | C | Y
C | West | ATC LLC | 341 | 2011-01-05 | newgrp19 | Rockdale-Mill Road 345 kV line projects | Construct Rockdale-Concord 345 kV line in parallel with existing 138 kV on existing double-width right-of-way. Construct a 345 kV bus and install a 345/138 kV, 500 MVA transformer at Concord. Convert Bark River-Mill Road 138 kV line to 345 kV. Construct | WI | [5 empty] | 94600000 | 2050-06-01 | 2050-06-01 | Conceptual | 345 | 138 | C | Y
C | West | ATC LLC | 1621 | 2010-09-15 | PR03198 | New Birchwood-Lake Delton 138-kV line | Construct new Birchwood-Lake Delton 138-kV line | WI |  |  | TBD | TBD |  | 5806000 | 2020-06-01 | 2020-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 1625 | 2010-09-15 | PR03283 | North Randolph Transformer | Install a 500 MVA 345/138 kV transformer at the North Randolph 138 kv SS by looping in the Columbia-South Fond du Lac 345-kV line | WI |  |  | BaseRel | Shared |  | 16552836 | 2025-12-31 | 2025-12-31 | Conceptual | 345 | 138 | C | Y
C | West | ATC LLC | 1697 | 2010-09-15 | PR03227 | Brick Church-Walworth 69 kV line | Uprate Brick Church-Walworth 69 kV line to 115 MVA | WI |  |  |  | Not Shared |  | 716000 | 2020-06-01 | 2020-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1703 | 2010-09-15 | PR03173 | Boscobel Capacitor Banks | Install one 8.16 MVAR capacitor bank at Boscobel 69 kV substation and upgrade existing 5.4 MVAR bank with an 8.16 MVAR bank | WI |  |  |  | Not Shared |  | 1335173 | 2019-06-01 | 2019-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1707 | 2009-12-01 |  | Holmes-Chandler 69 kV line | Rebuild/convert Holmes-Chandler 69 kV line to 138 kV operation | MI | WI |  |  |  |  | 56300000 | 2050-06-01 | 2050-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 1708 | 2010-09-15 | F2105, PRF1575a | Metomen and Mackford Prairie area upgrades | Construct Fairwater-Mackford Prairie 69 kV line, Reconfigure the North Randolph-Ripon 69-kV line to form a second Ripon-Metomen 69-kV line and retire the circuit between Metomen and the Mackford Prairie tap | WI |  |  | Other | Not Shared |  | 8879772.6 | 2018-06-01 | 2018-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1709 | 2010-09-15 | PR03176 | Eden Capacitor Banks | Install two 16.33 MVAR 69 kV capacitor banks at Eden Substation | WI |  |  |  | Not Shared |  | 1568118 | 2019-06-01 | 2019-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1710 | 2010-09-15 | PR03174 | Mazomanie capacitor banks | Install two 12.25 MVAR 69 kV capacitor banks at Mazomanie substation | WI |  |  |  | Not Shared |  | 1681113 | 2020-06-01 | 2020-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1712 | 2010-09-15 | PRF1007a | Horicon-East Beaver Dam 138 kV line | Construct a Horicon-East Beaver Dam 138 kV line | WI |  |  | TBD | TBD |  | 18186000 | 2022-06-01 | 2022-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 1717 | 2010-09-15 | PR03276 | Glenview 138/69 kV transformers | Replace two existing 138/69 kV transformers at Glenview Substaion with 100 MVA transformers | WI |  |  |  | Not Shared |  | 3440000 | 2020-06-01 | 2020-06-01 | Conceptual | 138 | 69 | C | Y
C | West | ATC LLC | 1718 | 2010-09-15 | F2081 | Custer 138/69 kV transformer | Install a 138/69 kV transformer at Custer substation | WI |  |  |  | Not Shared |  | 4904268 | 2022-06-01 | 2022-06-01 | Conceptual | 138 | 69 | C | Y
C | West | ATC LLC | 1719 | 2010-09-15 | F2081 | Shoto-Custer 138 kV line | Construct a Shoto-Custer 138 kV line | WI |  |  | TBD | TBD |  | 22938000 | 2022-06-01 | 2022-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 1720 | 2010-09-15 | F2480 | Wautoma 138/69 kV transformer | Install a second 138/69-kV transformer at Wautoma Substation | WI |  |  |  | Not Shared |  | 1440000 | 2017-06-01 | 2017-06-01 | Conceptual | 138 | 69 | C | Y
C | West | ATC LLC | 1721 | 2007-11-07 |  | Pulliam area 69 kV reconductor projects | Reconductor Pulliam-Danz 69kV line, reconductor Danz-Henry Street 69 kV line, reconductor Pulliam-Van Buren 69 kV line | WI |  |  |  | Not Shared |  |  | 2050-06-01 | 2050-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1723 | 2010-09-15 | PR03962 | Sunset Point transformer replacement | Replace two existing 138/69-kV transformers at Sunset Point Substation with 100 MVA transformers | WI |  |  |  | Not Shared |  | 3540000 | 2024-06-01 | 2024-06-01 | Conceptual | 138 | 69 | C | Y
C | West | ATC LLC | 1726 | 2010-09-15 | PR03902 | Uprate Royster-Sycamore 69 kV line | Uprate Royster-Sycamore 69 kV line to 115 MVA | WI |  |  |  | Not Shared |  | 790000 | 2019-06-01 | 2019-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1727 | 2010-09-15 | PR03957 | Dunn Road-Egg Harbor 69 kV line | Construct a second Dunn Road-Egg Harbor 69 kV line | WI |  |  | Other | Not Shared |  | 37194000 | 2018-06-01 | 2018-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 1730 | 2010-12-03 |  | Cardinal-Blount 138 kV line | Construct a Cardinal-Blount 138 kV line | WI |  |  |  | Not Shared |  | 60810250 | 2020-06-01 | 2020-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 2029 | 2010-09-15 |  | Brick Church 138 & 69kV Caps | Install 1-24.5 Mvar 138-kV capacitor bank and 1-18 Mvar 69-kV capacitor bank at Brick Church | WI |  |  |  | Not Shared |  |  | 2017-06-01 | 2017-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 2030 | 2010-09-15 |  | Concord 4x24.5 138 kV Caps | Install 4-24.5 Mvar 138-kV capacitor bank at Concord | WI |  |  |  | Not Shared |  | 3358282 | 2020-06-01 | 2020-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 2031 | 2010-09-15 |  | Y-32 Rebuild (Colley Rd-Brick Church 69 kV) | Y-32 Rebuild (Colley Rd-Brick Church 69 kV) | WI |  |  |  | Not Shared |  | 11225500.0001 | 2018-06-01 | 2018-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 2038 | 2010-09-15 |  | Spring Valley-S Lake Geneva 138 kV | Construct Spring Valley-Twin Lakes-S Lake Geneva 138 kV | WI |  |  |  | Not Shared |  | 33284914.5 | 2018-06-02 | 2018-06-02 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 2040 | 2010-09-15 |  | Sun Prairie 69kV Caps | Install 2x16.33 Mvar 69 kV capacitor banks at Sun Prairie | WI |  |  |  | Not Shared |  | 2566334.06 | 2020-06-01 | 2020-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 2042 | 2010-09-15 |  | Dam Heights 69kV Caps | Install 2x16.33 Mvar 69 kV caps at Dam Heights | WI |  |  |  | Not Shared |  | 2896361 | 2019-06-01 | 2019-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 2043 | 2010-09-15 |  | Convert Necedah from 69 to 138 kV | Convert Necedah from 69 to 138 kV and tap into the Petenwell-Council Creek 138 kV line | WI |  |  |  | Not Shared |  | 761500 | 2018-06-01 | 2018-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 2046 | 2010-09-15 |  | North Monroe 69 kV Caps | Install 2x16.33 Mvar 69 kV capacitor banks at North Monroe | WI |  |  |  | Not Shared |  | 2336040.28 | 2018-06-01 | 2018-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 2056 | 2010-09-15 |  | Uprate Oak Creek-Pennsylvania 138 kv | Uprate Oak Creek-Pennsylvania 138 kV | WI |  |  |  | Not Shared |  | 2409559 | 2020-06-01 | 2020-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 2162 | 2010-09-15 |  | 2nd McCue-LaMar 69 kV line | Construct a 2nd McCue-LaMar 69 kV line | WI |  |  |  | Not Shared |  | 5009084.97 | 2017-06-01 | 2017-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3117 | 2010-09-15 |  | Reconductor X-12 from Townline Rd to Bass Creek | Reconductor X-12 from Townline Rd to Bass Creek | WI | [5 empty] | 1900000 | 2021-06-01 | 2021-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 3124 | 2010-09-15 |  | construct a 2nd Forsyth-Gwinn 69kV line | construct a 2nd Forsyth-Gwinn 69kV line | MI | [5 empty] | 1000000 | 2018-06-01 | 2018-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3164 | 2010-09-15 | RGOS DC | Point Beach-Ludington HVDC line | Construct a HVDC line under Lake Michigan between Point Beach and Ludington and construct HVDC converter stations | MI | WI/MI |  |  |  |  | 828000000 | 2020-06-01 | 2020-06-01 | Conceptual | 350 |  | C | Y
C | West | ATC LLC | 3165 | 2010-09-15 |  | Elm Rd- DC Cook HVDC line | Construct a HVDC line under Lake Michigan between Elm Road and DC Cook and construct HVDC converter stations | MI | WI/MI |  |  |  |  | 1071000000 | 2020-06-01 | 2020-06-01 | Conceptual | 765 | 345 | C | Y
C | West | ATC LLC | 3166 | 2010-09-15 |  | 2nd Hillman 138/69kV transformer | Install a 2nd Hillman 138/69kV transformer | WI | [5 empty] | 4843288 | 2018-06-01 | 2018-06-01 | Conceptual | 138 | 69 | C | Y
C | West | ATC LLC | 3167 | 2010-09-15 |  | Y-87 North Monroe-South Monroe 69 kV Line Uprate | Y-87 North Monroe-South Monroe 69 kV Line Uprate | WI | [5 empty] | 7080193 | 2018-06-01 | 2018-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3189 | 2010-09-15 |  | Uprate line Y-93 from Ripon to Northwest Ripon | Uprate line Y-93 from Ripon to Northwest Ripon from 167 deg F to SN/SE | WI | [5 empty] | 2205426 | 2019-06-01 | 2019-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3190 | 2010-09-15 |  | Rebuild line Y-103 from Sunset Point to Winneconne | Rebuild line Y-103 from Sunset Point to Winneconne to SN/SE = 200/300 deg F | WI | [5 empty] | 12366239 | 2019-06-01 | 2019-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3207 | 2010-09-15 |  | Replace Harrison 138/69kV Tr | Replace the Harrison 56 MVA 138/69kV Tr with a 100 MVA unit | WI | [5 empty] | 3229974 | 2016-06-01 | 2016-06-01 | Conceptual | 138 | 69 | C | Y
C | West | ATC LLC | 3208 | 2010-09-15 |  | Replace Caroline 115/69kV Tr | Replace the Caroline 33 MVA 1115/69kV Tr with a dual high side 138-115/69-kV 100 MVA unit | WI | [5 empty] | 4010542 | 2018-06-01 | 2018-06-01 | Conceptual | 115 | 69 | C | Y
C | West | ATC LLC | 3429 | 2010-10-20 | PR04087 | Sun ValleyTap-Oregon 69kV line rebuild | Rebuild the Sun ValleyTap-Oregon 69kV line | WI | [5 empty] | 5561798 | 2020-06-01 | 2020-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3430 | 2010-10-20 | PR03211 | Dyckesville-Sawyer 69kV rebuild | Rebuild the Dyckesville-Brusbay-Sawyer 69 kV line | WI | [5 empty] | 11814128 | 2016-06-01 | 2016-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3486 | 2011-03-01 |  | Oak Creek-Bluemound Uprate | Uprate 138 kV line to 275 F | WI | [5 empty] | 1400000 | 2021-06-01 | 2021-06-01 | Conceptual | 138 |  | C | Y
C | West | ATC LLC | 3487 | 2011-03-22 |  | West Middleton-Pheasant Branch 69 kV new circuit | Replace existing single circuit from WMD-Pheasant Branch 69 kV with double circuit 69 kV lines. | WI | [5 empty] | 22711186 | 2022-06-01 | 2022-06-01 | Conceptual | 69 |  | C | Y
C | West | ATC LLC | 3512 | 2011-05-16 |  | Pleasant Prairie-Cook HVDC line | Construct a HVDC line under Lake Michigan between Pleasant Prairie and Cook and construct HVDC converter stations | MI | WI/MI |  |  |  |  | 828000000 | 2020-06-01 | 2020-06-01 | Conceptual | 350 |  | C | Y
C | West | ATC LLC, ALTW | 2230 | 2008-08-05 | 55 | MTEP08 Reference Future EHV Overlay - Salem to West Middleton | Build 345 kV circuit from West Middleton in Wisconsin to Salem Station in Iowa | WI | [5 empty] | 102000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 138 | C | Y
C | West | ATC LLC, XEL | 2211 | 2008-08-05 | 36 | MTEP08 Reference Future EHV Overlay - Longwood to Greenwood | Build 345 kV circuit from Longwood Station to Greenwood Station in Wisconsin | WI | [5 empty] | 200000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | DPC, ATC LLC | 2231 | 2008-08-05 | 56 | MTEP08 Reference Future EHV Overlay - LaCrosse-Columbia | Build 345 kV circuit from LaCrosse to Columbia Station in Wisconsin | WI | [5 empty] | 186000000 | 43313 | 43313 | Conceptual | 345 | 138 | C | Y
C | West | GRE | 2691 | 2010-09-15 | 20472 | Orrock 345/115 kV source and Orrock-Waco-Liberty 115 kV line. | Orrock 345/115 kV source and Orrock-Waco-Liberty 115 kV line. | MN | [5 empty] | 19661825 | 2017-06-01 | 2017-06-01 | Conceptual | 345 | 69 | C | Y
C | West | ITCM | 1738 | 2009-09-25 | Bert161 | Bertram-Hills 161kV Reconductor | Reconductor 33 miles of 161kV from Bertram to new Rose Hollow to Hills | IA |  |  | BaseRel | Shared |  | 22540000 | 2017-12-31 | 2017-12-31 | Proposed | 161 |  | C | Y
C | West | ITCM | 1742 | 2009-09-25 | 3MN | Split Rock-Heron Lake 161kV Rebuild | Rebuild from Split Rock-Magnolia-Elk-Heron Lake 161kV line. | MN |  |  | BaseRel | Shared |  | 33404000 | 2014-12-31 | 2016-12-31 | Proposed | 161 |  | C | Y
C | West | ITCM | 2830 | 2009-08-28 | FG5 | Lakefield Jct. – Rutland 345kV | Build a new 345kV station at Rutland and add a new 345/161kV transformer. Build a new 345kV circuit from Lakefield Jct station to Rutland 345kV station. | MN | [5 empty] | 98500000 | 2014-01-01 | 2014-01-01 | Proposed | 345 | 161 | C | Y
C | West | ITCM | 3086 | 2009-09-25 | 8th-Lore | 8th Street-Kerper-Lore 161kV Rebuild | Rebuild the dubuque area 8th Street-Kerper-Lore 161kV line. | IA |  |  | BaseRel | Shared |  | 7056500 | 2013-12-31 | 2014-12-31 | Proposed | 161 |  | C | Y
C | West | ITCM | 3087 | 2009-09-25 | Lansing-Harmony | Lansing-Harmony 161kV Rebuild | Rebuild portion of the line in IA due to structure condition. | IA |  |  | Other | Not Shared |  | 30000000 | 2016-12-31 | 2016-12-31 | Proposed | 161 |  | C | Y
C | West | ITCM | 3500 | 2011-03-28 |  | NERC Alert Facility Ratings for 2012 | Verify and remediate facilities as required due to the industry-wide NERC alert | IA | [6 empty] | 2012-12-31 | 2012-12-31 | Planned |  |  | C | Y
C | West | ITCM | 3501 | 2011-03-28 |  | NERC Alert Facility Ratings for 2013 | Verify and remediate facilities as required due to the industry-wide NERC alert | IA | [6 empty] | 2013-12-31 | 2013-12-31 | Planned |  |  | C | Y
C | West | ITCM | 3502 | 2011-03-28 |  | NERC Alert Facility Ratings for 2014 | Verify and remediate facilities as required due to the industry-wide NERC alert | IA | [6 empty] | 2014-12-31 | 2014-12-31 | Planned |  |  | C | Y
C | West | ITCM, XEL | 2223 | 2008-08-05 | 48 | MTEP08 Reference Future EHV Overlay - Lakefield to Adams | Build 345 kV double circuit line from Lakefield to Adams Station in Minnesota | MN | [5 empty] | 334000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 161 | C | Y
C | West | MDU | 3082 | 2009-09-15 | NW Bism | NW Bismarck Ring Bus | Install 115kV ring bus at the NW Bismarck substation | ND |  |  | TBD |  |  | 3050000 | 2014-06-01 | 2014-06-01 | Planned | 115 |  | C | Y
C | West | MDU | 3084 | 2009-09-15 | East Bism | East Bismarck Bus Split | Install 115 kV Bus Tie breaker and 2nd 115 kV WAPA Tie | ND |  |  | TBD |  |  | 2500000 | 2015-12-01 | 2015-12-01 | Proposed | 115 |  | C | Y
C | West | MDU | 3456 | 2010-10-21 | Glenham xfmr | Glenham transformer replacement | Replace the smaller Glenhame transformer and rebuild Glenhame 230 kV bus into a ring configuration | SD | [5 empty] | 7000000 | 2016-06-01 | 2016-06-01 | Planned | 230 | 115 | C | Y
C | West | MDU, NON-MISO | 2214 | 2008-08-05 | 39 | MTEP08 Reference Future EHV Overlay - Glenham to Ellendale | Build 345 kV circuit from Glenham in South Dakota to Ellendale in North Dakota | SD | SD/ND |  |  |  |  | 47000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 230 | C | Y
C | West | MEC | 2941 | 2010-09-21 | T8132 | Sub T - Boone Jct 161 kV Line Upgrade | Uprate MEC's portion of the Sub T - Boone Jct 161 kV line. | IA |  |  | BaseRel | TBD |  | 1600000 | 2014-12-31 | 2014-12-31 | Proposed | 161 |  | C | Y
C | West | MEC | 2943 | 2010-09-01 | G0205 | Hills 2nd 345-161 kV XFMR | Install 2nd 560 MVA 345-161 kV transformer at Hills Substation. Expand 345 and 161 kV ring busses to accommodate new transformer. | IA |  |  | BaseRel | TBD |  | 12000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 | 161 | C | Y
C | West | MEC | 2944 | 2010-09-01 | G0197 | Hills - Sub E 161 kV Line Reconductor | Reconductor the Hills - Sub E Iowa City 161 kV line. | IA |  |  | BaseRel | TBD |  | 1800000 | 2019-06-01 | 2019-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 2945 | 2009-09-14 | G0126 | Grimes Sub Add 2nd 345-161 kV Transformer | Add a second transformer at the Grimes Substation and expand the 345 and 161 kV ring buses by one breaker. | IA |  |  | BaseRel | Shared? |  | 11900000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 | 161 | C | Y
C | West | MEC | 2946 | 2010-09-01 | G0124 | Reconductor Greenfield Plaza-Army Post-Ashawa 161 kV line. | Reconductor the Greenfield Plaza-Army Post-Ashawa 161 kV line. | IA |  |  | BaseRel | TBD |  | 1200000 | 2018-06-01 | 2018-06-01 | Proposed | 161 |  | C | Y
C | West | MEC | 2947 | 2010-09-01 | T3204 | North Grimes 161-13 kV Substation | Construct the North Grimes Substation by tapping the Bittersweet Road-Granger Tap 161 kV line with in and out breakered line terminals. The Granger Tap is located on the Grimes-100th & 54th 161 kV line. | IA |  |  | Other | Not Shared | Distribution | 3900000 | 2012-06-01 | 2018-06-01 | Planned | 161 | 13.2 | C | Y
C | West | MEC | 2948 | 2010-09-01 | T3228 | West Waukee 161-13 kV Substation | Construct the West Waukee Substation. The Substation will tap (non-breakered in and out) a new 161 kV line from the Booneville Substation to the Grimes Substation. | IA | [5 empty] | 10650000 | 2018-06-01 | 2018-06-01 | Proposed | 161 | 13.2 | C | Y
C | West | MEC | 2949 | 2010-09-01 | T3344 | West Waukee 161-69 kV Transformer | Add a 161-69 kV transformer and 161 kV circuit breakers at the West Waukee Substation. | IA |  |  | Other | Not Shared | Reliability | 3100000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 | 69 | C | Y
C | West | MEC | 2951 | 2009-09-14 | T3704 | Boston 161-13 kV Substation | Contruct the Boston Substation by tapping (non-breakered in and out) the Sycamore-Forest & Vermont 161 kV line. | IA |  |  | Other | Not Shared |  | 2000000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 | 13 | C | Y
C | West | MEC | 2952 | 2009-09-14 | T3316 | East Altoona 161-13 kV Substation | Construct the East Altoona Substation and the Metro East - E Altoona and E Altoona-Bondurant 161 kV lines. Includes the addition of a breakered line terminal at Bondurant and the addition of breakers on the two existing line terminals at Metro East. | IA |  |  | Other | Not Shared |  | 11340000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 | 13 | C | Y
C | West | MEC | 2953 | 2010-09-01 | T2104 | Page County 345-161 kV Substation | Construct a 345-161 kV Substation that taps the Atchison County-Booneville 345 kV line and the Clarinda-Hastings 161 kV line. The substation will consist of a three (3) breaker 345 kV ring bus, a three (3) breaker 161 kV ring bus, and a 345-161 kV autotransformer. Reconductor the Page County-Clarinda 161 kV line. | IA | [5 empty] | 18600000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 | 161 | C | Y
C | West | MEC | 2954 | 2010-09-01 | T2135 | Clarinda 161 kV Capacitor | Install a 50 MVAR, 161 kV capacitor at the Clarinda Substation | IA |  |  | BaseRel | TBD |  | 1000000 | 2018-06-01 | 2018-06-01 | Proposed | 161 |  | C | Y
C | West | MEC | 3217 | 2010-09-07 | MEC2011 C-1 | Kewanee - Scott County 765 kV Line | Construct 765 kV line from new Kewanee 765 kV bus to Scott County Substation and associated substation equipment additions. | IA | IA/IL |  |  |  |  | 193000000 | 2019-12-31 | 2019-12-31 | Proposed | 765 |  | C | Y
C | West | MEC | 3219 | 2010-09-07 | MEC2011 C-3 | Kewanee - Louisa 765 kV Line | Construct 765 kV line from Kewanee to Louisa and associated substation equipment additions. | IA | IA/IL |  |  |  |  | 283000000 | 2019-12-31 | 2019-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC | 3224 | 2010-09-07 | MEC2011 C-8 | Woodbury County (Raun) - Hoskins 345 kV Lines | Construct double circuit 345 kV line from either Raun or new substation in Woodbury County to Hoskins Substation and associated substation equipment additions. | IA | NE |  |  |  |  | 167000000 | 2019-12-31 | 2019-12-31 | Proposed | 345 |  | C | Y
C | West | MEC | 3225 | 2010-09-07 | MEC2011 C-9 | Woodbury County (Raun) - Broadland 345 kV Lines | Construct double circuit 345 kV line from either Raun or new substation in Woodbury County to Broadland Substation and associated substation equipment additions. | IA | SD |  |  |  |  | 591000000 | 2019-12-31 | 2019-12-31 | Proposed | 345 |  | C | Y
C | West | MEC | 3226 | 2010-09-07 | MEC2011 C-10 | Pocahontas Co. - Woodbury County (Raun) 765 kV Line | Construct 765 kV line from new Pocahontas County Substation to either Raun Substation or new substation in Woodbury County and associated substation equipment additions. | IA | [5 empty] | 296000000 | 2024-12-31 | 2024-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC | 3227 | 2010-09-07 | MEC2011 C-11 | Pocahontas Co. - Hoskins 765 kV Line | Construct 765 kV line from new Pocahontas County Substation to Hoskins Substation and associated substation equipment additions. | IA | NE |  |  |  |  | 461000000 | 2024-12-31 | 2024-12-31 | Proposed | 765 |  | C | Y
C | West | MEC | 3229 | 2010-09-07 | MEC2011 C-13 | Pocahontas Co. - Osceola Co. 765 kV Line | Construct 765 kV line from new Pocahontas County Substation to new Osceola County 765 kV substation and associated substation equipment additions. | IA | [5 empty] | 220000000 | 2024-12-31 | 2029-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC | 3230 | 2010-09-07 | MEC2011 C-14 | Osceola Co. - Chanarambie 765 kV Line | Construct 765 kV line from new Osceola County substation to new Chanarambie substation and associated substation equipment additions. | IA | MN |  |  |  |  | 366000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 |  | C | Y
C | West | MEC | 3231 | 2010-09-07 | MEC2011 C-15 | Pocahontas Co. - Adair Co. 765 kV Line | Construct 765 kV line from new Pocahontas County Substation to new Adair County Substation and associated substation equipment additions. | IA | [5 empty] | 499000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC | 3232 | 2010-09-07 | MEC2011 C-16 | Adair Co. - St. Joseph 765 kV Line | Construct 765 kV line from new Adair County Substation to St. Joseph Substation and associated substation equipment additions. | IA | MO |  |  |  |  | 407000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 |  | C | Y
C | West | MEC | 3233 | 2010-09-07 | MEC2011 C-17 | Adair Co. - Hills 765 kV Line | Construct 765 kV line from new Adair County Substation to Hills Substation and associated substation equipment additions. | IA | [5 empty] | 691000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 |  | C | Y
C | West | MEC | 3234 | 2010-09-07 | MEC2011 C-18 | Hills - Kincaid 765 kV Line | Construct 765 kV line from Hills to Kincaid Substation and associated substation equipment additions. | IA | IL |  |  |  |  | 745000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 |  | C | Y
C | West | MEC | 3237 | 2010-09-07 | MEC C-20 | Avoca-Page County-Maryville 345 kV line | Construct a new 345 kV line from Avoca-Page County-Maryville with 161 kV underbuild and associated substation equipment additions. | IA | IA/MO |  |  |  |  | 203000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 | 161 | C | Y
C | West | MEC | 3238 | 2010-09-07 | MEC C-21 | CBEC-S3456 345 kV Line | Construct second 345 kV line from CBEC-OPPD's 3456 Sub and associated substation equipment additions. | IA | NE |  |  |  |  | 29100000 | 2019-06-01 | 2019-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC | 3239 | 2010-09-07 | MEC C-22 | Bunge-Hastings-Page County 161 kV Rebuild | Rebuild 161 kV Line from Bunge-Hastings and associated substation equipment additions. | IA | [5 empty] | 29100000 | 2018-06-01 | 2018-12-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3240 | 2010-09-07 | MEC C-23 | Denison-Avoca 161 kV Line | New 161 kV line from Denison-Avoca and associated substation equipment additions. | IA | [5 empty] | 20900000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3241 | 2010-09-07 | MEC C-24 | CBEC-Sub 701 161 kV Line | Construct a 161 kV line from CBEC-Sub 701 and associated substation equipment additions. | IA |  |  | BaseRel | TBD |  | 4600000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3242 | 2010-09-07 | MEC C-25 | Quick-Sub 701 161 kV Line | Construct a 161 kV line from Quick to Sub 701 and associated substation equipment additions. | IA | [5 empty] | 7700000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3243 | 2010-09-07 | MEC C-26 | Quick-Avoca 161 kV line | Construct a 161 kV line from Quick to Avoca and associated substation equipment additions. | IA | [5 empty] | 11700000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3246 | 2010-09-07 | MEC C-29 | Webster South-Lehigh 161 kV line | Construct new 161 kV line between future 161 kV terminals at the Lehigh Substation and Webster South switching station and associated substation equipment additions. | IA | [5 empty] | 3500000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3247 | 2010-09-07 | MEC C-30 | Lehigh 345-161 kV Transformer | Install a 345-161 kV transformer at the Lehigh Substation | IA | [5 empty] | 7500000 | 2016-06-01 | 2016-06-01 | Conceptual | 345 | 161 | C | Y
C | West | MEC | 3250 | 2010-09-07 | MEC C-33 | West Grand-88th St 161 kV Line | West Grand-88th St 161 kV Line and associated substation equipment additions. | IA | [5 empty] | 1800000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3251 | 2010-09-07 | MEC C-34 | Army Post-West Grand 161 kV Line | Army Post-West Grand 161 kV Line and associated substation equipment additions. | IA | [5 empty] | 4400000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3252 | 2010-09-07 | MEC C-35 | Norwalk-Scotch Ridge 161 kV Line | Norwalk-Scotch Ridge 161 kV Line and associated substation equipment additions. | IA | [5 empty] | 7100000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 | 13.2 | C | Y
C | West | MEC | 3253 | 2010-09-07 | MEC C-36 | Scotch Ridge-Avon Lake 161 kV Line | Scotch Ridge-Avon Lake 161 kV Line and associated substation equipment additions. | IA | [5 empty] | 5700000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 | 13.2 | C | Y
C | West | MEC | 3254 | 2010-09-07 | MEC C-37 | Avon Lake-DPS 161 kV Line or SE Polk | Avon Lake-DPS 161 kV Line or SE Polk and associated substation equipment additions. | IA | [5 empty] | 1400000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3255 | 2010-09-07 | MEC C-38 | Sub 91 - Cordova 345 kV Line | 345 kV line from Cordova - Sub 91, convert Sub 91 345 to ring bus and associated substation equipment additions. | IA | IL |  |  |  |  | 23400000 | 2015-06-01 | 2015-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC | 3256 | 2010-09-07 | MEC C-39 | Sub 39 - Cordova 345 kV ckt 2 | 2nd 345 kV line from Sub 39 to Cordova and associated substation equipment additions. | IL | [5 empty] | 20800000 | 2015-06-01 | 2015-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC | 3257 | 2010-09-07 | MEC C-40 | Eagle - LeMars - Spencer - Sioux County 161 kV Lines | Eagle - LeMars - Spencer - Sioux County 161 kV Line and associated substation equipment additions. | IA | [5 empty] | 54100000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3258 | 2010-09-07 | MEC C-41 | Little Sioux-Monona 161 kV line | Little Sioux-Monona 161 kV line and associated substation equipment additions. | IA | [5 empty] | 18700000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3259 | 2010-09-07 | MEC C-42 | Carroll-Denison 161 kV line | New Carroll County-Denison 161 kV line and associated substation equipment additions. | IA | [5 empty] | 16500000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC | 3260 | 2010-09-07 | MEC C-43 | Odebolt-Carroll 345 kV line | New Odebolt-Carroll County 345 kV line with 161 kV underbuild and associated substation equipment additions. | IA | [5 empty] | 57000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC | 3261 | 2010-09-07 | MEC C-44 | Wisdom-Odebolt 345 kV line | Wisdom-Buena Vista-Sac-Odebolt 345 kV line with 161 kV underbuild and associated substation equipment additions. | IA | [5 empty] | 79300000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC | 3267 | 2010-09-07 | T7018 | NW Sioux City 230-69 kV Substation | Add 230-69 kV sub and associated 230 kV and 69 kV ties and associated substation equipment additions. | IA |  |  | Other | Shared | Reliability | 10500000 | 2016-06-01 | 2016-06-01 | Conceptual | 230 | 69 | C | Y
C | West | MEC | 3269 | 2011-02-15 | G1458 | Blackhawk-Hazleton 161 kV Rebuild | Increase 161 kV line rating. | IA |  |  | BaseRel | Not Shared |  | 3400000 | 2012-06-01 | 2012-06-01 | Planned | 161 |  | C | Y
C | West | MEC | 3371 | 2010-09-15 | MEC C-49 | Hills-Parnell 161 kV Line Upgrade | Upgrate the Hills-Parnell 161 kV line | IA |  |  | BaseRel | Not Shared |  | 90000 | 2014-12-31 | 2014-12-31 | Proposed | 161 |  | C | Y
C | West | MEC | 3372 | 2010-09-15 | MEC C-50 | Parnell-Poweshiek 161 kV Line Upgrade | Upgrade the Parnell-Poweshiek 161 kv line | IA |  |  | BaseRel | Not Shared |  | 540000 | 2014-12-31 | 2014-12-31 | Proposed | 161 |  | C | Y
C | West | MEC | 3477 | 2011-02-15 | MEC C-52 | Oak Grove-Galesburg 161 kV Upgrade | Rebuild the Oak Gove-Galesburg 161 kV line to increase capacity | IL | [6 empty] | 2014-12-01 | 2014-12-01 | Proposed | 161 | 138 | C | Y
C | West | MEC | 3478 | 2011-02-15 | MEC C-51 | Webster-Black Hawk-Hazleton 161 kV Rebuild | Rebuild approx. 115 miles of existing 161 kV line from Webster to Black Hawk to Hazleton to increase capacity. | IA | [5 empty] | 23680000 | 2018-12-31 | 2018-12-31 | Planned | 161 |  | C | Y
C | West | MEC, ALTW | 2193 | 2008-08-05 | 15 | MTEP08 Reference Future EHV Overlay - Lehigh to Toledo | Builds 765 kV circuit from Lehigh Station to Toledo Station in Iowa | IA | [5 empty] | 313000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | West | MEC, ITCM | 2950 | 2010-09-01 | T3211 | Polk City 161-13 kV Substation | Construct the Polk City Substation. The Substation will tap the ITC Midwest 161 kV line from Bittersweet Road to NE Ankeny with in and out breakered line terminals. | IA | [5 empty] | 1500000 | 2018-06-01 | 2018-06-01 | Conceptual | 161 | 13.2 | C | Y
C | West | MEC, ITCM | 3218 | 2010-09-21 | MEC2011 C-2 | Scott County - Hazleton 765 kV Line | Construct 765 kV line from Scott County to Hazleton Substation and associated substation equipment additions. | IA | [5 empty] | 459000000 | 2019-12-31 | 2019-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC, ITCM | 3220 | 2010-09-21 | MEC2011 C-4 | Louisa-Hazleton 765 kV | Construct 765 kV line from Louisa to Hazleton and associated substation equipment additions. | IA | [5 empty] | 257000000 | 2019-12-31 | 2019-12-31 | Proposed | 765 |  | C | Y
C | West | MEC, ITCM | 3221 | 2010-09-21 | MEC2011 C-5 | Hazleton - Pocahontas Co. 765 kV Line | Construct 765 kV line from Hazleton to new Pocahontas County Substation and associated substation equipment additions. | IA | [5 empty] | 837000000 | 2019-12-31 | 2019-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC, ITCM | 3222 | 2010-09-21 | MEC2011 C-6 | Hills - Hazleton 345 kV Line | Construct 345 kV line from Hills to Hazleton Substation and associated substation equipment additions. | IA | [5 empty] | 83000000 | 2019-12-31 | 2019-12-31 | Proposed | 345 |  | C | Y
C | West | MEC, ITCM | 3223 | 2010-09-21 | MEC2011 C-7 | Hazleton - Adams 345 kV Lines | Construct double circuit 345 kV line from Hazleton to Adams Substation and associated substation equipment additions. | IA | MN |  |  |  |  | 227000000 | 2019-12-31 | 2019-12-31 | Proposed | 345 |  | C | Y
C | West | MEC, ITCM | 3228 | 2010-09-21 | MEC2011 C-12 | Hills - Hazleton 765 kV Line | Construct 765 kV line from Hills to Hazleton Substation and associated substation equipment additions. | IA | [5 empty] | 215000000 | 2024-12-31 | 2024-12-31 | Proposed | 765 | 345 | C | Y
C | West | MEC, ITCM | 3235 | 2010-09-21 | MEC2011 C-19 | Osceola Co. - Lakefield Jct. 765 kV Line | Construct 765 kV line from new Osceola County Substation to Lakefield Jct. Substation and associated substation equipment additions. | IA | MN |  |  |  |  | 230000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 |  | C | Y
C | West | MEC, ITCM | 3236 | 2010-09-21 | MEC2011 C-20 | Hazleton - Adams 765 kV Line | Construct 765 kV line from Hazleton to Adams Substation and associated substation equipment additions. | IA | MN |  |  |  |  | 312000000 | 2029-12-31 | 2029-12-31 | Proposed | 765 |  | C | Y
C | West | MEC, ITCM | 3244 | 2010-09-21 | MEC C-27 | OGS-Pleasant Corner-Beacon-Pella-Reasnor 161 kV Line | Construct a new 161 kV line from OGS-Pleasant Corner-Beacon-Pella-Reasnor with 69 kV underbuild and associated substation equipment additions. | IA | [5 empty] | 38650000 | 2017-06-01 | 2017-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC, ITCM | 3245 | 2010-09-21 | MEC C-28 | Lucas County-Knoxville-Pella-Reasnor 161 kV Line | Construct a 161 kV line from Lucas County-Knoxville-Pella-Reasnor and associated substation equipment additions. | IA | [5 empty] | 34100000 | 2017-06-01 | 2017-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC, ITCM | 3248 | 2010-09-21 | MEC C-31 | DPS/Reasnor Sub - East Altoona 161 kV Line | New 161 kV line from switching station on DPS-Reasnor line to East Altoona and associated substation equipment additions. | IA | [5 empty] | 6500000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC, ITCM | 3249 | 2010-09-21 | MEC C-32 | East Altoona-NE Ankeny/Jasper County Sub 161 kV line | New 161 kV line from East Altoona to a new sub off NE Ankeny/Jasper County line and associated substation equipment additions. | IA | [5 empty] | 7800000 | 2016-06-01 | 2016-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC, ITCM | 3262 | 2010-09-21 | MEC C-45 | Odebolt-Adair 345 kV line | Odebolt-Grand Junction-Adair 345 kV line and associated substation equipment additions. | IA | [5 empty] | 204100000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC, ITCM | 3263 | 2010-09-21 | MEC C-46 | Adair-Sub T 345 kV line | Adair-Ottumwa-Sub T 345 kV line and associated substation equipment additions | IA | [5 empty] | 244000000 | 2020-06-01 | 2020-06-01 | Conceptual | 345 |  | C | Y
C | West | MEC, ITCM | 3264 | 2010-09-21 | MEC C-47 | S.E. Polk - Ottumwa 161 kV Line | New S.E. Polk-Ottumwa 161 kV line and associated substation equipment additions. | IA | [5 empty] | 40000000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 |  | C | Y
C | West | MEC, ITCM | 3265 | 2010-09-21 | MEC C-48 | Carroll-Adair 161 kV line | New Carroll County-Grand Junction-Adair 161 kV line and associated substation equipment additions. | IA | [5 empty] | 60500000 | 2020-06-01 | 2020-06-01 | Conceptual | 161 |  | C | Y
C | West | MH, OTP | 2180 | 2011-07-01 | 2 | MTEP08 Reference Future EHV Overlay - Riel to Maple River | Builds 500 kV circuit from Riel Station in Manitoba to Maple River Station in North Dakota | Manitoba | ND |  |  |  |  | 374000000 | 2018-08-01 | 2018-08-01 | Conceptual | 500 | 115 | C | Y
C | West | MP | 2548 | 2009-11-13 | Hilltop | Hilltop | Add second 230/115 kV Transformer capacity and 230 kV line | MN |  |  | TBD |  |  |  | 2019-06-01 | 2019-06-01 | Proposed | 230 | 115 | C | Y
C | West | MP | 2551 | 2011-09-06 | 28L Tap | 28L Tap | Remove Tap and put line on its own breaker & upgrade capacity | MN |  |  | BaseRel | Not Shared |  | 1250000 | 2014-06-30 | 2014-06-30 | Proposed | 115 |  | C | Y
C | West | OTP | 2746 | 2010-01-06 |  | Turtle Lake-Mercer 41.6 kV Line Upgrade | Rebuild Existing 18-Mile 41.6 kV Line | ND |  |  | Other | Not Shared |  | 500000 | 2015-11-01 | 2015-11-01 | Proposed | 41.6 |  | C | NT
C | West | OTP | 2857 | 2010-09-28 | OTP1 | Green Valley 41.6 kV Line Upgrade | Rebuild Existing 4-Mile 41.6 kV Line | MN |  |  | Other | Not Shared |  | 550000 | 2014-12-31 | 2014-12-31 | Proposed | 41.6 |  | C | Y
C | West | OTP | 3484 | 2011-02-24 | OTP/MPC | Big Stone AQCS Addition | Install a new 230/13.8 kV transformer to accommodate a new load increase at Big Stone related to new pollution control equipment | SD | [5 empty] | 3000000 | 2015-07-01 | 2015-07-01 | Proposed | 230 | 13.8 | C | Y
C | West | OTP, GRE | 2225 | 2011-07-01 | 50 | MTEP08 Reference Future EHV Overlay - Big Stone-Crow River | Build 345 kV double circuit line from Big Stone in South Dakota to Crow River in Minnesota | MN | MN/SD |  |  |  |  | 328000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 115 | C | Y
C | West | OTP, MDU | 2219 | 2011-07-01 | 44 | MTEP08 Reference Future EHV Overlay - Maple River to Ellendale | Build 345 kV double circuit line from Maple River to Ellendale in North Dakota | ND | [5 empty] | 239000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 230 | C | Y
C | West | OTP, NON-MISO | 2182 | 2011-07-01 | 4 | MTEP08 Reference Future EHV Overlay - Maple River to Watertown | Builds 345 kV circuit from Maple River Station in North Dakato to Watertown Station in South Dakota | ND | SD |  |  |  |  | 202000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | OTP, XEL | 2181 | 2011-07-01 | 3 | MTEP08 Reference Future EHV Overlay - Maple River to Blue Lake | Builds 500 kV circuit from Maple River Station in North Dakota to Blue Lake Station in Minnesota | MN | SD/MN |  |  |  |  | 401000000 | 2018-08-01 | 2018-08-01 | Conceptual | 500 | 345 | C | Y
C | West | OTP, XEL | 2224 | 2011-07-01 | 49 | MTEP08 Reference Future EHV Overlay - Bigstone to Morris to Alexandria | Build 345 kV double circuit line from Big Stone in South Dakota to Morris and then to Alexandria Station in Minnesota | MN | SD\MN |  |  |  |  | 215000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 230 | C | Y
C | West | West | 3513 | 2011-06-07 | Bison 345/230 kV Transformers | Bison Substation | Bison 345/230 kV substation, associated breakers, 2-345/230 kV transformers | ND | [5 empty] | 17635000 | 2015-03-31 | 2015-03-31 | Planned | 345 | 230 | C | Y
C | West | XEL | 2177 | 2008-06-30 | RES | RES (230 kV Corridor study) | Convert Minn Valley - Panther - McLeod - Blue Lake 230 kV line to Double circuit 345 kV from Hazel to McLeod to West Waconia to Blue Lake. | MN |  |  | Other | Not Shared |  |  | 2016-06-01 | 2016-06-01 | Proposed | 345 | 115 | C | Y
C | West | XEL | 2184 | 2008-08-05 | 6 | MTEP08 Reference Future EHV Overlay - Splitrock to "New Blue Earth Sub" | Builds 345 kV circuit from Splitrock Station in South Dakota to a New Blue Earth Station in Minnesota | MN | SD/MN |  |  |  |  | 205000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | West | XEL | 2185 | 2008-08-05 | 7 | MTEP08 Reference Future EHV Overlay - Adams to Hampton Corners | Builds 765 kV circuit from Adams Station in Minnesota to Hampton Corners Station in Minnesota | MN | [5 empty] | 15000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | West | XEL | 2186 | 2008-08-05 | 8 | MTEP08 Reference Future EHV Overlay - Sherburne County to Chisago City | Builds 345 kV circuit from Sherbourne County Station to Chisago County Station in Minnesota | MN | [5 empty] | 69000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL | 2187 | 2008-08-05 | 9 | MTEP08 Reference Future EHV Overlay - Sherburne County to "New SW MPLS Sub" | Builds 345 kV circuit from Sherbourne County Station to New SW Minneapolis Station in Minnesota | MN | [5 empty] | 68000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL | 2188 | 2008-08-05 | 10 | MTEP08 Reference Future EHV Overlay - "New SW MPLS Sub" to Hampton Corners | Builds 765 kV circuit from Hampton Corner Station to New SW Minneapolis Station in Minnesota | MN | [5 empty] | 260000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | West | XEL | 2189 | 2008-08-05 | 11 | MTEP08 Reference Future EHV Overlay - Hampton Corners to Chisago Cty (east mpls loop) | Builds 345 kV circuit from Hampton Corner Station to Chisago County Station in Minnesota | MN | [5 empty] | 103000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL | 2191 | 2008-08-05 | 13 | MTEP08 Reference Future EHV Overlay - "New SW MPLS Sub" to "New Blue Earth Sub" | Builds 765 kV circuit from New SW Minneapolis Station to New Blue Earth Station in Minnesota | MN | [5 empty] | 215000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | West | XEL | 2217 | 2008-08-05 | 42 | MTEP08 Reference Future EHV Overlay - Granite Falls-Twin Cities | Build 345 kV circuit from Granite Falls (Hazel sub) to Blue Lake (Twin Cities) in Minnesota | MN | [5 empty] | 162000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL | 2222 | 2008-08-05 | 47 | MTEP08 Reference Future EHV Overlay - Minn Valley-Blue Lk 230 | Build 230 kV double circuit line from Minnesota Valley to West Waconia Station in Minnesota | MN | [5 empty] | 274000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 | 230 | C | Y
C | West | XEL | 2226 | 2008-08-05 | 51 | MTEP08 Reference Future EHV Overlay - Adams-N Rochester | Build 345 kV double circuit line from Adams Station to North Rochester in Minnesota | MN | [5 empty] | 101000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL | 2227 | 2008-08-05 | 52 | MTEP08 Reference Future EHV Overlay - Monticello-W Waconia-Helena | Build 345 kV double circuit line from Monticello to West Waconia to Helena in Minnesota | MN | [5 empty] | 102000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL, ATC LLC | 2210 | 2008-08-05 | 35 | MTEP08 Reference Future EHV Overlay - Chisago Cty to Longwood | Build 345 kV circuit from Chisago County Station in Minnesota to Longwood Station in Wisconsin | MN | WI |  |  |  |  | 165000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West | XEL, ITCM | 2212 | 2008-08-05 | 37 | MTEP08 Reference Future EHV Overlay - Adams to Rockcreek | Build 765 kV circuit from Adams Station in Minnesota to Rock Creek Station in Iowa | MN | IA |  |  |  |  | 627000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 |  | C | Y
C | West | XEL, MEC | 2192 | 2008-08-05 | 14 | MTEP08 Reference Future EHV Overlay - "New Blue Earth Sub" to Lehigh | Builds 765 kV Circuit from New Blue Earth Station in Minnesota to Lehigh Station in Iowa | IA | MN/IA |  |  |  |  | 273000000 | 2018-08-01 | 2018-08-01 | Conceptual | 765 | 345 | C | Y
C | West | XEL, MH, GRE, OTP, MP, MRE | 3398 | 2010-09-15 | Option W6 | Dorsey-Split Rock 500 kV line | Option W6: Dorsey(Manitoba)-Bison(ND)-Brookings(SD)-Split Rock (SD) 500 kV with 345/500 kV transformers. Also included is a 2nd 345 kV circuit on the Fargo-Alexandria-Quarry-Monticello 345 kV project (Project 286) and works in concert with the Brookings, SD - SE Twin Cities 345 kV project (Project ID 1203) and the Corridor project (Project ID 2177) | MB | SD |  |  |  |  | 1627000000 | 2017-12-31 | 2017-12-31 | Proposed | 500 | 345 | C | Y
C | West | XEL, Non-MISO | 2183 | 2008-08-05 | 5 | MTEP08 Reference Future EHV Overlay - Watertown to Split Rock | Builds 345 kV circuit from Watertown Station in South Dakota to Splitrock station in South Dakota | SD | [5 empty] | 131000000 | 2018-08-01 | 2018-08-01 | Conceptual | 345 |  | C | Y
C | West, Central, East | ITCM, AmerenIL | 2785 | 2009-04-23 | 6 | Northwest Iowa (New Substation)-Sorenson HVDC | Build new +/- 800 kV bi-pole HVDC line from a new Northwest Iowa substation to the existing Sorenson substation. The project will be capable of transferring approximately 1,500 MW independently or up to 7,900 MW coupled with the complimentary project (PrjID 2794). The project(s) also envision a regional collector system that will be vetted through the RGOS stakeholder process. | IA | IN |  |  |  |  | 1900500000 | 2014-05-01 | 2014-05-01 | Proposed | 800 |  | C | Y

## Fac Legend
MTEP11 MISO Transmission Expansion Plan 2011 |  | Appendices A, B,C
Facility Table Field Legend
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Facilty Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEP11 planning cycle. "A in MTEP11" projects were reviewed and approved in MTEP11. This column also indicates what projects were approved in prior MTEPs that are not yet in service.
Region | MISO Planning Region: Central, East or West
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Indicates the Facility's Project. Projects may have multiple facilities.
Facility ID | Facility ID: MISO facility identifier
Expected ISD | Expected In Service Date for this facility
From Sub | From substation for transmission line or location of transformer or other equipment
To Sub | To substation for transmission line or transformer designation
Ckt | Circuit identifier
Max kV | Maximum voltage of this facility
Min kV | Minumum voltage of this facility (transformer low-side voltage)
Facility Rating | Rating of the facility in applicable units. Typically Summer rate
Facility Description | Brief description of transmission facility
State | State the facility is located in
Miles Upg. | Transmission line miles on existing rights of way (ROW)
Miles New | Transmission line miles on new rights of way (ROW)
Plan Status | Indicates status of project in planning or implementation. Alternative, Conceptual, Proposed, Planned, Under Construction, In Service.
Estimated Cost | Total estimated facility cost
Cost Shared | Y if facility is cost shared per Attachment FF
Postage Stamp | Y if facility has postage stamp cost allocation per Attachment FF
MISO Facility | Y for facilities under MISO functional control. NT for non-transferred facilities under Agency Agreements
App ABC | Appendix the project is in. B>A or C>B for projects moving during this planning cycle.

## Facilities
MTEP11 MISO Transmission Expansion Plan 2011 | [28 empty] | Appendices A, B, C
Appendices A, B, C: Project Facility Table 9/7/2011
Target Appendix | Region | Geographic Location by TO Member System | PrjID | Prj Rec Date | Owner PrjID | Facility ID | Record Date | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Facility Rating | Facility Description | Map Grid | State | Miles Upg. | Miles New | Plan Status | Estimated Cost | Est Type | Gen Int Upgrade Type | TSR Cond Upg | Cost Shared | Postage Stamp | MISO Facility | App ABC
.
A in MTEP11 | Central | AmerenIL | 2065 | 2011-04-22 |  | 3961 | 2011-04-22 | TEQ | 2012-06-01 | Stallings | Stallings Tap (Wood River - Venice 138 line) | 1 | 138 |  | 280 | Replace terminal equipment at Stallings on Wood River - Venice 138 kV line (Line # 1452) | K11 | IL |  |  | Planned | 185000 |  |  |  | Y |  | Y | B>A
A in MTEP11 | Central | AmerenIL | 2065 | 2011-04-22 |  | 3960 | 2011-04-22 | TX | 2012-06-01 | Stallings | Stallings substation | 1 | 345 | 138 | 700 | Stallings 345/138 kV Substation-Replace 560 MVA, 345/138 kV Transformer with 700 MVA unit | K11 | IL |  |  | Planned | 9890000 |  |  |  | Y |  | Y | B>A
A in MTEP11 | Central | AmerenIL | 2237 | 2011-09-06 | MVP Port.1 | 4104 | 2011-09-07 | LN | 2018-11-15 | Pana | Mt. Zion | 1 | 345 |  | 1793 | new line - 28 miles of 345 kV |  | IL |  | 28 | Planned | 66610000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2237 | 2011-09-06 | MVP Port.1 | 5210 | 2011-09-07 | TX | 2018-11-15 | Kansas Sub | 2nd. 345/138 kV Xfmr | 2 | 345 | 138 | 560 | Kansas 345/138 kV Substation - Add 2nd 345/138 kV, 560 MVA Transformer, 345 kV Breaker-and-a-half arrangement. | L10 | IL |  |  | Planned | 25610000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2237 | 2011-09-06 | MVP Port.1 | 4151 | 2011-09-07 | TX | 2018-11-15 | Mt. Zion | Transformer | 1 | 345 | 138 | 560 | new transformer - 560 MVA, 345/138 kV, plus 345 kV ring bus |  | IL |  |  | Planned | 17770000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2237 | 2011-09-06 | MVP Port.1 | 4152 | 2011-09-07 | LN | 2018-11-15 | Mt. Zion | Kansas | 1 | 345 |  | 1793 | new line - 52 miles 345 kV |  | IL |  | 52 | Planned | 123710000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2237 | 2011-09-06 | MVP Port.1 | 4154 | 2011-09-07 | LN | 2019-11-15 | Kansas | Sugar Creek | 1 | 345 |  | 1793 | New 35 mi. single-circuit line, 3000 A SE capability |  | IL |  | 35 | Planned | 84710000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2239 | 2011-09-06 | 17 MVPP1 | 6595 | 2011-09-06 | LN | 2016-06-01 | Sidney |  | 1 | 345 |  | 1793 | Substation work for new Sidney-Risng 345 kV line |  | IL |  |  | Planned |  | 7/15 est |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2239 | 2011-09-06 | 17 MVPP1 | 6594 | 2011-09-06 | LN | 2016-06-01 | Rising |  | 1 | 345 |  | 1793 | Substation work for new Sidney-Risng 345 kV line |  | IL |  |  | Planned |  | 7/15 est |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2239 | 2011-09-06 | MVP Port.1 | 4153 | 2011-09-07 | LN | 2016-11-15 | Rising | Sidney | 1 | 345 |  | 1793 | New 28 mile, 345 kV line from Sidney to Rising Substations with 3000 A summer emergency capability. Establish ring bus at Rising and breaker-and-a-half arrangement at Sidney. |  | IL |  | 28 | Planned | 83230000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 2980 | 2010-12-06 |  | 5183 | 2011-04-22 | LN | 2013-06-01 | Tazewell | San Jose Rail | 1 | 138 |  | 269 | Tazewell-San Jose Rail Substation section of East Springfield-Tazewell-1384 138 kV Line - Reconductor 3.67 miles of 927 kcmil ACAR conductor at the Tazewell end of the line with conductor capable of carrying at least 1278 A under summer emergency conditio | K9 | IL | 3.67 |  | Planned | 3251000 | Engineering |  |  |  |  | Y | B>A
A in MTEP11 | Central | AmerenIL | 2981 | 2011-04-22 |  | 5184 | 2011-04-22 | LN | 2013-09-01 | McLean | El Paso Tap | 1 | 138 |  | 160 | Replace 9.72 miles of 138 kV line on L1382, from McLean County Substation to El Paso Tap to a minimum 1200A SE capability | K9 | IL | 9.72 |  | Planned | 5100000 | Engineering |  |  |  |  | Y | B>A
A in MTEP11 | Central | AmerenIL | 2989 | 2011-06-16 |  | 5193 | 2011-09-07 | TX | 2013-06-01 | Sidney Sustation | Transformer Addition |  | 345 | 138 | 560 | Sidney 345/138 kV Substation - Install 2nd. 345/138 kV, 560 MVA Transformer.and 345 kV Ring Bus | L9 | IL |  |  | Planned | 14200000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVPP1 | 6596 | 2011-09-06 | LN | 2016-06-01 | Palmyra Tap |  | 1 | 345 |  | 1793 | Build new 345 kV switching station at the Palmyra Tap location |  | IL |  |  | Planned |  |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVPP1 | 6598 | 2011-09-06 | LN | 2016-06-01 | Meredosia |  | 1 | 345 |  | 1793 | Substation work for new Meredosia-Ipava 345 kV line |  | IL |  |  | Planned |  |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVP Port.1 | 5616 | 2011-09-07 | TX | 2016-11-15 | Meredosia | Install 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Meredosia 345/138 kV Substation - Install 345/138 kV Xfmr, 345 kV ring bus. | J10 | IL |  |  | Planned | 18260000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | AMRN9 | 5202 | 2011-09-07 | LN | 2016-11-15 | Palmyra | Quincy | 1 | 345 |  | 1793 | New 14-mi. 345 kV 3000 A summer emergency capability line from Palmyra to Quincy. | J9 | IL |  | 14 | Planned | 25740000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVP Port.1 | 5227 | 2011-09-07 | LN | 2016-11-15 | Quincy Area | Meredosia | 1 | 345 |  | 1793 | New 47 m. single circuit line | J10 | IL |  | 47 | Planned | 108020000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | AMRN9 | 5203 | 2011-09-07 | TX | 2016-11-15 | Quincy Area | Xfmr Addition | 1 | 345 | 138 | 560 | Quincy Area 345/138 kV Substation - 1-560 MVA transformer, 345 kV ring bus. | J9 | IL |  |  | Planned | 19950000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVPP1 | 6597 | 2011-09-06 | LN | 2017-06-01 | Ipava |  | 1 | 345 |  | 1793 | Substation work for new Meredosia-Ipava 345 kV line |  | IL |  |  | Planned |  |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVP Port.1 | 4149 | 2011-09-07 | LN | 2017-11-15 | Meredosia | Ipava | 1 | 345 |  | 1793 | new line - 41 miles 345 kV. Establish 345 kV ring bus at Ipava Sub. |  | IL |  | 41 | Planned | 107900000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVP Port.1 | 4150 | 2011-09-07 | LN | 2017-11-15 | Meredosia | Pawnee | 1 | 345 |  | 1793 | New 55 mi. single-circuit line, 345 kV line |  | IL |  | 55 | Planned | 128610000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3017 | 2011-09-06 | 09 MVP Port.1 | 6430 | 2011-09-07 | TX | 2017-11-15 | Pawnee | Transformer | 2 | 345 | 138 | 560 | 2nd. 345/138, 560 MVA Xfmr, establish 345 kV breaker-and-a-half arrangement at Pawnee |  | IL |  |  | Planned | 23680000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3022 | 2011-09-06 | 16 MVPP1 | 6599 | 2011-09-06 | LN | 2019-06-01 | Fargo |  | 1 | 345 |  |  | Fargo substation work - add a new 345 kV position |  | IL |  |  | Planned |  | Planning 2010$ |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3169 | 2011-09-06 | MVP Port.1 | 5600 | 2011-09-07 | LN | 2018-11-15 | Pana | Pawnee | 1 | 345 |  | 1793 | New 31 mi. single-circuit line, 3000 A SE capability. |  | IL |  | 31 | Planned | 73750000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3169 | 2011-09-06 | MVP Port.1 | 6431 | 2011-09-07 | TX | 2018-11-15 | Pana | Transformer | 2 | 345 | 138 | 560 | Install 2nd. 345/138 kV Xfmr at Pana Sub., 345 kV breaker-and-a-half arrangement at Pana. |  | IL |  |  | Planned | 25610000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenIL | 3337 | 2011-04-22 |  | 6202 | 2010-12-06 | LN | 2013-12-01 | Paxton, East | Gilman | 1 | 138 |  | 240 | Reconductor to 1200 A summer emergency capability |  | IL | 22.1 |  | Planned | 7390000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3357 | 2011-04-22 |  | 6223 | 2011-04-22 | LN | 2012-12-31 | E. Kewanee | Princeton Tap L1552 | 1 | 138 |  | 160 | Increase ground clearance on 477 kcmil ACSR conductor to permit operation at 120 degrees C. Upgrade E. Kewanee breaker and terminal equipment to 1200 A capability |  | IL | 15.33 |  | Planned | 3180000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3358 | 2011-04-22 |  | 6224 | 2010-09-15 | CB | 2012-10-15 | E. Kewanee | Generator connection and bus rearrangement |  | 138 |  | 287 | Rearrange 138 kV bus at E. Kewanee and install terminal equipment (including 1200 A breaker) to connect wind farm (G545) |  | IL |  |  | Planned | 1501000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3359 | 2011-04-22 |  | 6225 | 2010-09-15 | CB | 2012-10-01 | E. Galesburg | Generator connection and bus upgrade |  | 138 |  | 287 | Upgrade 138 kV bus at E. Galesburg and install terminal equipment, including 1200 A breaker, to facilitate connection of wind farm (G569). |  | IL |  |  | Planned | 834000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3360 | 2011-04-22 | AMRN21 | 6227 | 2011-07-05 | SUB | 2011-05-06 | Sheldon South Sw. Station | Watseka | 1 | 138 |  | 240 | Replace or reset relaying as required to obtain 1200 A capability at the Watseka terminal |  | IL | 10 |  | In Service | 100000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3360 | 2011-04-22 | AMRN21 | 6226 | 2011-07-05 | SUB | 2011-05-06 | Sheldon South Sw. Station | Install ring bus with 3 - 1200 A breakers |  | 138 |  | 287 | Construct a new 138 kV switching station to connect a new wind farm (G931) to the Watseka-Morrison Ditch-1 138 kV line. |  | IL |  |  | In Service | 4325000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3361 | 2011-04-22 |  | 6228 | 2010-09-15 | CB | 2011-07-26 | Paxton, East | Generator connection |  | 138 |  | 478 | Install terminal equipment, including 2000 A breaker, to facilitate connection of wind farm (G996). Install 2000 A bus-tie breaker |  | IL |  |  | Planned | 1512200 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL | 3370 | 2011-04-22 |  | 6241 | 2010-09-15 | CB | 2012-06-01 | Oreana Sub. | Install 1-2000 A breaker and 2-2000 A disconnect switches. |  | 138 |  | 112 | Installation of a new 138-69 kV transformer at Oreana, install 1-2000 A breaker and 2-2000 A disconnect switches to expand ring bus. Install 138 kV, 600 A MOD switch at high-side of new 138-69 kV transformer. |  | IL |  |  | Planned | 750000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenIL, MEC | 3022 | 2011-09-06 | MVP Port.1 | 5232 | 2011-09-07 | LN | 2019-11-15 | Fargo | Oak Grove | 1 | 345 |  | 1793 | Fargo-Galesburg-Oak Grove (MEC) 345 kV Line - New 70 mile, 3000 A summer emergency capability line. 345 kV ring bus at Fargo. | K9 | IL |  | 70 | Planned | 200530000 | Planning 2010$ |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenMO | 2248 | 2011-09-06 | MVP Port.1 | 5187 | 2011-09-07 | TX | 2020-11-15 | West Adair Substation | Install Transformer | 1 | 345 | 161 | 560 | West Adair Substation - New 560 MVA, 345/161 kV Transformer, 345 kV ring bus. | I9 | MO |  |  | Planned | 18920000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenMO | 2306 | 2011-04-22 | AMRN2 | 4222 | 2011-04-22 | LN | 2016-06-01 | Lutesville | Northwest Cape | 1 | 345 |  | 1793 | Install approximately 11 miles of new line to supply substation | K11 | MO |  | 11 | Planned | 18181000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenMO | 2306 | 2011-04-22 | AMRN2 | 4221 | 2011-04-22 | SUB | 2016-06-01 | Northwest Cape 345/161 kV | New Substation |  | 345 | 161 | 560 | Install 560 MVA, 345/161 kV Transformer, 3-161 kV outlet lines | K11 | MO |  |  | Planned | 12570000 | Eng |  |  | Y |  | Y | B>A
A in MTEP11 | Central | AmerenMO | 3170 | 2011-09-06 | MVP Port.1 | 6603 | 2011-09-07 | SUB | 2016-11-15 | Palmyra Tap | Establish 345 kV Sub |  | 345 |  | 1793 | New Palmyra Tap Substation - Establish with breaker-and-a-half arrangement |  | MO |  |  | Planned | 17660000 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | AmerenMO | 3170 | 2011-09-06 | MVP Port.1 | 5601 | 2011-09-07 | LN | 2020-11-15 | West Adair | Palmyra Tap | 1 | 345 |  | 1793 | Construct new 58 mile, 345 kV Line | I9 | MO |  | 58 | Planned | 95130000 | Planning |  |  | Y | Y | y | B>A
A in MTEP11 | Central | AmerenMO | 3355 | 2011-04-22 | AMRN20 | 6220 | 2010-12-06 | CB | 2011-12-31 | Labadie | Bland | 3 | 345 |  | 1200 | Replace breaker at Labadie with 3000 A, 50 kA breaker |  | MO |  |  | Planned | 1305000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenMO | 3355 | 2011-04-22 | AMRN20 | 6221 | 2010-12-06 | CB | 2011-12-31 | Labadie | Montgomery | 4 | 345 |  | 1200 | Replace breaker at Labadie with 3000 A, 50 kA breaker |  | MO |  |  | Planned | 1305000 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenMO | 3368 | 2011-04-22 |  | 6239 | 2010-09-15 | CB | 2012-06-01 | Bailey | Install 2-2000 A breakers and circuit switchers |  | 138 |  | 214 | Install 2-2000 A bus-tie breakers and 2-138 kV circuit switchers |  | MO |  |  | Planned | 4000000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | AmerenMO, ITCM | 2248 | 2011-09-06 | MVP Port.1 | 4160 | 2011-09-07 | LN | 2020-11-15 | Ottumwa | West Adair | 1 | 345 |  | 1793 | New line - 345 kV, 71 mile single circuit |  | IA/MO |  | 71 | Planned | 154790000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | DEM | 3377 | 2010-09-15 | AMIN0342 | 6250 | 2010-09-15 | CAP | 2015-12-31 | Scottsburg | Capacitor |  | 69 |  | 28.8 MVAR | Replace Scottsburg 69kV - 7.2Mvar capacitor with a 28.8 Mvar capacitor and upgrade 69kV capacitor switching equipment |  | IN |  |  | Planned | 500000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3378 | 2010-09-15 | AMOH0286 | 6251 | 2010-09-15 | Dist | 2012-06-01 | Canal Road | new distribution sub |  | 69 | 12 |  | Canal Sub - Purchase land and build 22.4MVA, 69/12kV sub near Canal Road and Allison Street in the 5762 ckt. |  | OH |  |  | Planned | 756196 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3379 | 2010-09-15 | AMIN0138 | 6252 | 2010-09-15 | Dist | 2014-06-01 | Shelbyville McKay Rd. | new distribution sub |  | 69 | 12 |  | Shelbyville McKay Rd. - add new 69/12kV distribution sub in the 6976 ckt. Loop through with 954acsr and a set of 1200A line switches. |  | IN |  |  | Planned | 303710 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3380 | 2010-09-15 | AMIN0340 | 6253 | 2010-09-15 | CB | 2011-12-31 | Noblesville Gen. Station | breakers |  | 345 | 138 |  | Noblesville Gen. Sta. - Replace 138KV OB OCB: 138TR, 13869-9, 138230-7, 13886 and Circuit Switchers: 345230-11, 34519. |  | IN |  |  | Planned | 2909606 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3383 | 2010-10-12 | AMIN0364 | 6256 | 2011-06-23 | LN | 2011-02-06 | Sherman Rd. Jct (new) | H.E. Rocklane | 1 | 69 |  |  | Ckt. 6999 new Sherman Rd. Jct. to H.E. Rocklane line section. Replace DEM 69kV poles to accommodate new H.E. tap line. This will be an alternate feed to Rocklane - operated N.O. - built and owned by HE, inside DEM area. |  | IN |  |  | In Service | 64568 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3384 | 2010-09-15 | AMIN0382 | 6257 | 2010-09-15 | LNrc | 2012-12-01 | Hortonville | Marathon Jct. | 1 | 69 |  | 143 | Hortonville to Marathon Jct. section of ckt. 6917 - Replace 336ACSR and 477ACSR with 954ACSS@200C. Upgrade Marathon Jct 600A switches to 1200A. |  | IN | 3.86 |  | Planned | 1409099 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3385 | 2010-09-15 | AMIN0376 | 6258 | 2011-03-25 | LNrc | 2012-12-31 | Carmel Homeplace | Springmill Jct. | 1 | 69 |  | 143 | Carmel Homeplace to Springmill Jct. section of ckt. 69155 - Reconductor with 954ACSS@200C |  | IN | 3.66 |  | Planned | 1691315 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3386 | 2010-09-15 | AMIN0379 | 6259 | 2010-09-15 | LN | 2016-06-01 | Carmel Springmill Rd. | Hortonville | 1 | 69 |  | 143 | Carmel Springmill Rd. Sub - Add 3-69kV breakers; straight bus config; build .23 mi 69kV 954ACSS@200C from Springmill to old Springmill Jct. Completes circuit to Hortonville. Change operating mode at Homeplace to close loop from 146th to Springmill. |  | IN |  | 0.23 | Planned | 3000000 | Planning 2010 $ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3387 | 2010-09-15 | AMIN0386 | 6260 | 2011-03-25 | GEN | 2013-06-01 | Tri-County Wind Energy 230kV Station - DPP J028 | new gen i-connect | 1 | 230 |  |  | J028 - 230kV - Gen. interconnect sub - install three brkr ring bus for 200MW wind farm between Attica and Lafayette in the 23027 ckt. |  | IN |  |  | Planned | 3778246 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3388 | 2010-09-15 | AMIN0396 | 6261 | 2010-09-15 | LNrc | 2015-06-01 | Walton | Logansport South | 1 | 69 |  | 100 | Walton to Logansport S. - Reconductor 69kV - 69110 line with 477acsr at 100C |  | IN | 5.9 |  | Planned | 1900000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3389 | 2011-03-25 | DEM-WVPA01 | 6262 | 2011-03-25 | Dist | 2011-12-01 | WVPA Center Valley | new WVPA distribution sub |  | 138 | 12 |  | DEM to install new line switching in the 138kV - 13867 ckt. at intersection with SR39 for tap line to radially feed new WVPA Center Valley dist sub |  | IN |  |  | Planned | 236677 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3390 | 2010-10-12 | AMIN0414 | 6263 | 2011-01-11 | LNrc | 2011-12-31 | Inland Container | Hillsdale | 1 | 69 |  | 100 | Rebuild 69kV - 6906 line from Inland Container to WROW Jct. to Hillsdale - 477acsr26x7 at 100C |  | IN | 10.8 |  | Planned | 3663434 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3391 | 2010-09-15 | AMIN0415 | 6264 | 2010-09-15 | LNrc | 2011-12-31 | Elnora | Newberry | 1 | 69 |  | 100 | Rebuild 69kV - 6959 line section from Elnora to Newberry - 477acsr26x7 at 100C |  | IN | 5.4 |  | Planned | 1716818 | Engineering 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM | 3392 | 2011-01-24 | DEM-LGEE01 | 6265 | 2011-01-24 | LN | 2012-12-31 | Speed | LGEE Paddys West | 1 | 345 |  | 1529 | New DEM Speed to LGEE Paddys West 345kV tie line |  | IN |  | 16.66 | Planned | 15000000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | DEM, NIPS | 2202 | 2011-07-18 | 14 MVPP1 | 4074 | 2011-07-18 | LN | 2018-06-01 | Reynolds | Greentown | 1 | 765 |  | 3576 | new line |  | IN |  | 66 | Planned | 171875000 | planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | IPL | 3273 | 2010-09-15 |  | 6105 | 2010-09-15 | LNup | 2011-06-01 | Southwest | Stout CT | 1 | 138 |  | 350 | Line Survey and Potential Modifications |  | IN | 2.9 |  | Planned | 300000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | IPL | 3274 | 2010-09-15 |  | 6106 | 2010-09-15 | LNup | 2011-06-01 | South | Stout S | 1 | 138 |  | 287 | Line Survey and Potential Modifications |  | IN | 3.34 |  | Planned | 350000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | Central | NIPS | 2202 | 2011-07-18 | 14 MVPP1 | 4073 | 2011-07-18 | TX | 2018-08-01 | Reynolds | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | IN |  |  | Planned | 15000000 | planning |  |  | Y | Y | Y | B>A
A in MTEP11 | Central | Vectren | 2460 | 2008-10-31 | SIGE1 | 4424 | 2011-06-29 | SUB | 2013-06-01 | Leonard Rd 69kV Substation |  | 1 | 69 |  |  | Add new 69kV switching substation near Leonard Rd | L11 | IN |  |  | Planned | 2150000 | Budgetary |  |  |  |  | NT | C>B>A
A in MTEP11 | Central | Vectren | 2462 | 2008-10-31 | SIGE3 | 4426 | 2011-01-10 | LN | 2013-06-01 | Stringtown | Folz | 50-3 | 69 |  |  | Reconductor existing 69kV line for more capacity | L11 | IN |  |  | Planned | 2500000 | Budgetary |  |  |  |  | NT | C>B>A
A in MTEP11 | Central | Vectren | 2463 | 2008-10-31 | SIGE4 | 4427 | 2008-10-31 | LN | 2013-06-01 | Givens | North West | 31 | 69 |  |  | Reconductor existing 69kV line for more capacity | L11 | IN |  |  | Planned | 5700000 | Budgetary |  |  |  |  | NT | C>B>A
A in MTEP11 | Central | Vectren | 2464 | 2008-10-31 | SIGE5 | 4428 | 2011-01-10 | LN | 2014-06-01 | Mt Vernon | New Harmony | 33 | 69 |  |  | Reconductor existing 69kV line for more capacity | L11 | IN |  |  | Planned | 10600000 | Budgetary |  |  |  |  | NT | C>B>A
A in MTEP11 | East | ATC LLC | 3396 | 2010-09-15 | PR04184 | 6271 | 2011-03-18 | LNup | 2010-11-15 | Blue River Tap | Muscoda | 1 | 69 |  | 67 | Improve line clearance |  | WI | 9 |  | In Service | 580000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 1868 | 2010-10-20 |  | 3755 | 2010-10-20 | CB, TEQ | 2012-12-01 | Cato 120 kV | Substation Equipment |  | 120 |  |  | Rebuild GIS Bus and Replace 120 kV breaker |  | MI |  |  | Planned | 5400000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 2931 | 2009-09-14 |  | 5103 | 2011-01-11 | LN | 2012-06-30 | Burns1 | Jewel | 1 | 120 |  |  | Rebuild 2.4 miles of DC 3/0 Cu 120 kV lin to 1431 ACSR 230 kV construction. |  | MI | 2.4 |  | Planned | 1600000 | [5 empty] | Y | C>B>A
A in MTEP11 | East | ITC | 2931 | 2009-09-14 |  | 5102 | 2011-01-11 | LN | 2012-06-30 | Adams | Spokane | 1 | 120 |  |  | Rebuild 2.4 miles of DC 3/0 Cu 120 kV lin to 1431 ACSR 230 kV construction. |  | MI | 2.4 |  | Planned | 1600000 | [5 empty] | Y | C>B>A
A in MTEP11 | East | ITC | 3276 | 2010-09-15 | 2 | 6108 | 2010-09-15 | CB | 2013-12-31 | [6 empty] | Replace Damaged or Defective Breakers |  | Mi |  |  | Planned | 9000000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3277 | 2010-09-15 | 3 | 6109 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Meet NERC PRC-023 Compliance |  | Mi |  |  | Planned | 2400000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3278 | 2010-09-15 | 4 | 6110 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Replace Damaged or Defective Potential Devices |  | Mi |  |  | Planned | 300000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3279 | 2010-09-15 | 5 | 6111 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Replace Damaged or Defective Relays |  | Mi |  |  | Planned | 1800000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3280 | 2010-09-15 | 6 | 6112 | 2010-09-15 | LNrb | 2013-12-31 | [6 empty] | Replace Damaged or Defective Wood Poles |  | Mi |  |  | Planned | 3000000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3281 | 2010-09-15 | 7 | 6113 | 2010-09-15 | LN | 2012-12-31 | Majestic | Lima | 1 | 120 |  | 305 | Construct new 120 kV line between Majestic and Lima, along with associated breakers and terminal equiment at each termination. |  | Mi |  | 5 | Planned | 8400000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3283 | 2010-09-15 | 9 | 6115 | 2011-06-30 | LN | 2012-11-01 | Dexter Twp | Madrid | 1 | 120 |  | 300 | Loop Madrid to Majestic 120 kV line and new breaker station |  | Mi |  | 0.1 | Planned | 1338000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3283 | 2010-09-15 | 9 | 6116 | 2011-06-30 | LN | 2012-11-01 | Dexter Twp | Majestic | 1 | 120 |  | 300 | Loop Madrid to Majestic 120 kV line and new breaker station |  | Mi |  | 0.1 | Planned | 1338000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3284 | 2010-09-15 | 10 | 6117 | 2010-09-15 |  | 2015-12-31 | [6 empty] | Distribution Interconnection Request |  | Mi |  |  | Planned | 2000000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3285 | 2011-07-18 |  | 6516 | 2011-07-18 | CAP | 2013-06-01 | Shoal | 33.3 Mvar capacitor |  | 120 |  |  | 33.3 Mvar Capacitor at Shoal 120kV |  | Mi |  |  | Planned | 2200000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3285 | 2011-07-18 | 11 | 6118 | 2011-07-18 | CAP | 2014-06-01 | Fermi | 33.3 Mvar capacitor |  | 120 |  |  | 33.3 Mvar Capacitor at Fermi 120kV |  | Mi |  |  | Planned | 1600000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3286 | 2011-07-18 |  | 6519 | 2011-07-18 | TEQ | 2012-04-30 | Fermi |  |  | 345 |  |  | Add 3rd Fermi 345kV row |  | Mi |  |  | Planned | 4100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3286 | 2011-07-18 | 12 | 6119 | 2011-07-18 | TEQ | 2013-12-31 | Fermi |  |  | 345 |  |  | Replace 345kV Disconnects |  | Mi |  |  | Planned | 950000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3495 | 2011-03-28 | NERC Alert Ratings | 6455 | 2011-07-18 |  | 2011-12-31 | NERC Alert Facility Ratings for 2011 | Throughout system |  |  |  |  | Verify facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | 1700000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | ITC | 3503 | 2011-03-28 |  | 6463 | 2011-06-30 |  | 2012-12-31 | Air Flow Spoilers Installation |  |  | 345 |  |  | Install Air Flow Spoilers on Belle River-Greenwood-Pontiac and Belle River-Blackfoot 345 kV lines |  | MI |  |  | Planned | 1620000 | [5 empty] | Y | C>B>A
A in MTEP11 | East | ITC | 3516 | 2011-06-30 | J025 | 6500 | 2011-06-30 | RLY | 2011-09-01 | St. Clair P.P. | substation |  | 120 |  |  | Install a RFL 9745 Transmitter at St. Clair P.P. end of ITC line. |  | MI |  |  | Planned | 5000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | ITC | 3516 | 2011-06-30 | J025 | 6497 | 2011-06-30 | TAP | 2011-09-01 | Carbon | Carbon Tap |  | 120 |  |  | Tap the existing LES/Sumpter Energy Associates Carbon to Carbon Tap 120 kV radial line connecting to ITC's Jewell - St. Clair 120kV line with a new J025 Tap for the new customer. Install a one way disconnect switch and tap structure at the POI on the Car |  | MI |  |  | Planned | 237500 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | ITC | 3516 | 2011-06-30 | J025 | 6498 | 2011-06-30 | TAP | 2011-09-01 | J025 Tap | J025 Customer Sub |  | 120 |  |  | Install a one way disconnect switch and tap structure at the Point of Change of Ownership at the new J025 Tap on the radial line from the J025 Customer Substation. |  | MI |  |  | Planned | 237500 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | ITC | 3516 | 2011-06-30 | J025 | 6499 | 2011-06-30 | RLY | 2011-09-01 | Jewell | substation |  | 120 |  |  | Install a RFL 9745Transmitter at Jewell end of ITC line. |  | MI |  |  | Planned | 5000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 1809 | 2010-10-20 |  | 3632 | 2010-10-20 | LNrb | 2013-12-31 | Keystone | Hodenpyl | 1 | 138 |  | 351 | Rebuild 26.4 miles 138 kV line |  | Mi | 26.4 |  | Planned | 32600000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 2812 | 2010-10-20 |  | 4507 | 2010-10-20 | LNrb | 2012-05-31 | Twining | Whittemore | 1 | 138 |  | 215 | Rebuild the 12.7 mile Twining-Whittemore 138kV section to 954 ACSR future-double-circuit (pre-built to 230kV) |  | MI | 12.7 |  | Planned | 14200000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 2812 | 2010-10-20 |  | 4508 | 2010-10-20 | LNrb | 2012-05-31 | Whittemore | Loud Dam | 1 | 138 |  | 86 | Rebuild the 15.6 mile Twining-Mio 138kV section to 954 ACSR future-double-circuit (pre-built to 230kV) |  | MI | 15.6 |  | Planned | 17500000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 2812 | 2010-10-20 |  | 4509 | 2010-10-20 | LNrb | 2012-05-31 | Loud Dam | Alcona | 1 | 138 |  | 86 | Rebuild the 9.9 mile Twining-Mio 138kV section to 954 ACSR future-double-circuit (pre-built to 230kV) |  | MI | 9.9 |  | Planned | 11600000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3139 | 2010-10-20 |  | 5517 | 2010-10-20 | TEQ | 2012-06-01 | Tippy | Wexford | 1 | 138 |  |  | Replace terminal equipment at Tippy |  | MI |  |  | Planned | 20000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3287 | 2010-09-15 | 1 | 6120 | 2011-06-30 | TEQ | 2011-09-30 | Riggsville |  |  | 138 |  |  | Replace 138 kV Terminal Equipment |  | Mi |  |  | Planned | 4600000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3288 | 2010-09-15 | 2 | 6121 | 2010-09-15 | CB | 2013-12-31 | [6 empty] | Replace Damaged or Defective Breakers |  | Mi |  |  | Planned | 6000000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3289 | 2010-09-15 | 3 | 6122 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Meet NERC PRC-023 Compliance |  | Mi |  |  | Planned | 2400000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3290 | 2010-09-15 | 4 | 6123 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Replace Damaged or Defective Potential Devices |  | Mi |  |  | Planned | 300000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3291 | 2010-09-15 | 5 | 6124 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Replace Damaged or Defective Relays |  | Mi |  |  | Planned | 1200000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3292 | 2010-09-15 | 6 | 6125 | 2010-09-15 | LNrb | 2013-12-31 | [6 empty] | Replace Damaged or Defective Wood Poles |  | Mi |  |  | Planned | 4800000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3293 | 2010-09-15 | 7 | 6126 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Replace Damaged or Defective Batteries |  | Mi |  |  | Planned | 100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3294 | 2010-09-15 | 8 | 6127 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Relocate Power Plant Controls for better access |  | Mi |  |  | Planned | 3120000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3295 | 2010-09-15 | 9 | 6128 | 2010-09-15 | LNup | 2013-12-31 | [6 empty] | Address NECS Code Clearance Issues |  | Mi |  |  | Planned | 3600000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3296 | 2010-09-15 | 10 | 6129 | 2010-09-15 | TEQ | 2011-12-31 | [6 empty] | Install or upgrade secondary oil containment |  | Mi |  |  | Planned | 3100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3297 | 2010-09-15 | 11 | 6130 | 2010-09-15 | TEQ | 2012-12-31 | [6 empty] | Install or upgrade secondary oil containment |  | Mi |  |  | Planned | 3100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3298 | 2010-09-15 | 12 | 6131 | 2010-09-15 | TEQ | 2013-12-31 | [6 empty] | Install or upgrade secondary oil containment |  | Mi |  |  | Planned | 3100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3299 | 2010-09-15 | 13 | 6132 | 2010-09-15 | TEQ | 2015-12-31 | [6 empty] | Distribution Interconnection Request |  | Mi |  |  | Planned | 2500000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3303 | 2010-10-20 |  | 6136 | 2010-10-20 | LNrb | 2015-06-01 | Cottage Grove | East Tawas | 1 | 138 |  | 287 | Rebuild 12.3 miles of 138kV to 954 ACSR. |  | MI | 12.3 |  | Planned | 11400000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3304 | 2011-03-28 | 18 | 6137 | 2011-03-28 | LNrb | 2013-12-31 | Croton | Nineteen Mile Rd | 1 | 138 |  | 196 | Rebuild 21.5 miles 138 kV line |  | Mi | 21.5 |  | Planned | 26600000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3306 | 2010-09-15 | 20 | 6139 | 2010-09-15 | TEQ | 2012-06-01 | Karn |  |  | 138 |  |  | Replace relays |  | Mi |  |  | Planned | 200000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3308 | 2010-09-15 | 22 | 6143 | 2010-09-15 | TEQ | 2012-12-31 | Gaylord | Livingston | 1 | 138 |  |  | Install new dual pilot relay scheme on 138kV circuit |  | Mi |  |  | Planned | 315000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3491 | 2011-03-28 | NERC Alert Ratings | 6451 | 2011-07-18 |  | 2011-12-31 | NERC Alert Facility Ratings for 2011 | Throughout system |  |  |  |  | Verify facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | 2100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6472 | 2011-04-19 | SwSt | 2013-01-01 | Clinton Jct. |  | 1 | 138 |  |  | New Switching Station at existing Clinton Jct. Tap point on Delhi - Island Rd. circuit. Will connect exsiting 3 circuits plus new circuit to Eaton Rapids area. |  | MI |  |  | Planned | 4500000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6466 | 2011-04-19 | SwSt | 2013-01-01 | URV Junction |  |  | 138 |  |  | New Switching Station looping in Tompkins-Kipp Rd 138kV circuit |  | MI |  |  | Planned | 4100000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6467 | 2011-04-19 | LN | 2013-01-01 | Tompkins | Kipp Rd | 1 | 138 |  |  | Loop Tompkins-Kipp Rd into new URV Jct. Station |  | MI |  |  | Planned | 500000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6468 | 2011-04-19 | LN | 2013-01-01 | Eaton Rapids North | URV | 1 | 138 |  |  | New Line. On same structures as URV to Eaton Rapids Wolv. |  | MI |  | 2 | Planned | 1800000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6469 | 2011-04-19 | SUB | 2013-01-01 | URV |  | 1 | 138 |  |  | New Substation to serve Eaton Rapids load (URV-USA) |  | MI |  |  | Planned | 2600000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6470 | 2011-04-19 | LN | 2013-01-01 | URV | Eaton Rapids Wolv | 1 | 138 |  |  | New Line from URV to potential Wolverine Tap point. On same structures as Eaton Rapids North to URV. |  | MI |  | 2 | Planned | 1800000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3505 | 2011-04-19 |  | 6471 | 2011-04-19 | LN | 2013-01-01 | Eaton Rapids Wolv | Clinton Jct | 1 | 138 |  |  | New Line from Clinton Jct. to potential Wolverine Tap point. |  | MI |  | 10.4 | Planned | 13200000 | [5 empty] | Y | A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6502 | 2011-06-30 | LINE | 2011-10-31 | Redstone | Tittabawassee | 1 | 138 |  | 159 MVA | Line created when the existing Tittabawassee-Begole line is cut into Redstone |  | MI |  |  | Planned | 226000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6503 | 2011-06-30 | SUB | 2011-10-31 | Redstone |  |  | 138 |  |  | New Redstone substation will be layed out in a 3-breaker ring bus configuration. |  | MI |  |  | Planned | 4100000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6510 | 2011-06-30 | LINE | 2011-10-31 | Redstone | Gratiot Wind | 1 | 138 |  |  | Install a METC owned 138 kVdisconnect switch at the Redstone end of the interconnection customers radial line |  | MI |  |  | Planned | 390500 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6509 | 2011-06-30 | LINE | 2012-12-31 | Summerton | Begole | 1 | 138 |  | 159 MVA | New line created by looping the existing Alma-Summerton 138 kV line into Begole |  | MI |  | 2.4 | Planned | 1775000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6508 | 2011-06-30 | LINE | 2012-12-31 | Alma | Begole | 2 | 138 |  | 159 MVA | New line created by looping the existing Alma-Summerton 138 kV line into Begole |  | MI |  | 2.4 | Planned | 1775000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6501 | 2011-06-30 | LINE | 2012-12-31 | Redstone | Begole | 1 | 138 |  | 386 MVA | Rebuild the existing line between Redstone and Begole to 1431 ACSR |  | MI | 10.7 |  | Planned | 8109000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6507 | 2011-06-30 | LINE | 2012-12-31 | Alma | Vestaburg | 1 | 138 |  | 159 MVA | Replace terminal equipment at the Alma end of the Alma-Vestaburg 138 kV line |  | MI |  |  | Planned | 170000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6506 | 2011-06-30 | LINE | 2012-12-31 | Alma | Begole | 1 | 138 |  | 159 MVA | Replace terminal equipment at the Alma end of the Alma-Begole 138 kV line |  | MI |  |  | Planned | 170000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6505 | 2011-06-30 | LINE | 2012-12-31 | Cornell | Bennington | 1 | 138 |  | 159 MVA | Replace terminal equipment at the Cornell end of the Cornell-Bennington 138 kV line |  | MI |  |  | Planned | 15000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3517 | 2011-06-30 | G905 | 6504 | 2011-06-30 | SUB | 2012-12-31 | Begole |  |  | 138 |  |  | Reconfigure and expand the existing Begole substation into a 5-breaker ring bus layout |  | MI |  |  | Planned | 4900000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3518 | 2011-06-30 | G809 | 6511 | 2011-06-30 | LINE | 2012-06-01 | MCV | Tittabawassee | 1 | 345 |  | 1239 MVA | Remove 345 kV Disconnect switch from the Tittabawassee end of the MCV-Tittabawassee #1 345 kV line and extend the line entrance into the bus |  | MI |  |  | Planned | 32000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3518 | 2011-06-30 | G809 | 6512 | 2011-06-30 | LINE | 2012-06-01 | MCV | Tittabawassee | 2 | 345 |  | 1239 MVA | Remove 345 kV Disconnect switch from the Tittabawassee end of the MCV-Tittabawassee #2 345 kV line and extend the line entrance into the bus |  | MI |  |  | Planned | 32000 | Engineering |  |  | Y |  | Y | C>B>A
A in MTEP11 | East | METC | 3520 | 2011-07-18 | NERC Alert Ratings | 6517 | 2011-07-18 | Lnup | 2012-06-01 | Eureka 138kV | Vestaburg 138kV | 1 | 138 |  |  | Remediate sag limits to conductor rating of circuit |  | Mi |  |  | Planned | 1100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | METC | 3521 | 2011-07-18 | NERC Alert Ratings | 6518 | 2011-07-18 | Lnup | 2012-06-01 | Bullock 138kV | Summerton 138kV | 1 | 138 |  |  | Remediate sag limits to conductor rating of circuit |  | Mi |  |  | Planned | 3600000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | NIPS | 3203 | 2011-07-18 | 12 MVPP1 | 5949 | 2011-07-18 | LN | 2019-12-31 | Reynolds | Hiple | 2 | 345 |  |  | new line tap at Burr Oak |  | IN |  |  | Planned | 271000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | East | WPSC | 3328 | 2010-09-15 |  | 6191 | 2011-03-17 | TAP | 2011-12-31 | Hersey | Barryton | 1 | 69 |  |  | Barryton Taps the Hersey to Weidman 69kV circuit |  | MI |  |  | Planned | 100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3329 | 2010-09-15 |  | 6192 | 2011-03-17 | TAP | 2011-12-31 | Barryton | Weidman | 1 | 69 |  |  | Barryton Taps the Hersey to Weidman 69kV circuit |  | MI |  |  | Planned | 100000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3329 | 2010-09-15 | BP-WD | 6194 | 2011-01-05 | LNrb | 2013-12-31 | Goodwin | Wayland | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line to 795ACSS |  | MI | 4.58 |  | Planned | 1900000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3329 | 2010-09-15 | BP-WD | 6193 | 2011-01-05 | LNrb | 2013-12-31 | Burnips | Goodwin | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line to 795ACSS |  | MI | 13.09 |  | Planned | 5250000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3330 | 2010-09-15 | Casnovia Cap. Bank | 6195 | 2011-01-05 | CAP | 2011-12-31 | Casnovia | Capacitor Bank |  | 69 |  |  | Install a Capacitor Bank |  | MI |  |  | Planned | 260000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3331 | 2010-09-15 | RW-HT | 6196 | 2011-01-05 | LNrb | 2015-12-31 | Redwood | Hart | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line to 795ACSS |  | MI | 1.77 |  | Planned | 750000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3332 | 2011-03-17 | Bass Lake Xmsn | 6197 | 2011-03-17 | SUB | 2011-02-28 | Bass Lake | Substation Upgrade |  | 69 |  |  | Install Relaying at the current single breaker station |  | MI |  |  | In Service | 250000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3333 | 2010-09-15 | Lemon Jct Xmsn | 6198 | 2010-09-15 | SUB | 2011-12-31 | Lemon Junction | Substation Upgrade |  | 69 |  |  | Install a Single Breaker Station |  | MI |  |  | Planned | 350000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3334 | 2011-06-23 | CV-SG | 6199 | 2011-06-23 | LNrb | 2011-06-30 | Casnovia | Sternberg | 1 | 69 |  | 143.4MVA | Rebuild a portion of the line to accommodate work on the distribution underbuild |  | MI | 1.5 |  | In Service | 400000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | East | WPSC | 3335 | 2010-09-15 | Burnips Xsmn | 6200 | 2011-01-05 | SUB | 2013-12-31 | Burnips | Substation Upgrade |  | 69 |  |  | Replace bus work, breakers, relays, and any other necessary components |  | MI |  |  | Planned | 900000 | 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | West | AmerenMO, ITCM, MEC | 2248 | 2011-09-06 | 07 MVP Port.1 | 6584 | 2011-08-25 | LN | 2017-06-01 | Ottumwa | Adair | 1 | 345 |  | 1739 | New Ottumwa-Adair 345 kV line. ITCM & MEC to own Iowa portion, Ameren to own Missouri portion. |  | IA |  | 64 | Planned | 32164000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 174 | 2010-09-15 | 152, F1358 | 3477 | 2010-12-03 | TX | 2012-03-01 | Dunn Road | Transformer | 1 | 138 | 69 | 56 | Install 56 MVA 138/69 kV transformer at Dunn Road |  | WI |  |  | Planned | [6 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 174 | 2010-09-15 | 152, F1358 | 442 | 2011-02-24 | LN | 2012-03-01 | Canal | Dunn Road | 1 | 138 |  | 290 | New 138kV line from Canal to Dunn Rd | L6 | WI |  | 7.64 | Planned | 24763300 | Eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 333 | 2010-09-15 | F3068 | 596 | 2011-06-17 | LN | 2013-06-01 | Hiawatha | Indian Lake (string second 138 kV circuit) | 2 | 138 |  | 277 | terminate and energize unused 2nd 138 kV circuit | L5 | MI |  | 40 | Planned | 4900000 | Eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 333 | 2010-09-15 | F3068 | 474 | 2011-06-17 | LNrb | 2013-06-01 | Hiawatha | Indian Lake (convert double circuit 138 kV from 69 kV operation to 138 kV o | 2 | 138 |  | 277 | Convert from 69kV operation to 138kV operation | L5 | MI | 40 |  | Planned |  | Eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 1143 | 2010-12-03 | G282, F0339 | 1793 | 2011-02-24 | GEN | 2012-12-31 | Lafayette (aka Darlington Wind) | generator |  | 0.6 |  | 99 MW | new generator |  | WI |  |  | Planned | 4200000 |  | Generator |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 1699 | 2010-10-21 |  | 5979 | 2011-06-17 | CAP | 2011-07-31 | Chaffee Ck | Capacitor Bank |  | 69 |  | 14.4 MVAR | Upgrade Chaffee Ck 10.8 MVAR capacitor bank to 14.4 MVAR |  | WI |  |  | Planned | 282779 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 1699 | 2010-10-21 |  | 3478 | 2011-06-17 | CAP | 2011-07-31 | Mckenna | Capacitor bank |  | 69 |  | 15.3 MVAR | Upgrade Mckenna 6.3 MVAR capacitor bank to 15.3 MVAR |  | WI |  |  | Planned | 403971 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 1705 | 2010-09-15 |  | 3487 | 2011-06-17 | LN | 2011-04-01 | Townline Road | Bass Creek | 1 | 138 |  | 146 MVA | Uprate Townline Road-Bass Creek 138 kV line |  | WI | 11.7 |  | In Service | 935946.49 | [5 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 1705 | 2010-09-15 |  | 3486 | 2011-06-17 | TX | 2011-04-01 | Bass Creek | Transformer | 1 | 138 | 69 | 100 MVA | Install a 138/69 kV transformer at Bass Creek substation |  | WI |  |  | In Service | 6040000 | [5 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 1729 | 2010-09-15 | PR03341 | 3518 | 2011-06-17 | LN | 2011-04-20 | Straits | McGulpin | 1 | 138 |  | 127 MVA | Uprate the Straits-McGulpin 138 kV line 9901 for Frontier T-D |  | MI | 2.5 |  | In Service | 150000 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 1729 | 2010-09-15 | PR03341 | 3519 | 2011-06-17 | LN | 2011-04-20 | Straits | McGulpin | 3 | 138 |  | 127 MVA | Uprate the Straits-McGulpin 138 kV line 9903 for Frontier T-D |  | MI | 2.5 |  | In Service | 150000 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 1950 | 2010-09-15 | PR01874 | 3831 | 2011-06-17 | TX | 2011-03-17 | Kewaunee | transformer | 2 | 345 | 138 | 500 MVA | Add a 2nd Kewaunee 345-138 kV transformer |  | WI |  |  | In Service | 17697000 |  |  |  | Y |  | Y | B>A
A in MTEP11 | West | ATC LLC | 2036 | 2010-09-15 | F1444 | 3916 | 2011-03-18 | LNup | 2011-12-15 | Wauzeka | Boscobel | 1 | 69 |  | 64 MVA | Increase line clearance to 200/300 deg F SN/SE |  | WI | 12 |  | Planned | 3289758.342 | [5 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 2036 | 2010-09-15 | F1444 | 3915 | 2011-03-18 | LNup | 2011-12-15 | Gran Grae | Wauzeka | 1 | 69 |  | 73 MVA | Increase line clearance to 200/300 deg F SN/SE |  | WI | 7.3 |  | Planned | 2001269.658 | [5 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 2037 | 2011-04-19 |  | 3917 | 2011-04-19 | LNrb | 2012-06-19 | Dane | Lodi Tap | 1 | 69 |  | 95 MVA | Rebuild Dane-Lodi Tap 69 kV |  | WI |  | 4.39 | Planned | 6798033 | [5 empty] | Y | C>B>A
A in MTEP11 | West | ATC LLC | 2055 | 2010-09-15 | F2495 | 3942 | 2011-02-24 | SUB | 2012-06-01 | Woodmin | Substation |  | 115 |  | 175 MVA | Construst a new Woodmin distribution substation |  | WI |  |  | Planned |  |  | Interconnection |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 2055 | 2010-09-15 | F2495 | 3941 | 2011-02-24 | LN | 2012-06-01 | Clear Lake | Woodmin | 1 | 115 |  | 175 MVA | Construst a 7.5 mile 115 kv line from Clear Lake to a new Woodmin distribution substation |  | WI |  | 7.5 | Planned | 21331000 | [5 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 2800 | 2010-09-15 | F3042 | 4930 | 2010-12-03 | LN | 2010-09-10 | Arpin | Hume | 1 | 115 |  | 236 MVA | Marshfield Electric & Water Department project to increase ground clearance to operate the line at 200 Deg F |  | WI | 13.5 |  | In Service | 191000 | [5 empty] | Y | B>A
A in MTEP11 | West | ATC LLC | 2820 | 2010-12-03 | F2799 | 4958 | 2010-09-15 | TR | 2012-05-31 | Bluemound | transformer | 1 | 230 | 138 | 400 MVA | Replace Bluemound 230/138kV transformer T1 with a 400 MVA unit |  | WI |  |  | Planned | 8200000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 2842 | 2010-09-15 | F1656 | 5050 | 2011-06-17 | LN | 2011-04-08 | Stage Coach | Black Earth | 1 | 69 |  | 83 MVA | Uprate Stage Coach-Black Earth 69 kV |  | WI | 6.7 |  | In Service | 3554873 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 2842 | 2010-09-15 | F1656 | 5049 | 2011-06-17 | LN | 2011-04-08 | Spring Green | Arena | 1 | 69 |  | 84 MVA | Uprate Spring Green-Arena 69kV line |  | WI | 7 |  | In Service | 3402521 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 2844 | 2011-07-18 | 15 MVPP1 F3123 | 4998 | 2011-08-24 | LN | 2014-03-16 | Pleasant Prairie | Zion Energy Center | 1 | 345 |  | 1462 | Construct a new Pleasant-Zion Energy Center 345-kV line |  | WI/IL |  | 5.3 | Planned | 28856000 | Planning |  |  | Y | Y | Y | C>B>A
A in MTEP11 | West | ATC LLC | 2846 | 2010-12-03 | F2894 | 5068 | 2011-08-24 | TX | 2014-05-01 | Straits power flow control |  | 1 | 138 | 138 |  | Install AC-DC-AC Back to Back Voltage Source Converter (VSC) power flow controller at the Straits 138-kV substation |  | MI |  |  | Planned | 90000000 |  |  |  | Y |  | Y | A
A in MTEP11 | West | ATC LLC | 3095 | 2010-09-15 | PR03410 | 5420 | 2011-03-18 | LN | 2012-04-01 | Hulbert | Roberts | 1 | 69 |  | 37 MVA | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components |  | MI | 17.3 |  | Planned | 6034530.9823 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3095 | 2010-09-15 | PR03410 | 5418 | 2011-03-18 | LN | 2012-04-01 | Raco | Eckerman | 1 | 69 |  | 37 MVA | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components |  | MI | 12.1 |  | Planned | 4220683.5194 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3095 | 2010-09-15 | PR03410 | 5419 | 2011-03-18 | LN | 2012-04-01 | Eckerman | Hulbert | 1 | 69 |  | 37 MVA | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components |  | MI | 6.4 |  | Planned | 2232427.6466 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3095 | 2010-09-15 | PR03410 | 5416 | 2011-03-18 | LN | 2012-04-01 | 9Mile | Brimley | 1 | 69 |  | 37 MVA | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components |  | MI | 10.7 |  | Planned | 3732339.9717 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3095 | 2010-09-15 | PR03410 | 5417 | 2011-03-18 | LN | 2012-04-01 | Brimley | Raco | 1 | 69 |  | 37 MVA | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components |  | MI | 10.1 |  | Planned | 3523049.8799 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3108 | 2010-09-15 | PR03754 | 5450 | 2010-12-03 | LN | 2014-06-01 | Evergreen | Pine River | 1 | 69 |  | 174 MVA | Rebuild Straits-Pine River dbl ckt line with T2-477 ACSR |  | MI | 23.46 |  | Planned | 19145477 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3108 | 2010-09-15 | PR03754 | 5448 | 2010-12-03 | LN | 2014-06-01 | Straits | Pine River | 1 | 69 |  | 174 MVA | Rebuild Straits-Pine River dbl ckt line with T2-477 ACSR |  | MI | 25 |  | Planned | 20402257 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3108 | 2010-09-15 | PR03754 | 5449 | 2010-12-03 | LN | 2014-06-01 | Straits | Evergreen | 1 | 69 |  | 174 MVA | Rebuild Straits-Pine River dbl ckt line with T2-477 ACSR |  | MI | 1.54 |  | Planned | 1256779 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3126 | 2010-09-15 | PR03911 | 5477 | 2011-08-24 | TX | 2012-12-09 | Chandler | transformer | 2 | 138 | 69 | 60 MVA | Install a 2nd Chandler Transformer & reconfigure bus to 138 kV Ring bus |  | MI |  |  | Planned | 9700000 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5628 | 2011-07-25 | LN | 2018-12-31 | North Madison | Cardinal | 1 | 345 |  | 2110 | Construct a North Madison - Cardinal 345-kV line |  | WI |  | 20.546 | Planned | 45300000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5627 | 2011-07-25 | LNrb | 2018-12-31 | North Madison | Cardinal | 1 | 138 |  | 348 | Reconductor with T2-477 HAWK ACSR |  | WI | 20.546 |  | Planned | 6400000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5060 | 2011-07-25 | LN | 2020-12-31 | Arena | Mazomanie West | 1 | 138 |  | 348 MVA | Convert Arena-Mazomanie West from 69-kV to 138 kV |  | WI | 5 |  | Planned | 4400000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5065 | 2011-07-25 | LN | 2020-12-31 | Stage Coach | Cardinal | 1 | 138 |  | 348 MVA | Convert Stage Coach-West Middleton from 69-kV to 138 kV |  | WI | 4 |  | Planned | 9200000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5064 | 2011-07-25 | LN | 2020-12-31 | Black Earth | Stage Coach | 1 | 138 |  | 348 MVA | Convert Black Earth-Stage Coach from 69-kV to 138 kV |  | WI | 7 |  | Planned | 10800000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5063 | 2011-07-25 | LN | 2020-12-31 | Mazomanie | Black Earth | 1 | 138 |  | 348 MVA | Convert Mazomanie-Black Earth from 69-kV to 138 kV |  | WI | 4 |  | Planned | 2700000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5062 | 2011-07-25 | LN | 2020-12-31 | Mazomanie Industrial | Mazomanie | 1 | 138 |  | 348 MVA | Convert Mazomanie Industrial-Mazomanie from 69-kV to 138 kV |  | WI | 2 |  | Planned | 800000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5061 | 2011-07-25 | LN | 2020-12-31 | Mazomanie West | Mazomanie Industrial | 1 | 138 |  | 348 MVA | Convert Mazomanie West-Mazomanie Industrial from 69-kV to 138 kV |  | WI | 1 |  | Planned | 800000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 4978 | 2011-07-25 | TX | 2020-12-31 | Spring Green | Transformer | 1 | 345 | 138 | 500 | new transformer |  | WI |  |  | Planned | 0.01 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5059 | 2011-07-25 | LN | 2020-12-31 | Spring Green | Arena | 1 | 138 |  | 348 MVA | Convert Spring Green-Arena from 69-kV to 138 kV |  | WI | 7 |  | Planned | 5300000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5480 | 2011-07-25 | LNrb | 2020-12-31 | Nelson Dewey | Cassville | 1 | 161 |  | 342 MVA | Reconductor Nelson Dewey-Cassville |  | WI | 2.34 |  | Planned | 5200000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5481 | 2011-07-25 | LNrb | 2020-12-31 | Cassville | Turkey River | 1 | 161 |  | 445 MVA | Reconductor Cassville-Turkey River |  | WI/IA | 4 |  | Planned | 3700000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5483 | 2011-07-25 | SUB | 2020-12-31 | Spring Green | Substation |  | 345 | 138 |  | Spring Green substation modifications |  | WI |  |  | Planned | 23100000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 5484 | 2011-07-25 | SUB | 2020-12-31 | Cardinal | Substation |  | 345 | 138 |  | Cardinal substation modifications |  | WI |  |  | Planned | 9700000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3127 | 2011-07-18 | 05 MVPP1 | 4977 | 2011-07-25 | LN | 2020-12-31 | Spring Green | Cardinal | 1 | 345 |  | 2110 | new line |  | WI |  | 28 | Planned | 59900000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3157 | 2010-09-15 | F2386 | 5543 | 2011-08-24 | LN | 2011-06-17 | Red Granite Tap | ACEC Spring Lake Tap | 1 | 69 |  | 69 | Uprate Red Granite Tap to ACEC Spring Lake Tap 69 kV Line |  | WI | 2.5 |  | In Service | 39146 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3157 | 2010-09-15 | F2386 | 5542 | 2011-08-24 | LN | 2011-06-17 | Fountain Valley Tap | Red Granite Tap | 1 | 69 |  | 69 | Uprate Founain Valley Tap to Red Granite Tap 69 kV Line |  | WI | 3.6 |  | In Service | 56182 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3157 | 2010-09-15 | F2386 | 5541 | 2011-08-24 | LN | 2011-06-17 | Fountain Valley | Fountain Valley Tap | 1 | 69 |  | 69 | Uprate Founain Valley to Fountain Valley Tap 69 kV Line |  | WI | 9.2 |  | In Service | 143900 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3157 | 2010-09-15 | F2386 | 5545 | 2011-08-24 | LN | 2011-06-17 | Silver Lake Tap | Wautoma | 1 | 69 |  | 69 | Uprate Silver Lake Tap to Wautoma 69 kV Line |  | WI | 3.6 |  | In Service | 56183 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3157 | 2010-09-15 | F2386 | 5544 | 2011-08-24 | LN | 2011-06-17 | ACEC Spring Lake Tap | Silver Lake Tap | 1 | 69 |  | 69 | Uprate ACEC Spring Lake Tap to Silver Lake Tap 69 kV Line |  | WI | 4.3 |  | In Service | 67057 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3160 | 2010-09-15 | F3180 | 5550 | 2011-03-18 | LN | 2011-12-31 | Staff | Hamilton | 1 | 138 |  | 258 | Uprate Staff to Hamilton 138 kV Line for G706/H012 |  | WI | 12.7 |  | Planned | 471114 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3160 | 2010-09-15 | F3180 | 5551 | 2011-03-18 | LN | 2011-12-31 | Staff | Friesland | 1 | 138 |  | 348 | Uprate Staff to Friesland 138 kV Line |  | WI | 6 |  | Planned | 222733 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3160 | 2010-09-15 | F3180 | 5552 | 2011-03-18 | LN | 2011-12-31 | Friesland | North Randolph | 1 | 138 |  | 293 | Uprate Friesland to North Randolph 138 kV Line for G706/H012 |  | WI | 1.4 |  | Planned | 347573 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3160 | 2010-09-15 | F3180 | 5553 | 2011-03-18 | LN | 2011-12-31 | Hamilton | Portage | 1 | 138 |  | 293 | Uprate Hamilton to Portage 138 kV Line for G706/H012 |  | WI | 1.1 |  | Planned | 406259 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3161 | 2010-09-15 | F3094 | 5556 | 2010-09-15 | LN | 2012-11-30 | EcoMont | Rewey Tap | 1 | 69 |  | 78 | New EcoMont substation is tapped into Belmont Tap-Rewey Tap 69 kV Line & remote end terminal work for G749 |  | WI | 6.7 |  | Planned | 572112 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3161 | 2010-09-15 | F3094 | 5555 | 2010-09-15 | LN | 2012-11-30 | Belmont Tap | EcoMont | 1 | 69 |  | 78 | New EcoMont substation is tapped into Belmont Tap-Rewey Tap 69 kV Line & remote end terminal work for G749 |  | WI | 3.6 |  | Planned | 307404 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3161 | 2010-09-15 | F3094 | 5554 | 2010-09-15 | SUB | 2012-11-30 | EcoMont | Substation |  | 69 |  |  | New EcoMont substation G749 |  | WI |  |  | Planned | 3689667 | eng |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3188 | 2010-10-21 | F3056 | 5629 | 2011-03-18 | LN | 2011-03-25 | Pleasant Prairie | Zion | 1 | 345 |  | 1334 | Replace 345kV Wave trap and jumpers at the ComEd Zion SS |  | WI/IL |  |  | In Service | 1544571 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5970 | 2011-04-29 | LN | 2018-06-01 | Branch River | Point Beach | 1 | 345 |  | 883 | Loop the Point Beach-Forest Juction into the Branch River SS |  | WI |  |  | Planned | 5314000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5971 | 2011-04-29 | LN | 2018-06-01 | Branch River | Forest Jct | 1 | 345 |  | 883 | Loop the Point Beach-Forest Juction into the Branch River SS |  | WI |  |  | Planned | 2566000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5969 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Holland | 1 | 138 |  | 283 | Terminate the not-converted Holland 138 kV line at Barnhart 138 kV |  | WI |  |  | Planned | 142000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5968 | 2011-04-29 | LN | 2018-06-01 | Branch River | Forest Jct | 2 | 345 |  | 883 | Convert the existing Forest Junction-Howards Grove-Plymouth #4 138 kV line and the Branch Riverern portion of the existing Plymouth #4-Holland 138 kV line to 345 kV and loop into the Barnhart and Branch River substations |  | WI |  | 12.88 | Planned | 9397000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5966 | 2011-04-29 | LN | 2018-06-01 | Howards Grove | Erdman | 1 | 138 |  | 348 | Construct a new 138 kV line from Howards Grove to Erdman |  | WI |  | 6.6 | Planned | 11824000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5959 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Cedarsauk | 1 | 345 |  | 960 | Loop Edgewater-Cedarsauk into the new Barnhart SS and uprate the Barnhart to Cedarsauk secton to 960 MVA |  | WI |  |  | Planned | 5322000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5967 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Branch River | 1 | 345 |  | 1096 | Convert the existing Forest Junction-Howards Grove-Plymouth #4 138 kV line and the Branch River portion of the existing Plymouth #4-Holland 138 kV line to 345 kV and loop into the Barnhart and Branch River substations |  | WI |  | 35.5 | Planned | 20057000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5958 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Edgewater | 1 | 345 |  | 653 | Loop Edgewater-Cedarsauk into the new Barnhart SS |  | WI |  |  | Planned | 1299000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5957 | 2011-04-29 | LN | 2018-06-01 | Barnhart | South Fond du Lac | 1 | 345 |  | 1198 | Loop Edgewater-South Fond du Lac into the new Barnhart SS |  | WI |  |  | Planned | 9928000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5964 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Plymouth #4 | 1 | 138 |  | 348 | Construct a new 138 kV line from Barnhart to Plymouth #4 |  | WI |  | 5.87 | Planned | 8529000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5963 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Mullet River 138 kV | 1 | 138 |  | 488 | Loop the South Sheboygan Falls-Mullet River 138 kV line into Barnhart SS |  | WI |  |  | Planned | 6843000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5978 | 2011-04-29 | SUB | 2018-06-01 | Barnhart | Substation | 1 | 345 |  | 500 | New 345 kV Substation, including bus work and new 345/138 kV transformer |  | WI |  |  | Planned | 42475500 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5955 | 2011-04-29 | SUB | 2018-06-01 | Branch River | substation |  | 345 |  |  | Construct a new Branch River substation |  | WI |  |  | Planned | 25921500 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5962 | 2011-04-29 | LN | 2018-06-01 | Barnhart | South Sheboygan Falls | 1 | 138 |  | 293 | Loop the South Sheboygan Falls-Mullet River 138 kV line into Barnhart SS |  | WI |  |  | Planned | 3839000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5960 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Sheboygan Energy Center | 1 | 345 |  | 1096 | Loop Sheboygan Energy Center-Granville into the new Barnhart SS |  | WI |  |  | Planned | 3272000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5965 | 2011-04-29 | LN | 2018-06-01 | Plymouth #4 | Howards Grove | 1 | 138 |  | 348 | Construct a new 138 kV line from Plymouth #4 to Howards Grove |  | WI |  | 3.13 | Planned | 2938000 | eng |  |  |  |  | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5973 | 2011-04-29 | LN | 2018-06-01 | Branch River | Sheboygan Energy Center | 1 | 345 |  | 1096 | Loop the Point Beach-Sheboygan Energy Center 345 kV line into the Branch River SS |  | WI |  | 1 | Planned | 2861000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5961 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Granville | 1 | 345 |  | 1096 | Loop Sheboygan Energy Center-Granville into the new Barnhart SS |  | WI |  |  | Planned | 2294000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5956 | 2011-04-29 | LN | 2018-06-01 | Barnhart | Edgewater | 2 | 345 |  | 937 | Loop Edgewater-South Fond du Lac into the new Barnhart SS |  | WI |  |  | Planned | 4499000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3206 | 2010-11-04 | F3064, PR04117 | 5972 | 2011-04-29 | LN | 2018-06-01 | Branch River | Point Beach | 1 | 345 |  | 1096 | Loop the Point Beach-Sheboygan Energy Center 345 kV line into the Branch River SS |  | WI |  | 1 | Planned | 3988000 | eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC | 3395 | 2010-10-20 | F2906 | 6270 | 2011-05-02 | Dist | 2015-04-01 | Milwaukee Co |  |  | 138 | 13.2 |  | added distribution substation with 2 line breakers and a bus tie breaker |  | WI |  |  | Planned | 3500000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3395 | 2010-10-20 | F2906 | 6269 | 2011-05-02 | TAP | 2015-04-01 | Parkhill | Milwaukee Co | 1 | 138 |  | 321 | Tap Bluemound-Parkhill line and install 1.9 miles of new 138kV line to the new Milwaukee Co substation |  | WI |  | 1.9 | Planned | 15000000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3395 | 2010-10-20 | F2906 | 6268 | 2011-05-02 | TAP | 2015-04-01 | Bluemound | Milwaukee Co | 1 | 138 |  | 321 | Tap Bluemound-Tosa line and install 2.0 miles of new 138kV line to the new Milwaukee Co substation |  | WI |  | 2 | Planned | 15000000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3427 | 2010-10-20 | PR04090 | 6322 | 2011-03-18 | LNup | 2011-03-07 | Nordic | Perch Lk | 1 | 138 |  | 191 | Increase ground clearance for the Nordic-Perch Lk 138 kV line |  | MI | 29.6 |  | In Service | 1543040 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3428 | 2010-10-20 | PR04181 | 6323 | 2011-06-17 | LNup | 2011-04-08 | Stage Coach | Timberlane | 1 | 69 |  | 80 | Increase ground clearance for the Stage coach-Timberlane 69 kV line |  | WI | 2.4 |  | In Service | 35000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3432 | 2010-10-08 | PR04259 | 6330 | 2011-06-17 | LNup | 2011-04-21 | Stoughton | Stoughton South Tap | 1 | 69 |  | 69 | Uprate the Stoughton-Stoughton South Tap-Oregon 69 kV line Y-127 |  | WI | 8 |  | In Service | 456000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3432 | 2010-10-08 | PR04259 | 6331 | 2011-06-17 | LNup | 2011-04-21 | Stoughton South Tap | Oregon | 1 | 69 |  | 69 | Uprate the Stoughton-Stoughton South Tap-Oregon 69 kV line Y-127 |  | WI | 2 |  | In Service | 114000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3433 | 2010-10-08 |  | 6332 | 2011-08-24 | LNup | 2011-12-31 | Stagecoach | Mt Horeb NE | 1 | 69 |  | 69 | Uprate the Stagecoach-Mt Horeb NE-Mt Horeb 69 kV line Y-128 |  | WI | 0.5 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3433 | 2010-10-08 | PR04260 | 6333 | 2011-03-18 | LNup | 2011-12-31 | Mt Horeb NE | Mt Horeb | 1 | 69 |  | 69 | Uprate the Stagecoach-Mt Horeb NE-Mt Horeb 69 kV line Y-128 |  | WI | 0.8 |  | Planned | 36505 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3447 | 2010-12-02 | PR04350 | 6350 | 2011-03-18 | TEQ | 2010-12-07 | Ontonagon |  | 1 | 138 | 69 | 28 | Retap CT related to Ontonagon 138/69 kV Tr to obtain a higher rating |  | MI |  |  | In Service | 12410 | [5 empty] | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3448 | 2010-12-02 | PR04350 | 6351 | 2011-03-18 | TX | 2011-12-01 | Ontonagon |  | 1 | 138 | 69 | 47 | Replace the Ontonagon 138/69 kv Tr with a larger unit |  | MI |  |  | Planned | 935786 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3449 | 2010-12-03 | PR04376 | 6352 | 2010-12-03 | LNrb | 2013-12-31 | Atlantic | M38 | 1 | 69 |  | 146 | Rebuild the Atlantic-M38 69kV line |  | MI |  |  | Planned | 18878963 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3451 | 2010-12-06 | PR04338 | 6356 | 2010-12-06 | LNup | 2011-11-01 | Mt Horeb | Verona | 1 | 69 |  | 69 | Increase ground clearance on the Mt Horeb-Verona 69kV line |  | WI | 13 |  | Planned | 710000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3452 | 2010-12-06 | PR04340 | 6359 | 2010-12-06 | LNup | 2011-11-01 | RCEC Center | Union Town Line | 1 | 69 |  | 69 | Increase ground clearance on the Bass Ck-Sheepskin 69kV line |  | WI | 4.4 |  | Planned | 182342 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3452 | 2010-12-06 | PR04340 | 6360 | 2010-12-06 | LNup | 2011-11-01 | Union Town Line | Evansville Tap | 1 | 69 |  | 69 | Increase ground clearance on the Bass Ck-Sheepskin 69kV line |  | WI | 1.5 |  | Planned | 62162 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3452 | 2010-12-06 | PR04340 | 6358 | 2010-12-06 | LNup | 2011-11-01 | Footville | RCEC Center | 1 | 69 |  | 69 | Increase ground clearance on the Bass Ck-Sheepskin 69kV line |  | WI | 2.9 |  | Planned | 120180 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3452 | 2010-12-06 | PR04340 | 6357 | 2010-12-06 | LNup | 2011-11-01 | Bass Ck | Footville | 1 | 69 |  | 69 | Increase ground clearance on the Bass Ck-Sheepskin 69kV line |  | WI | 0.4 |  | Planned | 16577 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3452 | 2010-12-06 | PR04340 | 6361 | 2010-12-06 | LNup | 2011-11-01 | Evansville Tap | Sheepskin | 1 | 69 |  | 69 | Increase ground clearance on the Bass Ck-Sheepskin 69kV line |  | WI | 13 |  | Planned | 538739 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3453 | 2010-12-06 | PR04374 | 6362 | 2010-12-06 | LNup | 2012-02-28 | Waupun | Koch Tap | 1 | 69 |  | 59 | Increase ground clearance on the Waupun-S Fond du Lac 69kV line |  | WI | 2.6 |  | Planned | 314102 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3453 | 2010-12-06 | PR04374 | 6363 | 2010-12-06 | LNup | 2012-02-28 | Koch Tap | S Fond du Lac | 1 | 69 |  | 59 | Increase ground clearance on the Waupun-S Fond du Lac 69kV line |  | WI | 15.5 |  | Planned | 1872528 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3457 | 2011-01-04 | PR04372 | 6371 | 2011-08-24 | SUB | 2011-12-30 | Highway 2 | SUB |  | 138 |  |  | GIC-J060 Highway 2 SS tapped in the Indian Lk-Perkins #1 line |  | MI |  |  | Planned | 4779758 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3457 | 2011-01-04 | PR04372 | 6372 | 2011-03-18 | LN | 2011-12-30 | Highway 2 | Garden City Wind | 1 | 138 |  | 211 | GIC-J060 Highway 2 - Garden City Wind SS 138kV line |  | MI |  | 17 | Planned |  | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3457 | 2011-01-04 | PR04372 | 6373 | 2011-03-18 | TX | 2011-12-30 | Garden City Wind | Transformer | 1 | 138 | 34.5 | 30 | GIC-J060 Garden City Wind 138/34.5 kV step up transformer |  | MI |  |  | Planned |  | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3457 | 2011-01-04 | PR04372 | 6374 | 2011-03-18 | TX | 2011-12-30 | Garden City Wind | Transformer | 1 | 34.5 | 0.69 | 35 | GIC-J060 Garden City Wind 34.5/0.69 kV generator step up transformer |  | MI |  |  | Planned |  | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3458 | 2011-01-04 | PRF2015a | 6375 | 2011-06-17 | TX | 2011-06-03 | Aurora | Transformer | 1 | 115 | 69 | 60 | Aurora 115-69kV T3 Replacement |  | WI |  |  | In Service | 2958914 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3459 | 2011-01-04 | PR04423 | 6376 | 2011-06-17 | Lnup | 2011-04-12 | Hume | Wildwood | 1 | 115 |  | 207 | Increase ground clearance on the Hume-Wildwood 115kV line |  | WI | 2.7 |  | In Service | 50000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3460 | 2011-01-04 | PR04420 | 6377 | 2011-03-18 | Lnup | 2011-02-28 | Berlin | Dartford Tap | 1 | 69 |  | 72 | Increase ground clearance on the Y-93 Berlin-Ripon 69kV line |  | WI | 5.7 |  | In Service | 609350 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3460 | 2011-01-04 | PR04420 | 6378 | 2011-03-18 | Lnup | 2011-02-28 | Dartford Tap | NW Ripon | 1 | 69 |  | 72 | Increase ground clearance on the Y-93 Berlin-Ripon 69kV line |  | WI | 5.5 |  | In Service | 587969 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3460 | 2011-01-04 | PR04420 | 6379 | 2011-03-18 | Lnup | 2011-02-28 | NW Ripon | Ripon | 1 | 69 |  | 72 | Increase ground clearance on the Y-93 Berlin-Ripon 69kV line |  | WI | 1.8 |  | In Service | 192426 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3461 | 2011-01-05 | PR04411 | 6380 | 2011-03-18 | Lnup | 2011-02-28 | McMillan | Wildwood | 1 | 115 |  | 138 | Increase ground clearance on the McMillan-Wildwood 115kV line |  | WI | 4.4 |  | In Service | 50000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3488 | 2011-03-22 | PR04502 | 6446 | 2011-03-22 | Line | 2012-03-01 | Brick Church | Walworth | 1 | 69 |  | 84 | Fix clearance on Brick Church-Walworth 69 kV line to bring rating up |  | WI | 2.3 |  | Planned | 532000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3489 | 2011-03-22 | PR04503 | 6448 | 2011-03-22 | Line | 2012-03-01 | Wiota | Gratiot Tap | 1 | 69 |  | 66 | Fix clearance on Wiota-Gratiot Tap 69 kV line to bring rating up |  | WI | 3.8 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3489 | 2011-03-22 | PR04503 | 6447 | 2011-03-22 | Line | 2012-03-01 | Jennings Road | Wiota | 1 | 69 |  | 60 | Fix clearance on Jennings Road-Wiota 69 kV line to bring rating up |  | WI | 1.5 |  | Planned | 314000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3489 | 2011-03-22 | PR04503 | 6449 | 2011-03-22 | Line | 2012-03-01 | Gratiot Tap | Darlington | 1 | 69 |  | 64 | Fix clearance on Gratiot Tap-Darlington 69 kV line to bring rating up |  | WI | 8.9 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | ATC LLC | 3504 | 2011-03-28 | PR04529 | 6464 | 2011-03-28 | Line | 2012-12-01 | Omro | Winneconne | 1 | 69 |  | 64 | Rerate Line Y-80 conductor from Omro sub to Winneconne sub to a rating of 580 amps |  | WI | 5 |  | Planned | 205000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATC LLC, ITCM | 3127 | 2011-07-18 | 05 MVPP1 | 5482 | 2011-07-25 | SUB | 2020-12-31 | Dubuque Co | Substation |  | 345 |  |  | Construct the Dubuque Co switching station |  | IA |  |  | Planned | 13400000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC, ITCM | 3127 | 2011-07-18 | 05 MVPP1 | 4976 | 2011-07-25 | LN | 2020-12-31 | Spring Green | Dubuque Co | 1 | 345 |  | 2110 | new line |  | WI |  | 75.13 | Planned | 159300000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC, XEL | 3127 | 2011-07-18 | 05 MVPP1 | 5626 | 2011-07-25 | LN | 2018-12-31 | North LaCrosse | North Madison | 1 | 345 |  | 2110 | Construct a North LaCrosse - North Madison 345-kV line |  | WI |  | 136.331 | Planned | 301800000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATC LLC, XEL | 3127 | 2011-07-18 | 05 MVPP1 | 6573 | 2011-08-25 | SUB | 2018-12-31 | North LaCrosse (Briggs Road) | Substation |  | 345 | 161 | 448 MVA | Terminate North Madison - North LaCrosse 345 kV line into Briggs Road, create 345 kV breaker ring bus, add second 345/161 kV transformer, and 50 MVAR of 34.5 kV reactors on the tertiary |  | WI |  |  | Planned | 17460000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ATCLLC | 3472 | 2011-02-01 | PR04325 | 6399 | 2011-08-24 | SUB | 2013-03-22 | Pleasant Prairie |  |  | 345 |  |  | Construct a new 6 ring breaker and a half 345 kV bus at the P4 site adjacent to the existing P4 yard. |  | WI |  |  | Planned | 39400000 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATCLLC | 3479 | 2011-02-15 | PR04452 | 6428 | 2011-02-15 | Line | 2012-03-01 | Progress | Aviation | 1 | 138 |  | 230 MVA | Increase ground clearance for the Progress-Aviation line to 187 degrees F |  | WI | 1.85 |  | Planned | 492563 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ATCLLC | 3480 | 2011-02-15 | PR04040 | 6429 | 2011-02-15 | Line | 2012-10-01 | Engadine Tap | Engadine | 1 | 138 |  | 57 MVA | Construct a new radial 69-kV tap from the existing Indian Lake-Hiawatha 69-kV line 6913 to the Engadine Substation |  | WI |  | 0.15 | Planned | 810804 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | DPC | 3397 | 2010-09-15 | DPC | 6272 | 2011-03-24 | LNrb | 2014-06-01 | Genoa | La Crosse Tap | 1 | 161 |  | 400 | Rebuild line |  | WI | 20.9 |  | Planned | 18000000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | DPC | 3434 | 2010-11-10 | DPC | 6337 | 2010-11-10 | SUB | 2012-09-01 | Alma | Elk Mound |  | 161 |  |  | New Substation |  | WI |  |  | Planned | 2164000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 2649 | 2011-09-01 | TX | 2013-06-17 | Cedar Mountain | Transformer | 1 | 345 | 115 | 448 | new transformer | H6 | MN |  |  | Planned | 19300000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1885 | 2011-09-01 | LN | 2013-08-15 | Cedar Mountain | Helena | 2 | 345 |  | 2066 | new line |  | MN |  | 62.2 | Planned | 0 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1884 | 2011-09-01 | LN | 2013-08-15 | Cedar Mountain | Helena | 1 | 345 |  | 2066 | new line |  | MN |  | 62.2 | Planned | 141700000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1893 | 2011-09-01 | TX | 2013-10-09 | Lyon County | Transformer | 1 | 345 | 115 | 448 | new transformer | G6 | MN |  |  | Planned | 20700000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1883 | 2011-09-01 | LN | 2013-11-05 | Lyon County | Cedar Mountain | 2 | 345 |  | 2066 | new line |  | MN |  | 51.9 | Planned | 0 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1882 | 2011-09-01 | LN | 2013-11-05 | Lyon County | Cedar Mountain | 1 | 345 |  | 2066 | new line |  | MN |  | 51.9 | Planned | 111500000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 5624 | 2011-09-01 | LN | 2014-02-10 | Cedar Mountain | Franklin | 1 | 115 |  | 336 | new line |  | MN |  | 5 | Planned | 22600000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1894 | 2011-09-01 | TX | 2014-03-31 | Lake Marion | Transformer | 1 | 345 | 115 | 448 | new transformer | H6 | MN |  |  | Planned | 25900000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1886 | 2011-09-01 | LN | 2014-04-29 | Helena | Lake Marion | 1 | 345 |  | 2066 | new line |  | MN |  | 26.6 | Planned | 87800000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1887 | 2011-09-01 | LN | 2014-06-16 | Lake Marion | Hampton Corner | 1 | 345 |  | 2066 | new line |  | MN |  | 18.5 | Planned | 55600000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1881 | 2011-09-01 | LN | 2015-01-12 | Brookings County | Lyon County 345 kV | 1 | 345 |  | 2066 | new line |  | SD/MN |  | 48.1 | Planned | 134700000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1895 | 2011-09-01 | TX | 2015-01-22 | Hazel | Transformer | 1 | 345 | 230 | 336 | new transformer | G5 | MN |  |  | Planned | 25700000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1888 | 2011-09-01 | LN | 2015-02-02 | Lyon County | Hazel | 1 | 345 |  | 2066 | new line |  | MN |  | 23.5 | Planned | 59000000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 1203 | 2011-07-18 | 02 MVPP1 | 1889 | 2011-09-01 | LN | 2015-02-16 | Hazel Creek | Minnesota Valley | 1 | 230 |  | 1558 | new line |  | MN |  | 6 | Planned | 20500000 | Engineering |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE | 2571 | 2010-09-15 | 20222 | 4582 | 2011-03-28 | LN | 2014-11-15 | MN Pipeline | Menahga | 1 | 115 |  | 42 | MN Pipeline-Menahga 115 kV line operated at 34.5 kV, Menahga 2-way switch |  | MN |  | 8 | Planned | 4199990 | Engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | GRE | 2599 | 2010-09-15 | 20338 | 4610 | 2011-01-14 | LN | 2014-10-31 | Shell Lake | Shell Lake Tap | 1 | 115 |  |  | New Distribution |  | MN |  | 5 | Planned | 4201000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | GRE | 2634 | 2010-09-15 | 20388 | 6292 | 2011-07-01 | LN | 2012-11-02 | Savanna | Cedar Valley | 1 | 115 |  | 310 | Cedar Valley conversion to 115 kV from 69 kV |  | MN | 8 |  | Planned | 3900225 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | GRE | 2634 | 2010-09-15 | 20388 | 4645 | 2011-07-01 | LN | 2014-11-28 | Savanna | Cromwell | 1 | 115 |  | 310 | New 115 kV Cromwell-Floodwood Line |  | MN | 29 |  | Planned | 22000000 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | GRE | 2643 | 2010-09-15 | 20401 | 4659 | 2011-01-14 | LN | 2013-05-01 | Parkers Prairie | Parkers Prairie Tap | 1 | 115 |  | 141.6 | Parkers Prairie Conversion from 41.6 to 115 kV |  | MN |  | 2 | Planned | 1220998 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | GRE | 2679 | 2010-09-15 | 200331 | 4696 | 2011-01-14 | LN | 2019-11-01 | Ramsey | Grand Forks | 1 | 230 |  |  | 230 kV rebuild |  | MN | 81.02 |  | Planned | 40500000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | GRE | 3454 | 2010-12-06 | 200360 | 6267 | 2011-07-01 | SUB | 2013-05-01 | Medina | 115 kV breaker station |  | 115 |  | 0 | Convert WHCEA’s Median 69 kV distribution substation to 115 kV. Retire the 69 kV portion of the Medina 115/69 kV substation, reconfigure Medina to a straight bus breaker station and re-terminate the existing 115kV lines and the new Median – Pomerleau Lake 115 kV line at the Medina breaker station. Medina is recommended to have additional positions for future 115 kV line terminations. |  | MN | 0 | 0 | Planned | 1386164 | Planning |  |  | N |  | Y | C>B>A
A in MTEP11 | West | GRE | 3467 | 2011-01-11 | 200608 | 6394 | 2011-07-01 | LN | 2011-07-01 | Oak Glen Wind | Riverpoint | 1 | 69 |  |  | SW-RB rebuild to double circuit line |  | MN | 4 | 0 | Under Construction | 1722464 | Eng |  |  |  |  | Y | B>A
A in MTEP11 | West | GRE | 3468 | 2011-01-11 | 200698 | 6395 | 2011-07-01 | SUB | 2011-09-01 | Claybank | Substation | 1 | 69 |  |  | Claybank breaker station |  | MN | 0 | 0 | Under Construction | 1312741 | Eng |  |  |  |  | Y | B>A
A in MTEP11 | West | GRE | 3469 | 2011-01-11 | 200784 | 6396 | 2011-07-01 | LN | 2011-10-01 | H061 | Tap Switch | 1 | 69 |  |  | H061 switch on the Vasa Tap line |  | MN | 0 | 0 | Planned | 192530 | Eng |  |  |  |  | Y | B>A
A in MTEP11 | West | GRE, XEL | 1203 | 2011-07-18 | 02 MVPP1 | 1898 | 2011-07-18 | TX | 2011-06-01 | Morris | Transformer | 2 | 230 | 115 | 150 | Upgrade 100 MVA to 150 MVA | G5 | MN |  |  | Planned | 4000000 | Planning |  | Y | Y | Y | Y | B>A
A in MTEP11 | West | GRE, XEL | 1203 | 2011-07-18 | 02 MVPP1 | 1899 | 2011-07-18 | TX | 2011-06-01 | Willmar | Transformer | 2 | 115 | 69 | 112 |  | G5 | MN |  |  | Planned | 3000000 |  |  | Y | Y | Y | NT | B>A
A in MTEP11 | West | ITCM | 3191 | 2010-06-28 | G164 | 5635 | 2011-07-01 | SUB | 2011-04-29 | Lakefield Jct | Substation | 1 | 345 |  |  | Convert the Lakefield 345kV ring bus to breaker and a half. |  | MN |  |  | In Service | 8148000 | Engineering |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3192 | 2010-06-28 | G604 | 5636 | 2011-02-15 | SUB | 2010-08-15 | Ellendale | Breaker Station | 1 | 69 |  | 143 MVA | Construct a new Ellendale 69kV four terminal breaker station near the existing River Point Tap. |  | MN |  |  | In Service | 1854906 | Engineering |  |  |  |  | Y | B>A
A in MTEP11 | West | ITCM | 3192 | 2010-06-28 | G604 | 5638 | 2011-02-15 | LN | 2011-12-31 | Ellendale | County Line | 1 | 69 |  | 77 MVA | Change the N.O. switch to normally closed after breaker station is operational. |  | MN |  |  | Under Construction | 58800 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3192 | 2010-06-28 | G604 | 5637 | 2011-02-15 | LN | 2011-12-31 | Ellendale | G604 customer sub | 1 | 69 |  | 77 MVA | Construct a new Ellendale-G604 customer 69kV tap. |  | MN |  | 3.5 | Under Construction | 0 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3193 | 2010-06-28 | G741 | 5639 | 2011-02-15 | LN | 2010-10-01 | Trimont | G741 Tap | 1 | 69 |  |  | Tap Trimont(IPL)-Sherburn(SCREC) 69kV line for the new tap to G741 customer. |  | MN |  |  | In Service | 10000 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3193 | 2010-06-28 | G741 | 5640 | 2011-02-15 | LN | 2010-10-01 | Sherburn(SCREC) | G741 Tap | 1 | 69 |  |  | Tap Trimont(IPL)-Sherburn(SCREC) 69kV line for the new tap to G741 customer. |  | MN |  |  | In Service | 10000 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3193 | 2010-06-28 | G741 | 5641 | 2011-02-15 | LN | 2010-10-01 | G741 Tap | G741 Customer Sub | 1 | 69 |  |  | Radial tap from G741 Tap-G741Customer sub |  | MN |  | 2.5 | In Service | 197884 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3193 | 2010-06-28 | G741 | 5642 | 2011-02-15 | SUB | 2010-10-01 | Fox Lake | Relay Upgrade | 1 | 69 |  |  | Adjust relays at Fox Lake 69kV breaker730. |  | MN |  | 2.5 | In Service | 6000 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3194 | 2010-06-28 | G798 | 5643 | 2011-02-15 | SUB | 2010-07-31 | Story County | Breaker Station | 1 | 161 |  | 558 MVA | Expand the 161kV ring bus at Story County. |  | IA |  |  | In Service | 422664 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3195 | 2010-06-28 | G870 | 5647 | 2011-02-15 | LN | 2010-10-01 | Freeborn | G870 Wind Sub | 1 | 161 |  |  | Radial tap from Freeborn-G870 |  | MN |  | 4 | In Service | 0 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3195 | 2010-06-28 | G870 | 5644 | 2011-02-15 | SUB | 2010-10-01 | Freeborn | Breaker Station | 1 | 161 |  | 558 MVA | Construct a new Freeborn 161kV three terminal breaker station. |  | MN |  |  | In Service | 3076795 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3195 | 2010-06-28 | G870 | 5646 | 2011-02-15 | LN | 2010-10-01 | Freeborn | Winnebago | 1 | 161 |  |  | Tap Hayward-Winnebago Jct 161kV line for the new Freeborn Breaker Station. |  | MN |  |  | In Service | 139368 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3195 | 2010-06-28 | G870 | 5645 | 2011-02-15 | LN | 2010-10-01 | Freeborn | Hayward | 1 | 161 |  |  | Tap Hayward-Winnebago Jct 161kV line for the new Freeborn Breaker Station. |  | MN |  |  | In Service | 300000 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3196 | 2010-06-28 | H007 | 5648 | 2011-07-01 | SUB | 2011-07-01 | Bond | Breaker Station | 1 | 69 |  | 143 MVA | Construct a new Bond 69kV four terminal breaker station near the existing Greely T. |  | IA |  |  | In Service | 1897882 | Engineering |  |  |  |  | Y | B>A
A in MTEP11 | West | ITCM | 3196 | 2010-06-28 | H007 | 5649 | 2011-07-01 | LN | 2011-07-01 | Bond | Backbone Tap | 1 | 69 |  | 69 MVA | Construct 2 miles of 69kV double circuit. |  | IA |  |  | In Service | 831141 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3196 | 2010-06-28 | H007 | 5650 | 2011-07-01 | LN | 2011-07-01 | Bond | Manchester REC Tap | 1 | 69 |  | 69 MVA | Construct 2 miles of 69kV double circuit. |  | IA |  |  | In Service | 831140 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6526 | 2011-09-01 | LN | 2015-12-31 | Rutland | Winnebago | 1 | 161 |  | 446 MVA | Construct 345-161kV double circuit |  | MN | 15.24 |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6535 | 2011-09-01 | LN | 2015-12-31 | Winnebago | Fairbault Co | 1 | 161 |  | 446 MVA | Construct 345-161kV double circuit |  | IA | 15.13 |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6534 | 2011-09-01 | LN | 2015-12-31 | Winnco | Fairbault Co | 1 | 161 |  | 446 MVA | Construct 345-161kV double circuit |  | MN/IA | 22 |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6533 | 2011-09-01 | LN | 2015-12-31 | Winnco West | Burt | 1 | 345 |  | 1800 MVA | Construct 345kV circuit |  | IA |  | 19 | Planned | 41225660 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6532 | 2011-09-01 | LN | 2015-12-31 | Winnebago | Winnco West | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | MN/IA |  |  | Planned | 1105632 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6531 | 2011-09-01 | LN | 2015-12-31 | Winnebago | Winnco West | 1 | 345 |  | 1800 MVA | Construct 345-161kV double circuit |  | MN/IA |  | 22 | Planned | 47734975 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6530 | 2011-09-01 | SUB | 2015-12-31 | Winnco West | substation | 1 | 345 |  | 1800 MVA | Construct a new Winnco West 3-terminal 345kV switch station. |  | IA |  |  | Planned | 10980000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6529 | 2011-09-01 | SUB | 2015-12-31 | Lakefield | Substation |  | 345 |  | 1800 MVA | Add a 345kV terminal at Lakefield including 2 new 345kv bkrs |  | IA |  |  | Planned | 5000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6527 | 2011-09-01 | LN | 2015-12-31 | Fox Lake | Rutland | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | MN |  |  | Planned | 804097 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6525 | 2011-09-01 | LN | 2015-12-31 | Fox Lake | Rutland | 1 | 161 |  | 446 MVA | Construct 345-161kV double circuit |  | MN | 16.5 |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6524 | 2011-09-01 | LN | 2015-12-31 | Lakefield | Fox Lake | 1 | 161 |  | 446 MVA | Construct 345-161kV double circuit |  | MN | 23 |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6523 | 2011-09-01 | LN | 2015-12-31 | Lakefield | Fox Lake | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | MN |  |  | Planned | 1155888 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6521 | 2011-09-01 | TX | 2015-12-31 | Winnebago | transformer |  | 345 | 161 | 450 MVA | Add a 345/161kV TRF |  | IA |  |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6520 | 2011-09-01 | SUB | 2015-12-31 | Winnebago | Substation |  | 345 | 161 | 1800 MVA | Construt a new sub with a 345kV ring bus with 2 line terminals and one 345/161kV TRF |  | IA |  |  | Planned | 27360000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6528 | 2011-09-01 | LN | 2015-12-31 | Rutland | Winnebago | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | MN |  |  | Planned | 804097 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3205 | 2011-07-18 | 03 MVPP1 | 6522 | 2011-09-01 | LN | 2015-12-31 | Lakefield | Winnebago | 1 | 345 |  | 1800 MVA | Construct 345-161kV double circuit |  | MN |  | 55 | Planned | 119337438 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6547 | 2011-09-01 | LN | 2015-12-31 | Lime Creek | Emery | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | IA |  |  | Planned | 804096 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6545 | 2011-09-01 | LN | 2015-12-31 | Lime Creek | Emery | 1 | 345 |  | 1800 MVA | Construct 345-161kV double circuit |  | IA |  | 16 | Planned | 34716345 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6544 | 2011-09-01 | TX | 2015-12-31 | Emery | transformer |  | 345 | 161 | 450 MVA | Add a 345/161kV TRF |  | IA |  |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6543 | 2011-09-01 | SUB | 2015-12-31 | Emery | Substation |  | 345 | 161 | 1800 MVA | Construt a new sub with a 345kV ring bus with 2 line terminals and one 345/161kV TRF |  | IA |  |  | Planned | 19380000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6541 | 2011-09-01 | SUB | 2015-12-31 | Lime Creek | Substation |  | 345 | 161 | 1800 MVA | Construt a new sub with a 345kV ring bus with 2 line terminals and one 345/161kV TRF |  | IA |  |  | Planned | 18930000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6546 | 2011-09-01 | LN | 2015-12-31 | Lime Creek | Emery | 1 | 161 |  | 335 MVA | Construct 345-161kV double circuit |  | IA |  | 16 | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6542 | 2011-09-01 | TX | 2015-12-31 | Lime Creek | transformer |  | 345 | 161 | 450 MVA | Add a 345/161kV TRF |  | IA |  |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6553 | 2011-09-01 | SUB | 2015-12-31 | Hazleton | Substation |  | 345 | 161 | 1800 MVA | Convert the 345kV ring bus to a breaker and half and add a 345kV line terminal. |  | IA |  |  | Planned | 14200000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6552 | 2011-07-25 | LN | 2015-12-31 | Blackhawk | Hazleton | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | IA |  |  | Planned | 603072 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6537 | 2011-09-01 | LN | 2015-12-31 | Lime Creek | Worth County | 1 | 161 |  | 200 MVA | Construct 345-161kV double circuit |  | IA |  | 7 | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6536 | 2011-09-01 | LN | 2015-12-31 | Winnco West | Lime Creek | 1 | 345 |  | 1800 MVA | Construct 345-161kV double circuit |  | IA |  | 61 | Planned | 132356067 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6538 | 2011-09-01 | LN | 2015-12-31 | Winnco West | Winnco | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | IA |  |  | Planned | 804096 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6539 | 2011-09-01 | LN | 2015-12-31 | Worth County | Lime Creek tap | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | IA |  |  | Planned | 251280 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3213 | 2011-07-18 | 04 MVPP1 | 6540 | 2011-09-01 | LN | 2015-12-31 | Lime Creek tap | Lime Creek | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | IA |  |  | Planned | 226152 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM | 3406 | 2010-09-15 | Adams-Roch | 6293 | 2011-07-01 | TEQ | 2011-04-29 | Adams | Rochester | 1 | 161 |  | 501 MVA | Upgrades terminal equipment |  | MN |  |  | In Service | 360000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3407 | 2010-09-15 | Bluff | 6294 | 2010-09-15 | SUB | 2011-12-31 | Bluff | Substation | 1 | 69 |  |  | Expand the Bluff sub |  | IA |  |  | Planned | 1920000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3408 | 2010-09-15 | Boone Quartz | 6295 | 2010-09-15 | SUB | 2011-12-31 | Boone Quartz | Substation | 1 | 69 |  |  | Construct the 69/dist sub |  | IA |  |  | Planned | 1700000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3409 | 2010-09-15 | Bricelyn-Walters | 6296 | 2011-07-01 | Lnrb | 2013-12-31 | Bricelyn | Walters | 1 | 69 |  |  | Rebuild 5 miles to T2-477 |  | IA | 5.03 |  | Planned | 2625000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3410 | 2010-09-15 | Bridgeport TEQ | 6297 | 2010-09-15 | TEQ | 2011-12-31 | Bridgeport | Ottumwa | 1 | 161 |  |  | Upgrades terminal equipment |  | IA |  |  | Planned | 200000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3411 | 2010-09-15 | Bridgeport T8 | 6298 | 2010-09-15 | SUB | 2011-12-31 | Bridgeport | Substation | 1 | 69 |  |  | Add new T8 69/dist TRF |  | IA |  |  | Planned | 360000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3412 | 2010-09-15 | FTMadison | 6299 | 2011-07-01 | SUB | 2012-12-31 | Fort Madison | Substation | 1 | 69 |  |  | Add new 69/dist TRF |  | IA |  |  | Planned | 360000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3413 | 2010-09-15 | Gladbrook | 6300 | 2011-07-01 | LN | 2013-12-31 | Gladbrook | Gladbrook Tap | 1 | 161 | 161 |  | Add new 69/dist TRF |  | IA |  |  | Planned | 300000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3413 | 2010-09-15 | Gladbrook | 6301 | 2011-07-01 | LN | 2013-12-31 | Marshalltown | Gladbrook Tap | 1 | 161 | 161 |  | Add new 69/dist TRF |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3413 | 2010-09-15 | Gladbrook | 6302 | 2011-07-01 | LN | 2013-12-31 | Traer | Gladbrook Tap | 1 | 161 | 161 |  | Add new 69/dist TRF |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3414 | 2010-09-15 | Magnolia Cap | 6303 | 2011-07-01 | CAP | 2012-12-31 | Magnolia | capacitor | 1 | 69 |  |  | Add a 7.1 MVAR cap at Magnolia |  | IA |  |  | Planned | 480000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3415 | 2010-09-15 | Marion TEQ | 6304 | 2011-07-01 | TEQ | 2011-12-31 | Marion | Prairie Creek | 1 | 115 |  | 195 MVA | Upgrades terminal equipment |  | IA |  |  | In Service | 10000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3416 | 2010-09-15 | Marion 0410 | 6305 | 2011-07-01 | LN | 2012-12-31 | Marion | 0410 circuit | 1 | 34 | 34 |  | Rebild to doulbe ckt 69kV |  | IA |  |  | Planned | 10500000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3417 | 2010-09-15 | Marshalltown East Nevada | 6306 | 2011-07-01 | SUB | 2011-12-31 | Marshalltown East Nevada | Substation | 1 | 34 |  |  | Add new 34/dist TRF |  | IA |  |  | In Service | 280000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3418 | 2010-09-15 | Mt Vernon 6420 | 6307 | 2011-07-01 | LN | 2013-12-31 | Mt Vernon 6420 | 6420 circuit | 1 | 34 | 34 |  | Rebild ckt 69kV |  | IA |  |  | Planned | 7150000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3419 | 2010-09-15 | Bertram Sewage | 6308 | 2011-07-01 | LN | 2012-12-31 | Bertram Sewage | Bertram Sewage Tap | 1 | 69 |  |  | Add new 69/dist sub and tap |  | IA |  |  | Planned | 270000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3420 | 2010-09-15 | OGS BKR | 6309 | 2010-09-15 | SUB | 2011-12-31 | Ottumwa Generating Station | Substation | 1 | 345 |  |  | Replace the failed circuit switcher with a new breaker |  | IA |  |  | Planned | 1350000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3421 | 2010-09-15 | S Centervlle Cap | 6310 | 2010-09-15 | CAP | 2011-12-31 | South Centerville | capacitor | 1 | 69 |  |  | Add a 7 MVAR cap at South Centerville |  | IA |  |  | Planned | 1350000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3422 | 2010-09-15 | S Brdwy TEQ | 6311 | 2011-07-01 | TEQ | 2012-12-31 | South Broadway | Substation | 1 | 69 |  | 195 MVA | Upgrades terminal equipment |  | IA |  |  | Planned | 150000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3423 | 2010-09-15 | Truro | 6313 | 2010-09-15 | LN | 2011-12-31 | Truro tap | White Oak REC | 1 | 69 |  |  | Tap White Oak-Medora |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3423 | 2010-09-15 | Truro | 6312 | 2010-09-15 | LN | 2011-12-31 | Truro | Truro tap | 1 | 69 |  | 77 MVA | Add new 69kV tap |  | IA | 10.03 |  | Planned | 3360000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3423 | 2010-09-15 | Truro | 6314 | 2010-09-15 | LN | 2011-12-31 | Truro tap | Medora | 1 | 69 |  |  | Tap White Oak-Medora |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3425 | 2010-09-15 | VMEU | 6318 | 2011-07-01 | LN | 2011-12-31 | VMEU | VMEU tap | 1 | 34 |  |  | Add new switches for tap |  | IA |  |  | In Service | 110000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3426 | 2010-09-15 | DPC/ITC Osage | 6319 | 2011-07-01 | LN | 2013-12-31 | Osage | Osage | 1 | 69 |  |  | Move interconnect point |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | ITCM | 3499 | 2011-03-28 |  | 6459 | 2011-03-28 |  | 2011-12-31 | NERC Alert Facility Ratings for 2011 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | IA |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | ITCM,MEC | 2248 | 2011-09-06 | 07 MVP Portofio | 6585 | 2011-08-25 | Sub | 2017-06-01 | Ottumwa |  | 1 | 345 |  |  | New terminal at Ottumwa for Adair - Ottumwa 345 kV line. Add three 345 kV circuit breakers. |  | IA |  |  | Planned | 3295000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM/MEC | 3213 | 2011-07-18 | 04 MVPP1 | 5991 | 2011-09-01 | LN | 2015-12-31 | Blackhawk | Hazleton | 1 | 345 |  | 1800 MVA | Construct 345-161kV double circuit |  | IA |  | 12 | Planned | 23866416 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM/MEC | 3213 | 2011-07-18 | 04 MVPP1 | 6548 | 2011-09-01 | LN | 2015-12-31 | Emery | Blackhawk | 1 | 345 |  |  | Construct 345-161kV double circuit |  | IA |  | 29 | Planned | 57677172 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM/MEC | 3213 | 2011-07-18 | 04 MVPP1 | 6550 | 2011-09-01 | LN | 2015-12-31 | Emery | Blackhawk | 1 | 161 |  |  | Retire existing 161kV H frame circuit |  | IA |  |  | Planned | 1457424 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM/MEC | 3213 | 2011-07-18 | 04 MVPP1 | 6549 | 2011-09-01 | LN | 2015-12-31 | Emery | Blackhawk | 1 | 161 |  |  | Construct 345-161kV double circuit and transfer existing 161kV conductor |  | IA |  |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM/MEC | 3213 | 2011-07-18 | 04 MVPP1 | 6551 | 2011-09-01 | LN | 2015-12-31 | Blackhawk | Hazleton | 1 | 161 |  | 335 MVA | Construct 345-161kV double circuit |  | IA | 12 |  | Planned | 0 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | ITCM/MEC | 3213 | 2011-07-18 | 04 MVPP1 | 6557 | 2011-09-01 | LN | 2015-12-31 | Blackhawk | Emery | 1 | 345 |  |  | 345/161 kV double circuit line via Franklin |  | IA | 63 |  | Planned | 124122070 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MDU | 3199 | 2010-07-12 | G359 | 5657 | 2011-03-30 | TX | 2011-03-21 | Ellendale | Transformer | 1 | 230 | 115 | 150 | new transformer, replace existing |  | ND |  |  | Under Construction | 2000000 | Engineering | Generator |  |  |  | Y | B>A
A in MTEP11 | West | MDU | 3199 | 2010-07-12 | G359 | 5656 | 2010-07-12 | LN | 2011-12-01 | Ellendale | G359 POI | 1 | 230 |  | 380 | new line |  | ND |  | 24 | Planned | 12400000 | Engineering | Generator |  |  |  | Y | B>A
A in MTEP11 | West | MDU | 3199 | 2010-07-12 | G359 | 5658 | 2010-07-12 | TEQ | 2011-12-01 | Ellendale | Wavetrap on line to Oaks |  | 230 |  |  | new wave trap |  | ND |  |  | Planned | 75000 | Engineering | Generator |  |  |  | Y | B>A
A in MTEP11 | West | MDU | 3199 | 2010-07-12 | G359 | 6407 | 2011-01-28 | SUB | 2011-12-01 | Merricourt | New Generator Interconnection Substation |  | 230 |  |  | New Generator Interconnection Substation |  | ND |  |  | Planned | 4655000 | Engineering |  |  |  |  | Y | B>A
A in MTEP11 | West | MEC | 2248 | 2011-09-06 | 07 MVPP1 | 6565 | 2011-07-25 | LN | 2017-06-01 | Ottumwa | Iowa boarder | 1 | 345 | 161 |  | 345/161 double circuit line |  | IA | 16.6 |  | Planned | 32163860 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3022 | 2011-09-06 | 16 MVP Port.1 | 6586 | 2011-08-25 | Sub | 2014-12-01 | Oak Grove |  | 1 | 345 |  |  | New 345 kV terminal at Oak Grove for Oak Grove - Galesburg-Fargo 345 kV line |  | IL |  |  | Planned | 2337000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3022 | 2011-09-06 | 16. MVP Underbuild | 6564 | 2011-08-25 | LNrc | 2016-12-01 | Sub 56 | Sub 85 |  | 161 |  | 410 | Reconductor Sub 56-Sub 85 161 kV line with T2- 556.5 ACSR conductor |  | IA | 7.5 |  | Planned | 2200000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3022 | 2011-09-06 | 16 MVPP1 | 6562 | 2011-07-25 | TEQ | 2018-06-01 | Oak Grove | 345 kV terminal |  | 345 |  |  | add 345 kV terminal for Galesburg line |  | IA |  |  | Planned | 2336952 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3022 | 2011-09-06 | 16 MVPP1 | 5989 | 2011-07-25 | LN | 2019-06-01 | Oak Grove | Galesburg | 1 | 345 |  |  | new 345/161 kV double circuit line |  | IA | 32 |  | Planned | 64846017 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3205 | 2011-07-18 | 03 MVP Port.1 | 5990 | 2011-08-25 | SwSt | 2016-12-01 | Sheldon |  |  | 345 |  |  | New Sheldon three-way 345 kV Switching Station |  | IA |  |  | Planned | 10450000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3205 | 2011-07-18 | 03 MVP Port.1 | 5951 | 2011-08-25 | LN | 2016-12-01 | Sheldon | Webster |  | 345 |  | 1739 | Sheldon to Webster 345/161 kV double ckt line - Candidate MVP Portfolio #1. Includes rebuild of non-MISO 161 kV circuit from Wisdom to Webster. |  | IA |  | 122 | Planned | 231261000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3205 | 2011-07-18 | 03 MVP Port.1 | 6561 | 2011-08-25 | Sub | 2016-12-01 | Burt |  |  | 345 |  |  | New three-way 345 kV Switching Station near Burt Substation |  | IA |  |  | Planned | 10450000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3205 | 2011-07-18 | 03 MVP Port.1 | 6560 | 2011-08-25 | Sub | 2016-12-01 | Webster |  |  | 345 |  |  | New terminal at Webster for Sheldon - Webster 345 kV line |  | IA |  |  | Planned | 6401000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | 04 MVP Port.1 0011-01 | 5992 | 2011-08-25 | SUB | 2015-12-01 | Black Hawk | Black Hawk |  | 345 | 161 | 560 | Black Hawk 345-161 kV substation with line terminals to Emery and Hazleton |  | IA |  |  | Planned | 15019000 | Planning 2011$ |  |  | Y | Y | Y
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | MEC C-51 | 6424 | 2011-08-25 | LNup | 2015-12-01 | Franklin | Butler | 1 | 161 |  | 410 | Rebuild Franklin-Butler 161 kV line. |  | IA | 26.24 |  | Planned |  | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | 04 MVP Port.1 0011-01 | 6587 | 2011-08-25 | LN | 2015-12-01 | Black Hawk | Emery |  | 345 |  | 1739 | Blackhawk - Emery 345/161 kV double circuit line via Franklin. Includes rebuild of non-MISO 161 kV circuit from Franklin to Emery. |  | IA |  | 88 | Planned | 124122000 | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | MEC C-51 | 6427 | 2011-08-25 | LNup | 2015-12-01 | Black Hawk | Hazleton | 1 | 161 |  | 410 | Rebuild Black Hawk-Hazleton 161 kV line. |  | IA | 24 |  | Planned |  | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | MEC C-51 | 6426 | 2011-08-25 | LNup | 2015-12-01 | Union Tap | Black Hawk | 1 | 161 |  | 410 | Rebuild Union Tap-Black Hawk 161 kV line. |  | IA | 7.9 |  | Planned |  | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | MEC C-51 | 6425 | 2011-08-25 | LNup | 2015-12-01 | Butler | Union Tap | 1 | 161 |  | 410 | Rebuild Butler-Union Tap 161 kV line. |  | IA | 15.93 |  | Planned |  | Planning 2011$ |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3213 | 2011-07-18 | 04 MVPP1 | 6556 | 2011-07-25 | TX | 2015-12-31 | Blackhawk | 345-161 kV transformer |  | 345 | 161 |  | add 345-161 kV transformer & 2 line terminals |  | IA |  |  | Planned | 15019305 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MEC | 3268 | 2011-02-15 | G1393 | 6091 | 2010-09-07 | IND | 2012-11-01 | Lehigh | Reactor |  | 345 |  | 50 | Lehigh: 345 kV 50 MVAr Reactor |  | IA |  |  | Planned | 2750000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | West | MEC | 3270 | 2011-02-15 | G1375 | 6093 | 2010-09-07 | LNrb | 2011-06-01 | Council Bluffs | River Bend |  | 161 |  | 410 | CBEC-River Bend 161 kV Rebuild |  | IA | 0.5 |  | Planned | 675000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | West | MEC | 3271 | 2011-02-15 | G1377 | 6094 | 2010-09-07 | LNrb | 2011-06-01 | River Bend | Bunge |  | 161 |  | 410 | River Bend-Bunge 161 kV Rebuild |  | IA | 1.88 |  | Planned | 700000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | West | MEC | 3272 | 2010-09-07 | 02321 | 6090 | 2010-09-07 | CB | 2011-06-01 | Raun |  |  | 345 |  | 1195 | Replace 345 kV circuit breaker |  | IA |  |  | Planned | 500000 | Planning 2010$ |  |  |  |  | Y | C>B>A
A in MTEP11 | West | MEC, ITCM | 2248 | 2011-09-06 | 07 MVPP1 | 6566 | 2011-09-01 | TEQ | 2017-06-01 | Ottumwa | 345 kV terminal |  | 345 |  |  | add 345 kV terminal for Adair line |  | IA |  |  | Planned | 3294904 |  |  |  | Y | Y | Y | B>A
A in MTEP11 | West | MP | 2549 | 2010-12-18 | 15L | 4561 | 2010-12-18 | LN | 2014-06-01 | 15th AVE West | Fond du Lac H.E. | 1 | 115 |  | 182 | MP Line #15 Upgarde |  | MN | 11.33 |  | Planned | 3179000 |  |  |  | y |  | y | C>B>A
A in MTEP11 | West | MP | 2634 | 2010-09-15 | Savanna | 6369 | 2011-01-05 | SUB | 2012-12-01 | Savanna |  | 1 | 115 |  |  | Savanna 115 kV breaker Station |  | MN |  |  | Planned | 2600000 | Engineering |  |  | Y |  | Y | B>A
A in MTEP11 | West | MP | 2634 | 2010-09-15 | Savanna | 6370 | 2011-01-05 | LN | 2014-12-01 | Savanna | Floodwood Tap | 1 | 115 |  |  | Thermal upgrade of Savanna-9 Line tap |  | MN |  |  | Planned | 1500000 | Planning |  |  | Y |  | Y | B>A
A in MTEP11 | West | MP | 3373 | 2010-11-01 | 9 Line | 6244 | 2010-11-01 | LnUp | 2012-12-30 | Blackberry | Floodwood Tap | 1 | 115 |  |  | Thermal Upgrade |  | MN | 16 | 0 | Planned | 8000000 |  |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | MP | 3374 | 2010-09-15 | Greenway | 6245 | 2011-03-25 | Dist | 2012-11-01 | Diamond Lake (old Greenway) |  |  | 115 | 23 | 15 | re-energize existing substation |  | MN |  |  | Planned | 700000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | MP | 3374 | 2010-09-15 | Greenway | 6246 | 2011-03-25 | LN | 2012-11-01 | Diamond Lake (old Greenway) | Diamond Lake (old Greenway) 28L tap | 1 | 115 |  |  | re-energize existing 28L to Greenway |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | MP | 3374 | 2010-09-15 | Greenway | 6247 | 2011-03-25 | LN | 2012-11-01 | Diamond Lake (old Greenway) | Diamond Lake (old Greenway) 45L tap | 1 | 115 |  |  | re-energize existing 45L to Greenway |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | OTP | 2856 | 2011-07-01 | Victor-New Effington 41.6 kV Line Upgrade | 5009 | 2011-09-06 | LN | 2011-06-30 | Victor 41.6 kV | New Effington 41.6 kV |  | 41.6 |  | 24 MVA | Rebuild Existing 4-Mile 41.6 kV Line |  | SD |  |  | In Service | 200000 | In Service |  |  |  |  | Y | C>B>A
A in MTEP11 | West | OTP | 3466 | 2011-01-11 | Project J-035 5 MW Wind OTP Doran 41.6 kV line. | 6392 | 2011-01-01 | LN | 2012-08-01 | Doran Tap | Doran 41.6 kV | 1 | 41.6 |  |  | Add 3 Way Switch on 41.6 kV line between Doran 41.6 kV substation to Doran Jct. |  | MN |  |  | Planned | 140000 | Planning |  |  |  |  | Y | B>A
A in MTEP11 | West | OTP | 3481 | 2011-02-24 | Buffalo - Casselton 115 kV Line | 6432 | 2011-02-24 | LN | 2013-07-01 | Buffalo 115 kV | Casselton Ethanol 115 kV | 1 | 115 |  | 337 MVA | Construct new 16-mile 115 kV line from Buffalo - Casselton |  | ND |  | 16 | Planned | 7000000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | OTP | 3481 | 2011-02-24 | Buffalo - Casselton 115 kV Line | 6434 | 2011-02-24 | TX | 2014-12-31 | Buffalo 345 kV | Buffalo 115/41.6 kV | 1 | 345 | 115 | 187 MVA | Replace existing 112 MVA 345/115/41.6 kV transformer with a new 187 MVA 345/115/41.6 kV transformer |  | ND |  |  | Planned | 3000000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | OTP, MDU | 2220 | 2011-07-18 | 06 MVPP1 Big Stone S-Ellendale | 4092 | 2011-09-01 | LN | 2019-12-31 | Big Stone South | Ellendale |  | 345 |  |  | Line |  | SD/ND |  | 145 | Planned | 300000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, MDU | 2220 | 2011-07-18 | 06 MVPP1 Big Stone S-Ellendale | 6382 | 2011-09-01 | TX | 2019-12-31 | Ellendale 345/230 | Transformer |  | 345 | 230 |  | Transformer 345/230 |  | ND |  |  | Planned | 26164000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 4116 | 2011-09-01 | TX | 2017-12-31 | Big Stone South 345/230 | Transformer | 1 | 345 | 230 | 672 MVA | Transformer #1 345/230/13.8 kV |  | SD |  |  | Planned | 4000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 4117 | 2011-09-01 | LN | 2017-12-31 | Big Stone South | Brookings 345 kV double circuit | 1,2 | 345 |  |  | Line #1 and #2 |  | SD |  | 65 | Planned | 165000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 6572 | 2011-08-25 | SUB | 2017-12-31 | Brookings County | Substation |  | 345 |  |  | Termination for Big Stone - Brookings Co 345 kV line and conversion of the existing ring bus to a breaker-and-a-half |  | SD |  |  | Planned | 9720000 | Eng |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 6588 | 2011-09-01 | TX | 2017-12-31 | Big Stone South Sub | Equipment |  | 345 | 230 |  | Substation Equipment |  | SD |  |  | Planned | 30000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 6387 | 2011-09-01 | TX | 2017-12-31 | Big Stone South 345/230 | Transformer | 2 | 345 | 230 | 672 MVA | Transformer #2 345/230/13.8 kV |  | SD |  |  | Planned | 4000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 6589 | 2011-09-01 | TX | 2017-12-31 | Big Stone 230 | Big Stone 230 |  | 230 | 230 |  | Substation Equipment |  | SD |  |  | Planned | 10000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 6383 | 2011-09-01 | LN | 2017-12-31 | Big Stone | Big Stone South | 1 | 230 |  |  | Line #1 |  | SD |  | 2 | Planned | 2000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP, XEL | 2221 | 2011-07-18 | 01 MVPP1 Big Stone S-Brookings | 6384 | 2011-09-01 | LN | 2017-12-31 | Big Stone | Big Stone South | 2 | 230 |  |  | Line #2 |  | SD |  | 2 | Planned | 2000000 | Planning |  |  | Y | Y | Y | B>A
A in MTEP11 | West | OTP/XEL | 3481 | 2011-02-24 | Buffalo - Casselton 115 kV Line | 6433 | 2011-02-24 | LN | 2014-12-31 | Mapleton 115 kV | Sheyenne 115 kV | 1 | 115 |  | 147 MVA | Rebuild 8 mile portion of the existing Sheyenne - Mapleton 115 kV line from 266 ACSR conductor to 795 ACSS conductor |  | ND | 8 |  | Planned | 4000000 | Planning |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | XEL | 1203 | 2011-07-18 | 02 MVPP1 | 4224 | 2011-09-01 | TX | 2014-01-22 | Franklin | Transformer | 2 | 115 | 69 | 70 | Upgrade 47 MVA to 70 MVA (Time line is dependant on SW MN - Twinc Cities 345 kV line |  | MN |  |  | Planned | 4000000 | Scoping estimate |  |  | Y | Y | NT | B>A
A in MTEP11 | West | XEL | 1203 | 2011-07-18 | 02 MVPP1 | 1897 | 2011-09-01 | TX | 2014-01-22 | Franklin | Transformer | 1 | 115 | 69 | 70 | Upgrade 47 MVA to 70 MVA (Time line is dependant on SW MN - Twinc Cities 345 kV line |  | MN |  |  | Planned | 2400000 | Scoping estimate |  |  | Y | Y | NT | B>A
A in MTEP11 | West | XEL | 3309 | 2010-09-15 | Buffalo Ridge Sub Equipment | 6145 | 2011-03-25 | SUB | 2011-08-01 | Pipestone |  | 1 | 115 |  |  | Retap the breaker CTs going to Buffalo Ridge to 2000:5. |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3309 | 2010-09-15 | Buffalo Ridge Sub Equipment | 6144 | 2011-03-25 | SUB | 2011-08-01 | Buffalo Ridge |  | 1 | 115 |  |  | Upgrade the wave traps and line switches at Buffalo Ridge going to Lake Yankton and Pipestone substations from 1200 A to 2000 A. |  | MN |  |  | Planned | 286000 | engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6150 | 2010-09-15 | LN | 2012-06-01 | Victoria tap | West Creek | 1 | 115 |  | 361 | New 115 kV line |  | MN | 1 | 1 | Planned | 19450000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6154 | 2010-09-15 | LNcnv | 2012-06-01 | Chaska | Scott County | 1 | 115 |  |  | upgrade 69 kV line to 115 kV |  | MN | 1.9 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6148 | 2010-09-15 | LNcnv | 2012-06-01 | Augusta | Victoria tap | 1 | 115 |  | 361 | Upgrade 69 kV line to 115 kV |  | MN | 1.5 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6149 | 2010-09-15 | SUB | 2012-06-01 | Victoria |  |  | 115 |  |  | Upgrade substation to 115 kV |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6156 | 2010-09-15 | CB | 2012-06-01 | Chaska |  |  | 115 |  |  | Add new line termination |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6155 | 2010-09-15 | CB | 2012-06-01 | West Waconia |  |  | 115 |  |  | Add new line termination |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6146 | 2010-09-15 | LNcnv | 2012-06-01 | West Waconia | Augusta | 1 | 115 |  | 361 | upgrade 69 kV line to 115 kV |  | MN | 1 | 2.5 | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6152 | 2010-09-15 | LNcnv | 2012-06-01 | West Creek | Chaska | 1 | 115 |  | 361 | Upgrade 69 kV line to 115 kV |  | MN | 1.9 | 1 | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6151 | 2010-09-15 | SUB | 2012-06-01 | West Creek |  |  | 115 |  |  | New 115 kV disttribution substation |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6147 | 2010-09-15 | SUB | 2012-06-01 | Augusta |  |  | 115 |  |  | Upgrade substation to 115 kV |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3310 | 2010-09-15 | Highway 212 | 6153 | 2010-09-15 | SUB | 2012-06-01 | Chaska |  |  | 115 |  |  | Upgrade 69 kV substation to 115 kV |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3312 | 2010-09-15 | MN Valley - Maynard - Kerkhoven tap upgrade | 6158 | 2011-06-16 | LNup | 2014-06-01 | Minnesota Valley | Maynard | 1 | 115 |  | 361 | upgrade existing 115 kV line to higher capacity |  | MN | 10.89 |  | Planned | 5790000 |  |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | XEL | 3312 | 2010-09-15 | MN Valley - Maynard - Kerkhoven tap upgrade | 6159 | 2011-06-16 | LNup | 2014-06-01 | Maynard | Kerkhoven tap | 1 | 115 |  | 361 | upgrade existing 115 kV line to higher capacity |  | MN | 14.8 |  | Planned | 7870000 |  |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | XEL | 3313 | 2010-09-15 | New Prague switch | 6160 | 2011-06-29 | TAP | 2012-06-01 | SMMPA New Prague tap |  |  | 69 |  |  | Install 1 way switch |  | MN |  |  | Planned | 180000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3314 | 2010-09-15 | Kohlman Lake - Long Lake 2nd circuit | 6161 | 2010-09-15 | LN | 2014-06-01 | Kohlman Lake | Long Lake | 2 | 115 |  | 361 | Convert the bifurcated 115 kV line to double circuit |  | MN |  | 0.08 | Planned | 3000000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3314 | 2010-09-15 | Kohlman Lake - Long Lake 2nd circuit | 6163 | 2010-09-15 | CB | 2014-06-01 | Long Lake |  |  | 115 |  |  | Add new line termination |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3314 | 2010-09-15 | Kohlman Lake - Long Lake 2nd circuit | 6162 | 2010-09-15 | CB | 2014-06-01 | Kohlman Lake |  |  | 115 |  |  | Add new line termination |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3315 | 2010-09-15 | ChisagoCo 2nd TR | 6165 | 2010-09-15 | CB | 2014-06-01 | Chisago County |  |  | 345 |  |  | Install breakers to accommodate the new TR |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3315 | 2010-09-15 | ChisagoCo 2nd TR | 6164 | 2010-09-15 | TX | 2014-06-01 | Chisago County |  | 5 | 345 | 115 | 448 | Install 2nd 345/115 kV transformer |  | MN |  |  | Planned | 7000000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3315 | 2010-09-15 | ChisagoCo 2nd TR | 6166 | 2010-09-15 | CB | 2014-06-01 | Chisago County |  |  | 115 |  |  | Install breakers to accommodate the new TR |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3316 | 2010-09-15 | Riverside - Apache upgrade | 6167 | 2010-09-15 | LNup | 2014-06-01 | Riverside | Apache | 1 | 115 |  | 361 | Upgrade line to higher capacity |  | MN | 3.5 |  | Planned | 3000000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3316 | 2010-09-15 | Riverside - Apache upgrade | 6168 | 2010-09-15 | TEQ | 2014-06-01 | Apache |  |  | 115 |  |  | Upgrade Apache switch |  | MN |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3317 | 2010-09-15 | Goose Lake - Kohlman Lake 2nd circuit | 6169 | 2010-09-15 | LN | 2014-06-01 | Goose Lake | Kohlman Lake | 2 | 115 |  | 361 | Build 2nd Goose Lake - Kohlman Lake circuit by rebuilding the existing line to double circuit. |  | MN |  | 3.2 | Planned | 6000000 |  |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | XEL | 3317 | 2010-09-15 | Goose Lake - Kohlman Lake 2nd circuit | 6171 | 2010-09-15 | CB | 2014-06-01 | Kohlman Lake |  |  | 115 |  | 361 | Install breakers to accommodate 2nd line to Goose Lake |  | MN |  |  | Planned |  |  |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | XEL | 3317 | 2010-09-15 | Goose Lake - Kohlman Lake 2nd circuit | 6170 | 2010-09-15 | CB | 2014-06-01 | Goose Lake |  |  | 115 |  | 361 | Install breakers to accommodate 2nd line to Kohlman Lake |  | MN |  |  | Planned |  |  |  |  | Y |  | Y | C>B>A
A in MTEP11 | West | XEL | 3318 | 2010-09-15 | Parkers Lake Overstressed Breakers | 6172 | 2011-06-29 | SUB | 2011-10-01 | Parkers Lake |  |  | 115 |  |  | Replace the Parkers Lake breakers 5M48, 5M49, 5M50, 5M51, 5M52, 5M53, 5M57, 5M58, and 5M62 |  | MN |  |  | Planned | 1900000 | engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3319 | 2010-09-15 | Split Rock Overstressed Breakers | 6173 | 2011-06-29 | SUB | 2011-12-01 | Split Rock |  |  | 115 |  |  | Replace the Split Rock breakers 5X28, 5X29, 5X32, 5X34, 5X35, 5X36, 5X75, 5X76, 5X77, 5X81, and 5X83 |  | SD |  |  | Planned | 1344000 | engineering |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3320 | 2010-09-15 | Split Rock Reactor replacement | 6174 | 2011-03-25 | SUB | 2011-12-01 | Split Rock |  |  | 115 |  |  | Replace the broken 50 MVAR reactor and failed associated breaker at the Split Rock substation |  | SD |  |  | Planned | 100000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3321 | 2010-09-15 | Chemolite Breaker Addition | 6175 | 2011-03-25 | SUB | 2011-01-14 | Chemolite |  |  | 115 |  |  | Two breakers will be added to complete Breaker and 1/2 configuration |  | MN |  |  | In Service | 580000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3322 | 2010-09-15 | Cedar Falls - Clear Lake Rebuild | 6178 | 2011-06-29 | LNrb | 2013-06-01 | Colfax | Wheeler | 1 | 69 |  |  | Rebuild line ot 477 ACSR |  | WI | 3.7 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3322 | 2010-09-15 | Cedar Falls - Clear Lake Rebuild | 6177 | 2011-06-29 | LNrb | 2013-06-01 | Hay River | Colfax | 1 | 69 |  |  | Rebuild line ot 477 ACSR |  | WI | 0.8 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3322 | 2010-09-15 | Cedar Falls - Clear Lake Rebuild | 6176 | 2011-06-29 | LNrb | 2013-06-01 | Cedar Falls | Hay River | 1 | 69 |  |  | Rebuild line ot 477 ACSR |  | WI | 7.6 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3322 | 2010-09-15 | Cedar Falls - Clear Lake Rebuild | 6179 | 2011-06-29 | LNrb | 2013-06-01 | Wheeler | Ridgeland | 1 | 69 |  |  | Rebuild line ot 477 ACSR |  | WI | 10.2 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3322 | 2010-09-15 | Cedar Falls - Clear Lake Rebuild | 6180 | 2011-06-29 | LNrb | 2013-06-01 | Ridgeland | Clear Lake |  | 69 |  |  | Rebuild line ot 477 ACSR |  | WI | 20.4 |  | Planned | 14000000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3323 | 2010-09-15 | Park Falls Bio-Refinery | 6182 | 2010-09-15 | CB | 2012-12-01 | Park Falls |  |  | 115 |  |  | Install new termination on straight bus at Park Falls for radial line |  | WI |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3323 | 2010-09-15 | Park Falls Bio-Refinery | 6181 | 2010-09-15 | SUB | 2012-12-01 | Flambeau Bio |  |  | 115 | 13.8 |  | Install new Customer supply sub |  | WI |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3323 | 2010-09-15 | Park Falls Bio-Refinery | 6465 | 2011-03-30 | LNrb | 2012-12-01 | Park Falls | Osprey | 1 | 115 |  | 120 | Rebuild 27 miles from 2/0 ACSR to 477 ACSR |  | WI | 27 |  | Planned | 18000000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3323 | 2010-09-15 | Park Falls Bio-Refinery | 6183 | 2011-03-25 | LN | 2013-06-01 | Park Falls | Flambeau Bio | 1 | 115 |  |  | Install ~1.5 miles of 336 ACSR 115 kV line |  | WI |  |  | Planned | 5769000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3324 | 2010-09-15 | Eau Claire Overstressed Breakers | 6184 | 2011-06-29 | CB | 2011-12-01 | Eau Claire |  |  | 69 |  |  | Replace overstressed Eau Claire 69 kV breakers. 4E185, 4E186, 4E187, 4E188, 4E189, 4E190, 4E191, 4E192, 4E193, 4E195. |  | WI |  |  | Planned | 1683000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3325 | 2010-09-15 | Orono 115 kV conversion | 6187 | 2010-09-15 | TAP | 2012-12-01 | Orono | Crow River | 1 | 115 |  |  | Run an in and out to Orono from the Medina - Crow River line |  | MN |  | 0.5 | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3325 | 2010-09-15 | Orono 115 kV conversion | 6186 | 2010-09-15 | TAP | 2012-12-01 | Orono | Medina | 1 | 115 |  |  | Run an in and out to Orono from the Medina - Crow River line |  | MN |  | 0.5 | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3325 | 2010-09-15 | Orono 115 kV conversion | 6185 | 2010-09-15 | DIST | 2012-12-01 | Orono |  |  | 115 |  |  | Convert sub to 115 kV |  | MN |  |  | Planned | 5340000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3326 | 2010-09-15 | Black Dog Outlet | 6188 | 2011-06-29 | LNrb | 2012-06-01 | Black Dog | Savage | 1 | 115 |  | 239 | Rebuild line to 795 ACSS |  | MN |  |  | Planned | 4564000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3327 | 2010-09-15 | Eau Claire - Madison Street Rebuild | 6190 | 2011-06-29 | LNrb | 2011-12-01 | Sterling | Madison Street | 1 | 69 |  | 117 | Replace .4 miles of 4/0 conductor with 795 ACSR |  | WI | 0.4 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3327 | 2010-09-15 | Eau Claire - Madison Street Rebuild | 6189 | 2011-06-29 | LNrb | 2011-12-01 | Eau Claire | Sterling | 1 | 69 |  | 68 | Replace .5 miles of 4/0 conductor with 795 ACSR |  | WI | 0.5 |  | Planned | 1600000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3454 | 2010-12-06 | Hollydale 115 kV upgrade | 6366 | 2010-12-06 | DIST | 2013-06-01 | Hollydale |  | 1 | 115 | 13.8 |  | Rebuild substation for 115 kV line |  | MN |  |  | Planned | 4340000 | Scoping |  |  | N |  | Y | C>B>A
A in MTEP11 | West | XEL | 3454 | 2010-12-06 | Hollydale 115 kV upgrade | 6365 | 2010-12-06 | LNrb | 2013-06-01 | Hollydale | Pomerleau Lake | 1 | 115 |  | 361 | Rebuild 69 kV line from Hollydale to new Plymouth area substation |  | MN | 3.4 |  | Planned | 3690000 | Scoping |  |  | N |  | Y | C>B>A
A in MTEP11 | West | XEL | 3454 | 2010-12-06 | Hollydale 115 kV upgrade | 6367 | 2010-12-06 | SUB | 2013-06-01 | Pomerleau Lake | switching station | 1 | 115 |  |  | New 115 kV switching station to tie 115 kV line to Medina into the GRE Parkers Lake - Elm Creek line. |  | MN |  |  | Planned | 7880000 | Scoping |  |  | N |  | Y | C>B>A
A in MTEP11 | West | XEL | 3473 | 2011-01-28 | Sioux Falls 115 kV Phase 1 | 6403 | 2011-01-28 | SUB | 2014-06-01 | Sioux Falls (New) |  |  | 115 | 13.8 |  | New 115/13.8 kV substation located near the existing Sioux Falls substation |  | SD |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3473 | 2011-01-28 | Sioux Falls 115 kV Phase 1 | 6404 | 2011-01-28 | SUB | 2014-06-01 | Lawrence |  |  | 115 | 34.5 |  | Rebuild 115 kV yard to breaker and a half to accommodate new 115 kV line |  | SD |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3473 | 2011-01-28 | Sioux Falls 115 kV Phase 1 | 6402 | 2011-01-28 | SUB | 2014-06-01 | West Sioux Falls |  |  | 115 | 13.8 |  | Add new line termination and breaker |  | SD |  |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3473 | 2011-01-28 | Sioux Falls 115 kV Phase 1 | 6401 | 2011-01-28 | LNrb | 2014-06-01 | Sioux Falls (New) | West Sioux Falls | 1 | 115 |  | 361 | Rebuild line to 115 kV |  | SD | 4.3 |  | Planned | [6 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3473 | 2011-01-28 | Sioux Falls 115 kV Phase 1 | 6400 | 2011-01-28 | LNrb | 2014-06-01 | Lawrence | Sioux Falls (New) | 1 | 115 |  | 361 | Rebuilding line to 115/69 kV double circuit |  | SD | 5.4 |  | Planned | 35000000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3474 | 2011-01-28 | Adams 345 kV Reactor Installation | 6405 | 2011-01-28 | SUB | 2012-06-01 | Adams |  |  | 345 |  |  | Install a 50 MVAR reactor on the Pleasant Valley line, along with breaker and disconect switch |  | MN |  |  | Planned | 2260000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3475 | 2011-01-28 | Prairie 3rd transformer | 6406 | 2011-01-28 | SUB | 2014-06-01 | MPC Prairie | NSP Prairie | 7 | 230 | 115 |  | 230/115 kV 336 MVA transformer and 230 kV line from MPC Prairie to NSP Prairie |  | ND |  |  | Planned | 12000000 | [5 empty] | Y | C>B>A
A in MTEP11 | West | XEL | 3476 | 2011-02-14 | Maple River - Cass County 345 kV line | 6408 | 2011-02-14 | SUB | 2014-06-01 | Cass Coutny |  | 1 | 345 | 115 | 448 | New 345/115 kV transformer and 3 row 115 kV breaker and Half |  | ND |  |  | Planned | 7000000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3476 | 2011-02-14 | Maple River - Cass County 345 kV line | 6409 | 2011-02-14 | SUB | 2014-06-01 | Maple River | Cass County | 1 | 345 |  | 2390 | New 4.5 mile 345kV line from Maple River to Cass Coutny substation |  | ND |  | 4.5 | Planned | 4436000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3476 | 2011-02-14 | Maple River - Cass County 345 kV line | 6410 | 2011-02-14 | SUB | 2014-06-01 | Maple River |  |  | 345 |  |  | New 345 kV breakers at Maple River substation to accommodate the proposed 345 kV line |  | ND |  |  | Planned | 1790000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3509 | 2011-05-10 | Stinson to Bayfront Rebuild | 6480 | 2011-05-10 | LNrb | 2013-01-01 | Iron River | Ownership change near Lakeside | 1 | 115 |  | 230 | Rebuild 5 miles of 115 kV from 336 ACSR to 795 ACSR |  | WI | 5 |  | Planned | 2400000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3509 | 2011-05-10 | Stinson to Bayfront Rebuild | 6479 | 2011-05-10 | LNrb | 2013-01-01 | Ino Pump | Iron River | 1 | 115 |  | 230 | Rebuild 9 miles of 115 kV from 336 ACSR to 795 ACSR |  | WI | 9 |  | Planned | 4200000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL | 3509 | 2011-05-10 | Stinson to Bayfront Rebuild | 6478 | 2011-05-10 | LNrb | 2013-01-01 | Bayfront | Ino Pump | 1 | 115 |  | 230 | Rebuild 19 miles of 115 kV from 336 ACSR to 795 ACSR |  | WI | 19 |  | Planned | 8800000 | Planning |  |  |  |  | Y | C>B>A
A in MTEP11 | West | XEL, GRE | 3454 | 2010-12-06 | Hollydale 115 kV upgrade | 6364 | 2010-12-06 | LNrb | 2013-06-01 | Medina | Hollydale | 1 | 115 |  | 361 | Rebuild 4.6 Miles of 69 kV line to 795 ACSS 115 kV |  | MN | 4.6 |  | Planned | 7380000 | Scoping |  |  | N |  | Y | C>B>A
A in MTEP11 |  | AmerenIL | 3022 | 2011-09-06 | 16 MVPP1 | 6554 | 2011-09-06 | TX | 2019-06-01 | Galesburg | 345/138 kV transformer | 1 | 345 | 138 | 560 MVA | new |  |  |  |  | Planned |  |  |  |  | Y | Y | Y | B>A
A in MTEP03 | Central | SIPC | 81 | 2011-04-22 |  | 60 | 2010-12-06 | LN | 2012-09-01 | Power Plant | Carrier Mills 161kV |  | 161 |  |  | 25-mile 161kV transmission line from Southern Illinois Power Cooperative's power plant to a new 161/69kV substation |  | IL |  | 25 | Planned | 9200000 | [5 empty] | Y | A
A in MTEP09 | Central | Ameren | 1240 | 2008-12-10 |  | 1940 | 2009-09-14 | LNrc | 2012-06-01 | Sioux | Huster | 3 | 138 |  | 370 | Reconductor 13 miles | J10 | MO | 13 |  | Planned | 5550000 | Engineering |  |  | Y |  | Y | A
A in MTEP09 | Central | Ameren | 1240 | 2008-12-10 |  | 1939 | 2009-09-14 | LNrc | 2012-06-01 | Sioux | Huster | 1 | 138 |  | 370 | Reconductor 15 miles | J10 | MO | 15 |  | Planned | 5550000 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | Central | Ameren | 1235 | 2010-04-05 |  | 1934 | 2010-04-05 | LNup | 2016-06-01 | Fredericktown | AECI Fredericktown Tap | 1 | 161 |  | 250 | Increase ground clearance | K11 | MO | 12 |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP08 | Central | Ameren | 1238 | 2006-03-17 |  | 1937 | 2011-07-05 | LN | 2011-11-17 | GM 161 kV Sub. | AECI Enon Substation | 1 | 161 |  | 280 | Extend 1 mile of line to AECI Enon Substation | J10 | MO |  | 1 | Planned | 1896500 | Engineering |  |  |  |  | Y | A
A in MTEP07 | Central | Ameren | 152 | 2010-04-05 |  | 399 | 2010-06-28 | LN | 2011-11-30 | Big River | Rockwood | 1 | 138 |  | 339 | new line | J11 | MO |  | 10 | Planned | 13381100 | Engineering |  |  | Y |  | Y | A
A in MTEP10 | Central | AmerenIL | 1528 | 2008-02-14 |  | 2604 | 2010-07-08 | TX | 2012-06-01 | Rising | Transformer | 1 | 345 | 138 | 560 | Replace existing transformer with a 560 MVA | K9 | IL |  |  | Planned | 5000000 | [5 empty] | Y | A
A in MTEP10 | Central | AmerenIL | 1535 | 2010-06-04 |  | 2612 | 2009-09-14 | TEQ | 2012-06-01 | Wood River | Stallings | 1 | 138 |  | 259 | Replace terminal equipment at Stallings, reconductor section of line (Line # 1456) | K10 | IL | 6 |  | Planned | 2036000 | [5 empty] | Y | A
A in MTEP10 | Central | AmerenIL | 2064 | 2010-06-04 |  | 3973 | 2009-09-14 | LNrc | 2012-06-01 | South Bloomington | Diamond Star Tap | 1 | 138 |  | 382 | Reconductor 3.33 miles of 336 ACSR in S Bloomington - Danvers line to 1600 Amps | K9 | IL | 3.33 |  | Planned | 2113000 | [5 empty] | Y | A
A in MTEP10 | Central | AmerenIL | 2288 | 2010-06-04 |  | 4204 | 2009-09-14 | LN | 2012-06-01 | Line 1364 (new tap) | Washington Street Substation | 2 | 138 |  |  | Tap 138 kV Line 1364 for 'in-out' arrangement, replace Line 1326 w/ 'in-out' | K9 | IL |  | 0.17 | Planned | 4155000 | [5 empty] | Y | A
A in MTEP10 | Central | AmerenIL | 2957 | 2010-06-04 |  | 5155 | 2009-09-14 | LN | 2012-12-31 | Edwards Plant | Tazewell | 2 | 138 |  | 322 | Edwards-Tazewell 138 kV Line 1373 - Reconductor 1.57 miles of 795 kcmil ACSR conductor and 7.5 miles of 927 kcmil ACAR conductor with conductor capable of carrying 1600 A under summer emergency conditions. Replace a 1200 A wavetrap and CT's at Edwards. | K9 | IL | 9.07 |  | Planned | 121000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenIL | 2986 | 2010-05-08 | AMRN7 | 5190 | 2009-12-23 | LN | 2014-06-01 | Wood River-Stallings-1456 | Tap to Supply North Alton 138-34.5 kV Sub | 1 | 138 |  | 240 | North Alton 138-34.5 kV Substation Supply - Supply new 138-34.5 kV Substation from an in-out connection to the Wood River-Stallings-1456 138 kV line. Approximately 4 miles of double-circuit 138 kV line needed. | J10 | IL |  | 4 | Planned | 6445500 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenIL | 2986 | 2010-05-08 | AMRN7 | 5189 | 2010-05-08 | LN | 2015-12-01 | Wood River-North Staunton-1436 | Tap to Supply North Alton 138-34.5 kV Sub | 1 | 138 |  | 240 | North Alton 138-34.5 kV Substation Supply - Supply new 138-34.5 kV Substation from an in-out connection to the Wood River-Stallings-1456 138 kV line. Approximately 4 miles of double-circuit 138 kV line needed. | J10 | IL |  | 4 | Planned | 6445500 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenIL | 2992 | 2010-05-08 |  | 5197 | 2009-09-14 | LN | 2014-06-01 | Bondville | S.W. Campus | 1 | 138 |  | 411 | Bondville-S.W. Campus 138 kV - Construct 8 miles of new 138 kV line. Construct 138 kV Ring Bus at Bondville (2 new PCB's) and a 138 kV Ring Bus at Champaign S.W. Campus (4 new PCB's). | K9 | IL |  | 8 | Planned | 10000000 | Planning |  |  |  |  | Y | A
A in MTEP09 | Central | AmerenIL | 2273 | 2010-04-05 |  | 4187 | 2011-07-05 | LN | 2013-06-01 | LaFarge | 161 kV Supply to Customer Substation |  | 161 |  |  | Provide 161 kV supply to customer substation | K11 | IL |  |  | Planned | 570000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | Central | AmerenIL | 2279 | 2010-04-05 |  | 4195 | 2011-07-05 | LN | 2011-10-05 | Campbell | Steelville | 1 | 138 |  | 220 | Reconductor 477 kcmil ACSR to carry 1200 A summer emergency | K11 | IL | 6.19 |  | Planned | 1866000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | Central | AmerenIL | 2472 | 2010-04-05 | AMRN3 | 4446 | 2010-04-05 | SUB | 2016-12-01 | Maple Ridge 345 kV Switching Station | New Substation |  | 345 |  |  | Install switching station in Duck Creek-Tazewell 345 kV line | K9 | IL |  |  | Planned | 6523000 | Eng |  |  | Y | Y | Y | A
A in MTEP09 | Central | AmerenIL | 2472 | 2010-04-05 | AMRN3 | 4444 | 2010-04-05 | SUB | 2016-12-01 | Fargo 345/138 kV | New Substation |  | 345 | 138 | 560 | Install 560 MVA, 345/138 kV Transformer | K9 | IL |  |  | Planned | 9370000 | Eng |  |  | Y |  | Y | A
A in MTEP09 | Central | AmerenIL | 2472 | 2010-04-05 | AMRN3 | 4445 | 2010-04-05 | LN | 2016-12-01 | Fargo | Maple Ridge | 1 | 345 |  | 1793 | Install approximately 20 miles of new line to supply Fargo Substation | K9 | IL |  | 20 | Planned | 62275000 | Eng |  |  | Y | Y | Y | A
A in MTEP08 | Central | AmerenIL | 1529 | 2010-04-05 |  | 2605 | 2011-07-05 | LNrc | 2011-12-22 | Brokaw | State Farm Line 1596 | 1 | 138 |  | 337 | Reconductor to 2000 A Summer Emergency | K9 | IL | 3.2 |  | Planned | 2566900 | [5 empty] | Y | A
A in MTEP08 | Central | AmerenIL | 2060 | 2010-06-28 |  | 3958 | 2010-06-28 | LNup | 2012-06-01 | East Peoria | Flint | 1 | 138 |  | 233 | Reconductor to 1200 A capability | K9 | IL | 4.54 |  | Planned | 2113000 | [5 empty] | Y | A
A in MTEP08 | Central | AmerenIL | 2068 | 2010-04-05 |  | 3964 | 2010-06-28 | LN | 2014-12-01 | Latham | Oreana | 1 | 345 |  | 1195 | Build 8.5 miles of 345 kV line and remove the Latham - Maroa W connection |  | IL | 8.5 |  | Planned | 35077000 |  |  |  | Y | Y | Y | A
A in MTEP08 | Central | AmerenIL | 2069 | 2010-04-05 |  | 3962 | 2010-06-28 | LN | 2014-12-01 | Brokaw | South Bloomington | 1 | 345 |  | 1793 | Build approximately 5 miles of 345 kV line from Brokaw - South Bloomington substation | K9 | IL | 5 |  | Planned | 13429000 |  |  |  | Y | Y | Y | A
A in MTEP08 | Central | AmerenIL | 2069 | 2010-04-05 |  | 3963 | 2010-06-28 | TX | 2014-12-01 | South Bloomington | South Bloomington XFMR | 1 | 345 | 138 | 560 | Install 560 MVA 345/138 kV transformer at South Bloomington substation | K9 | IL |  |  | Planned | 6600000 |  |  |  | Y |  | Y | A
A in MTEP06 | Central | AmerenIL | 739 | 2006-03-17 |  | 1432 | 2008-08-29 | LN | 2012-11-01 | Line 4561 Tap | Franklin County Power Plant | 1 | 345 |  |  | 345 kV connection (new ring bus) to new generation | K11 | IL |  |  | Planned | 6410900 | Engineering | Interconnection |  |  |  | Y | A
A in MTEP05 | Central | AmerenIL | 725 | 2010-06-28 | 725 | 1418 | 2010-06-28 | LN | 2012-04-26 | N. LaSalle | Wedron Fox River | 1 | 138 |  | 266 | 2 CB at N LaSalle, 1 CB at Wedron Fox River Substation | K8 | IL |  | 25 | Planned | 21357530 | Engineering |  |  |  |  | Y | A
A in MTEP05 | Central | AmerenIL | 726 | 2010-06-28 | 725 | 1419 | 2010-06-28 | LN | 2013-07-30 | Ottawa | Wedron Fox River | 1 | 138 |  | 266 | 1 CB at Ottawa, new 138 kV line to Wedron Fox River Substation | K8 | IL |  | 8 | Planned | 8962967 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 2972 | 2010-05-08 |  | 5172 | 2009-12-23 | LN | 2012-06-01 | Bailey | Joachim | 1 | 138 |  | 411 | Sandy Creek-Joachim-1 138 kV Line - Reconductor 6.2 miles of 795 kcmil ACSR with conductor having 1600 A summer emergency capability between Sandy Creek and Bailey Substations | J11 | MO | 0.5 |  | Planned | 246700 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 2972 | 2010-05-08 |  | 5173 | 2009-12-23 | LN | 2012-06-01 | Bailey | Sandy Creek | 1 | 138 |  | 322 | Sandy Creek-Joachim-1 138 kV Line - Reconductor 6.2 miles of 795 kcmil ACSR with conductor having 1600 A summer emergency capability between Sandy Creek and Bailey Substations |  | MO | 6.2 |  | Planned | 3059000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 2976 | 2010-05-08 | AMRN6 | 5177 | 2009-09-14 | LN | 2012-12-01 | Cahokia-Central-1 | Relocate Central 138-34.5 kV Substation | 1 | 138 |  | 370 | Central 138-34.5 kV Substation - Relocate Substation - Reterminate Cahokia-Central-1 138 kV line to the new Central Substation. New substation will be located roughly one-half mile from existing substation. | J11 | MO |  |  | Planned | 1544300 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 2976 | 2010-05-08 | AMRN6 | 5178 | 2009-09-14 | LN | 2012-12-01 | Cahokia-Central-2 | Relocate Central 138-34.5 kV Substation | 2 | 138 |  | 370 | Central 138-34.5 kV Substation - Relocate Substation - Reterminate Cahokia-Central-2 to the new Central Substation. New substation will be located roughly one-half mile from existing substation. | J11 | MO |  |  | Planned | 1544300 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 2976 | 2010-05-08 | AMRN6 | 5179 | 2009-09-14 | LN | 2012-12-01 | Central-Watson-1 | Relocate Central 138-34.5 kV Substation | 1 | 138 |  | 367 | Central 138-34.5 kV Substation - Relocate Substation - Reterminate Central-Watson-1 138 kV line to the new Central Substation. New substation will be located roughly one-half mile from existing substation. | J11 | MO |  |  | Planned | 1544300 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 3107 | 2010-01-05 | AMRN19 | 5444 | 2010-01-05 | SUB | 2011-06-17 | Arnold | Tyson | 3 | 138 |  | 241 | Install 4-138 kV Breakers at Arnold Substation and rearrange 138 kV bus configuration at Arnold Substation. | J11 | MO |  |  | Planned | 570800 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 3107 | 2010-01-05 | AMRN19 | 5447 | 2010-01-05 | SUB | 2011-06-17 | Arnold | Meramec | 4 | 138 |  | 241 | Install 4-138 kV Breakers at Arnold Substation and rearrange 138 kV bus configuration at Arnold Substation. | J11 | MO |  |  | Planned | 570800 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 3107 | 2010-01-05 | AMRN19 | 5446 | 2010-01-05 | SUB | 2011-06-17 | Arnold | Tyson | 4 | 138 |  | 241 | Install 4-138 kV Breakers at Arnold Substation and rearrange 138 kV bus configuration at Arnold Substation. | J11 | MO |  |  | Planned | 570800 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | AmerenMO | 3107 | 2010-01-05 | AMRN19 | 5445 | 2010-01-05 | SUB | 2011-06-17 | Arnold | Meramec | 3 | 138 |  | 240 | Install 4-138 kV Breakers at Arnold Substation and rearrange 138 kV bus configuration at Arnold Substation. | J11 | MO |  |  | Planned | 570800 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 1520 | 2009-09-17 | 502G6713 | 2596 | 2010-06-25 | SUB | 2017-06-01 | Durbin | 230/69 substation | 1 | 230 | 69 |  | Build a new 230 69kv 150mva sub with 2 69kv line terminals |  | IN |  |  | Planned | 7000000 | Planning |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 1903 | 2009-09-17 | 504G6710 | 3800 | 2008-01-10 | LNrc | 2014-06-01 | Fishers North | Fishers 69 | 1 | 69 |  | 245 | Reconductor 1.05 miles 69kV line from Fishers No to Fishers with 954ACSR@100C conductor | M9 | IN | 1.05 |  | Planned | 455228.77 | Engineering |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2050 | 2009-09-17 | AMIN0083 | 5033 | 2011-01-11 | SUB | 2011-12-31 | Dresser | Trans Sub |  | 345 | 138 |  | Reconfigure Dresser substation bus and breakers, etc. for final Bank 3 configuration. | L10 | IN |  |  | Under Construction | 2980000 | 2009$, Engr |  |  | Y |  | Y | A
A in MTEP10 | Central | DEM | 2123 | 2009-09-17 | AMIN0071 | 2908 | 2010-01-06 | LN | 2012-06-01 | Bloomington 230 | Martinsville SE Jct | 1 | 69 |  | 153 | Bloomington to Martinsville 69kV - 6903 ckt. - Rebuild 9.2 miles of 336ACSR with 954ACSR@100C | M10 | IN | 9.2 |  | Planned | 2020000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2134 | 2009-09-17 | AMIN0317 | 2919 | 2010-01-06 | LN | 2013-06-30 | Bloomington 230 | Needmore Jct. | 1 | 69 |  | 143 | Bloomington 230kV Sub to Needmore Jct (Pole #825-3379) reconductor 6949 line with 954ACSR 100C conductor and replace (2) Needmore Jct. 69kV - 600 amp switches with 1200 amp switches. Old PIN 804J3052 | M10 | IN | 10.85 |  | Planned | 2712500 | Planning |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2136 | 2009-09-17 | 604J3051 | 2921 | 2010-01-06 | LN | 2012-06-30 | Greenwood HE Honey Creek Jct | Frances Creek Jct | 1 | 69 |  | 100 | Greenwood HE Honey Creek Jct to Frances Creek Jct uprate 69kV - 69102 line 1.12 mile for 100C | M10 | IN | 1.12 |  | Planned | 63533 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2137 | 2009-09-17 | 604J3056 | 2922 | 2010-01-06 | LN | 2012-06-30 | Greenwood Averitt Rd Jct | HE Honey Creek Jct | 1 | 69 |  | 100 | Greenwood Averitt Rd Jct to HE Honey Creek Jct 69 kV - 69102 Uprate 1.05 mile line section of 477acsr for 100C conductor temperature operation | M10 | IN | 1.05 |  | Planned | 53461 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2143 | 2009-09-17 | 602J3066 | 2929 | 2010-06-25 | TX | 2014-06-01 | Frances Creek | bank 2 | 2 | 345 | 69 | 200 | Add Frances Creek 345/69kV Bank 2 - 200MVA with LTC | M10 | IN |  |  | Planned | 6887000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2858 | 2009-09-14 | 504G6697 | 5011 | 2010-06-25 | LNrc | 2017-06-01 | Geist | Fortville | 1 | 69 |  | 153 | Reconductor 69kV 3.62 mile line from Geist sub to Fortville sub with 954ACSR conductor. | M10 | IN | 3.62 |  | Planned | 1820000 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2859 | 2009-09-17 | AMIN0123 | 5012 | 2009-09-17 | LNrc | 2012-06-01 | Peru Muni Jct | Wabash Jct | 1 | 69 |  | 100 | Peru Muni J to Wabash J 6986 Reconductor approx., 10.3 miles of 4/0 ACSR with 477 ACSR | M9 | IN | 10.3 |  | Planned | 3810000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2860 | 2009-09-14 | AMIN0130 | 5013 | 2009-09-17 | LNrc | 2012-06-01 | Brazil East | Reelsville Jct | 1 | 69 |  | 100 | Reconductor 6938 line from Brazil East to Reelsville Jct. with 477ACSR 100C conductor. Replace Reelsville Jct switches with 1200 amp switches. | M10 | IN | 6.58 |  | Planned | 2550000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2861 | 2009-09-14 | AMIN0129 | 5014 | 2010-06-25 | LNrc | 2012-06-01 | Greencastle Madison J | Greencastle Ind Pk | 1 | 69 |  | 143 | Reconductor 6996 line from Greencastle Madison Jct. to Greencastle East Jct. to Greencastle Ind. Pk. with 954ACSR 100C conductor. Replace or upgrade 2-600 amp Greencastle East Jct switches to 1200amp. | M10 | IN | 5.83 |  | Planned | 1482000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2863 | 2009-09-17 | 504H6972 & AMIN0057 | 5016 | 2010-01-06 | LN | 2012-06-02 | Carmel SE | new Jct in 69145 ckt. | 1 | 69 |  | 143 | Build new 69kV-954ACSR circuit from Carmel SE to new Jct in the 69145 line on Cumberland Rd, completing a loop from Carmel 146th St to Geist. also, (AMIN0057) Carmel SE Bank 2 69kV 22.4MVA; retire the 138-12kV existing bank fed from IPL (NERC tie) | M9 | IN |  | 5.5 | Planned | 4274200 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2865 | 2009-09-14 | 604G6620 | 5018 | 2010-06-25 | LNup | 2012-06-01 | Frankfort Burlington St | Middlefork | 1 | 69 |  | 53 | Frankfort Brlngtn St to Midfrk - 69133 ckt - uprate 11.5 miles of 4/0ACSR to 100C and reconductor 1.0 mile of 2/0CUB7 to 954ACSR@100C | M9 | IN | 12.5 |  | Planned | 582035 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2869 | 2009-09-14 | 902G1843 | 5022 | 2011-01-11 | SUB | 2012-06-01 | Zimmer 345kV sub | Trans Sub |  | 345 |  |  | Replace 345kV gas insulated sub with an air insulated sub | N10 | OH |  |  | Under Construction | 4032000 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2871 | 2009-09-17 | AMKY0125 | 5024 | 2011-03-25 | SUB | 2011-12-31 | EKPC Hebron | 138/69 substation | 1 | 138 | 69 |  | Add new EKPC Hebron 138/69kV transformer (outside DEM area 208). Includes 3 position – 138kV CB ring bus and associated Duke owned facilities (inside DEM area 208). 138kv Tie from DEM to EKPC is being revised slightly. 100% to be paid for by EKPC. | N11 | KY |  |  | Planned | 3345000 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2872 | 2010-06-25 | AMIN0354 | 5025 | 2010-06-25 | SUB | 2011-12-31 | Manhattan | new dist sub | 1 | 138 | 12 |  | Install 1200A - 138kv line switching on both sides of proposed tap line to new joint use DEM/WVPA Manhattan distribution sub in the 13802 ckt. | L10 | IN |  |  | Planned | 525723 | 2010$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2874 | 2009-09-14 | AMIN0233 | 5027 | 2011-06-23 | LN | 2011-12-01 | Noblesville Gen. Station | Geist | 1 | 230 |  | 319 | Relocate section of 23007 between Noblseville and Giest to new RoW around expanding mine operation - approx. 0.6 mile of added line length | M9 | IN |  | 0.6 | Planned | 1766218 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2875 | 2010-06-25 | AMIN0230 | 5028 | 2010-09-22 | SUB | 2011-12-31 | Edwardsville | new dist sub | 1 | 138 | 12 |  | Construct new Edwardsville 138/12kV distribution substation - single 22.4 MVA transformer | M11 | IN |  |  | Planned | 467387 | 2010$, Engr |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2876 | 2009-09-14 | AMOH0192 | 5029 | 2009-09-14 | SUB | 2013-06-01 | Red Bank | Trans Sub |  | 345 |  |  | Replace 345kV gas insulated bus with an air insulated bus | N10 | OH |  |  | Planned | 3467832 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2877 | 2009-09-14 | AMOH0194 | 5030 | 2010-06-25 | SUB | 2015-12-31 | West End | Trans Sub |  | 138 | 13.2 |  | Modifications to West End Substation facilities, 138 kV transmission lines and distribution lines to accommodate Brent Spence Bridge project | N10 | OH |  |  | Planned | 13780000 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2878 | 2009-09-14 | AMOH0100 | 5031 | 2010-01-06 | SUB | 2014-06-01 | Miami Fort | Trans Sub |  | 345 |  |  | Replace 345kV gas insulated bus with an air insulated bus and Miami Fort-Tanner Cir 4504 Relocate | N10 | OH |  |  | Planned | 1440000 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP10 | Central | DEM | 2879 | 2009-09-14 | AMIN0256 | 5032 | 2009-09-14 | SUB | 2012-12-31 | Brazil West | new dist sub | 1 | 69 | 12 |  | Construct Brazil West 10.5MVA 69/12kV sub in the 6902 Line to be located on 900N east of 425W | M10 | IN |  |  | Planned | 150000 | 2009$, Plan |  |  |  |  | NT | A
A in MTEP10 | Central | DEM | 2882 | 2009-09-14 | X02C8883 | 5035 | 2009-09-14 | CB | 2012-12-31 | Lateral | 138kV Bus 7 to Bus 8 tie |  | 138 |  | 478 | Replace bus tie breaker #840 and associated disconnect sw's - new limits will be CB - 3000A and D/S's - 2000A. | N10 | OH |  |  | Planned | 445302 | 2009$, Engr |  |  |  |  | Y | A
A in MTEP09 | Central | DEM | 1647 | 2009-09-17 | 503H6967 | 3378 | 2010-09-22 | SUB | 2012-06-01 | Carmel SE | 69/12 substation |  | 69 | 12 | 245 | Construct Carmel SE Bank 1 22.4MVA bank with 2 exits - extend a new radial 69kv - 954ACSS@200C from Carmel 146th St (no new bkr - share dist bk terminal) | M9 | IN |  | 4 | Planned | 2000000 | Plan |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 1880 | 2008-01-10 | 103H9056 | 3774 | 2011-01-11 | Dist | 2012-12-31 | Columbia | distribution sub |  | 138 | 12 |  | Columbia 138kV-22.4MVA Sub - New site or purchase and rebuild existing Siemens Sub #537- in F5484 between Warren and Maineville | N10 | OH |  |  | Planned | 215000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | Central | DEM | 2127 | 2008-04-07 | 804H3039 | 2912 | 2009-09-17 | TEQ | 2019-06-01 | Martinsville 69 | 69163-1 switch |  | 69 |  | 143 | 69163-1 switch replacement near tap to HE Cope with 1200A switch | M10 | IN |  |  | Planned | 40000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2132 | 2008-04-07 | 602J3049 | 2917 | 2009-09-17 | CAP | 2012-06-30 | Frances Creek | capacitor |  | 69 |  | 36 MVAR | Frances Creek Install 36MVAR 69kV capacitor bank | M10 | IN |  |  | Planned | 615500 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2133 | 2008-04-07 | 604H3011 | 2918 | 2009-09-17 | LN | 2012-06-01 | Franklin 230 | Franklin Forsythe | 2 | 69 |  | 143 | Franklin 230 sub to Forsythe 69 sub - Build new 3.5 mile 69kV - 69159 line; new line terminal at Forsythe; use existing terminal at Franklin 230 | M10 | IN |  | 3.5 | Planned | 1030000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2148 | 2008-04-07 | 504F6518 | 2935 | 2011-03-25 | LN | 2012-05-01 | Cadiz | Milner's Corner Jct | 1 | 69 |  | 143 | Cadiz-Markleville-Milner's Corner J - Reconductor 69kv - 69131 ckt - 9.24 mile section with 477ACSR@100C; Replace 69kv three way switch at Milner's Corner Jct with three one way 1200A switches; Upgrade the Markleville 600A switches #1 and #2 to 1200A | M9 | IN | 9.24 |  | Planned | 3208251 | Engineering 2010$ |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2149 | 2008-04-07 | X02C7984 | 2936 | 2010-09-22 | SUB | 2011-12-31 | West End | bus tie bkr & line bkr | 1 | 138 |  | 478 | West End substation - Install a 138kV circuit breaker to tie the east and west 138 kV busses together and a line breaker in the 1389 ckt | N10 | OH |  |  | Under Construction | 1040000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | Central | DEM | 2153 | 2008-04-07 | 504G6695 | 2941 | 2011-01-11 | LN | 2017-06-01 | Mohawk | Lee Hanna | 1 | 69 |  | 71.7 | Mohawk to Lee Hanna 69kV reconductor 69130 ckt (5.27 mi) with 954acsr@100C | M10 | IN | 5.27 |  | Planned | 2317000 | Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2154 | 2010-06-25 | AMIN0360 | 2942 | 2010-09-22 | SUB | 2013-12-31 | Carmel Rohrer Rd. | distribution sub |  | 69 | 12 |  | Carmel Rohrer Rd 69/12-22.4MVA sub to looped through the 6989 ckt. at or near the existing Carmel Shell Oil tap | M9 | IN | 0.4 | 0.4 | Planned | 591143 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2327 | 2008-10-01 | 704J3096 | 4259 | 2009-02-18 | LNrc | 2013-06-01 | Speed | HE Bethany | 1 | 69 |  | 53 | Speed to HE Bethany 69kV - 6955 Reconductor Ph1 - Replace 5.2 miles of 3/0 ACSR with 477 ACSR (new limiter 4/0acsr @ 80C) | M10 | IN | 5.2 |  | Planned | 1560000 | 2008$, Plan |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2331 | 2008-10-01 | 504F6413 | 4263 | 2009-02-18 | LNrc | 2012-06-01 | Shelbyville NE | Knauf | 1 | 69 |  | 153 | Shelbyville NE to Knauf Reconductor 1.75 miles of 397ACSR on 6946 ckt. with 954acsr@100C | M10 | IN | 1.75 |  | Planned | 777000 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2332 | 2008-10-01 | 504G6696 | 4264 | 2009-02-18 | LNrc | 2012-06-01 | Zionsville Turkeyfoot | Zionsville 96th St Jct | 1 | 69 |  | 153 | Zionsville Turkeyfoot to Zionsville 96th St Jct Reconductor 1.59 mile 69kV - 69155 ckt with 954ACSR@100C | M9 | IN | 1.59 |  | Planned | 704000 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP09 | Central | DEM | 2334 | 2009-09-17 | AMIN0132 | 4266 | 2010-09-22 | SUB | 2012-06-01 | Fishers 106th St | distribution sub |  | 69 | 12 |  | New Fishers 106th St 69/12 kv sub: Construct 69kV line in and out of sub and 69kv bus; located in the proposed loop between Carmel SE 69 sub and Fishers 69145 | M9 | IN |  |  | Planned | 174000 | 2009$, Engr |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 834 | 2005-07-11 | 802D5899 | 3071 | 2009-02-18 | CAP | 2014-06-01 | Kingman | Capacitor |  | 69 |  | 7.2 MVAR | Add capacitor | L9 | IN |  |  | Planned | 500000 | Planning |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 835 | 2008-04-07 | 602D6064 | 3072 | 2009-06-26 | CAP | 2013-06-01 | Pittsboro | Capacitor |  | 69 |  | 14.4 MVAR | Add capacitor | M9 | IN |  |  | Planned | 422362 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 841 | 2009-02-18 | AJ | 820 | 2009-02-18 | TX | 2015-06-01 | Westwood Bk1 | transformer | 1 | 345 | 138 | 369.4 | Replace 1600A 138kV breaker with 3000A to allow full xfr rating. | L9 | IN |  |  | Planned | 141623 | 2007$, Engr |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1245 | 2008-04-07 | 602G6617 | 1959 | 2011-01-11 | SwSta | 2014-06-01 | Potato Creek Switching Station |  |  | 69 |  |  | Construct 69kV switching station |  | IN |  |  | Planned | 1007000 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1245 | 2008-04-07 | 604G6616 | 1958 | 2011-01-11 | LN | 2014-06-01 | Frankfort Jefferson | Potato Creek |  | 69 |  | 153 | 69178 Build 2.7 miles of 954 ACSR 69kV |  | IN |  | 2.7 | Planned | 1087115.23 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1501 | 2007-03-02 | 502G6712 | 2574 | 2009-02-18 | CAP | 2014-06-01 | Carmel 146th St | Capacitor 2 |  | 69 |  | 36 MVAR | Install a 2nd 69kV 36MVAR cap bank |  | IN |  |  | Planned | 624145 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1512 | 2008-10-01 | AMOH0017 | 4270 | 2011-03-25 | LN | 2012-06-01 | Ridgeway | Ashland | 1 | 138 |  | 282 | Install underground 138 kV circuit from Ridgeway to Ashland - expand Ashland sub to complete 138kv ring bus. Build new Ridgeway sub - 138kv-13.1kv | N10 | OH |  | 1.31 | Planned | 1000000 | 2008$, Plan |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1512 | 2008-10-01 | AMOH0017 | 2588 | 2010-09-22 | LN | 2012-12-31 | Rochelle | Ridgeway | 1 | 138 | 13.1 | 282 | Install underground 138 kV circuit from Rochelle - Ridgeway - expand Rochelle sub to complete 138kv ring bus. | N10 | OH |  | 1.04 | Planned | 7802000 | 2008$, Engr |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1512 | 2008-10-01 | 402J9113 | 2939 | 2010-09-22 | TEQ | 2012-12-31 | Red Bank | Ashland | 1 | 138 |  |  | Install 3.8 ohm-1410Amp-138kV reactors in Feeder 7484 at Oakley sub (line runs through Oakley with no connections to other ckts - transitions to UG here) | N10 | OH |  |  | Planned | 832051 | 2008$, Engr |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1513 | 2007-03-02 | 602G6719 | 2589 | 2011-06-23 | CAP | 2011-07-15 | Metea | Capacitor |  | 69 |  | 14.4 MVAR | Install 14.4MVAR 69kV unit | M9 | IN |  |  | Under Construction | 865946 | 2010$, Engr |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1514 | 2007-03-02 | 804H6816 | 3776 | 2011-06-23 | LNrc | 2011-12-31 | Wabash River Station | Burnett Jct | 1 | 138 |  |  | Reconductor the 6-wire 13847 477ACSR underbuild from 976-1005 to 976-1035 (34,000 ft), with 3-wire 954ACSSTW conductor to allow uprating of 23002 line overbuild. Wab Riv to Spelterville to Burnett Jct. | L10 | IN | 6.44 |  | Under Construction | 1286147 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1514 | 2007-03-02 | 804H6816 | 2590 | 2011-06-23 | LN | 2011-12-31 | Wabash River Station | Staunton |  | 230 |  | 478 | Uprate Wabash River to Staunton 23002 to 100C summer operating temperature and 80C winter (559MVA). 478mva/1200A equipment limited - also, have to modify the 13847 underbuild from 6-wired to 954 3-wire | L10 | IN | 18.03 |  | Under Construction | 0 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1519 | 2007-03-02 | 504G6706 | 2595 | 2011-06-23 | LN | 2012-12-31 | Noblesville NE | Geist |  | 69 |  |  | Build a new 69kV line from Noblesville NE sub to tap the Fishers North - Geist 69kV line |  | IN |  |  | Planned | 2640107 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1560 | 2007-06-30 | 802H6857 | 3111 | 2011-06-23 | CAP | 2011-07-15 | Edwardsport | capacitor |  | 138 |  | 57.6 MVAR | Install a 138kV 57.6MVAR capacitor at Edwardsport. | L10 | IN |  |  | Under Construction | 709293 | Engineering 2010$ |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1561 | 2007-06-30 | 602F6500 | 3112 | 2010-09-22 | TEQ | 2012-06-01 | Kokomo Webster St (terminal equipment) | New London | 1 | 230 |  | 797 | Retire existing 1600A circuit switcher and complete the Webster St ring in order to utilize the full capacity of the bundled 477 ACSS wire on the 23016 line. | M9 | IN |  |  | Planned | 399579.8 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1564 | 2007-06-30 | 502H6902 | 3116 | 2011-01-11 | CAP | 2011-12-31 | Roseburg Switching Station | Capacitor |  | 69 |  | 21.6 MVAR | Install 69kV 21.6MVAR std capacitor | M10 | IN |  |  | Planned | 518503 | 2008$, Engr |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1568 | 2007-06-30 | 602H6935 | 3120 | 2009-02-18 | TX | 2013-06-01 | Qualitech | transformer | 1 | 345 | 138 | 300 | Qualitech Sub- Install one 345/138kv, 300Mva Xtr and 2-345kv Bkrs and 1-138kv Bkr to provide second 138kv source to proposed Hendricks Co 138kv system | M9 | IN |  |  | Planned | 4561673.88 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1569 | 2007-06-30 | 604H6936 | 3121 | 2009-02-18 | LN | 2013-06-02 | Qualitech | Pittsboro Jct | 1 | 138 |  | 306 | Construct new 138kv line, Qualitech to Pittsboro Jct, and connect to the Pittsboro-Brownsbg line to provide new 954ACSR outlet line from Qualitech 345/138kV Bank | M9 | IN |  | 3.3 | Planned | 1507855.84 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1570 | 2007-06-30 | 604H6907 | 3122 | 2009-02-18 | LN | 2013-06-03 | Plainfield South | Pittsboro Jct | 1 | 138 |  | 306 | Convert the existing 69KV (69144) line from Plainfield S. to Pittsboro Jct(and 4 distribution subs) over to 138KV operation and connect to the new Qualitech to Pittsboro 138KV line | M9 | IN | 17.6 |  | Planned | 4139000 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1650 | 2007-10-05 | AMIN0064 | 3381 | 2009-02-18 | LNrc | 2014-06-30 | Fairview | HE Fairview | 1 | 138 |  | 306 | Fairview to HE Fairview 13854 Reconductor with 954ACSR @ 100C | M10 | IN | 3.3 |  | Planned | 1236383.93 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1881 | 2008-01-10 | X02P6673 | 3775 | 2010-04-03 | CB | 2011-12-31 | Bloomington Rogers St | Whitehall Pike | 1 | 138 |  | 201 | Bloomington Rogers St - replace 13836 breaker and WT; replace 13871 breaker, WT, and disc sw's - All 2000Amp rated; Replace relays for 13836, 13837, 13871 | M10 | IN |  |  | Planned | 1051992 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1889 | 2011-06-23 | 604B5486 | 3785 | 2011-06-23 | LNup | 2011-06-23 | Danville | Danville Jct | 1 | 69 |  | 153 | Danville to Preswick Jct to Danville Jct - recond. 5.2 mi of the 6945 ckt. with 954acsr OVAL @100C and replace the 600 amp, two way switches at Danville Jct with two 1200 amp one way switches and replace the 600 amp switch at Prestwick Jct with a 1200 amp | M10 | IN | 5.2 |  | Under Construction | 1622359 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1890 | 2008-01-10 | 504G6684 | 3786 | 2011-06-23 | LN | 2011-08-16 | Geist | 69181 Fishers N. Jct (new) | 1 | 69 |  | 153 | Build new 69kV line - 69181 - 4 miles with 954ACSR along 126th St. (completes approx 5.9 mile line section) | M9 | IN |  | 4 | Under Construction | 1977421 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1893 | 2009-01-05 | AMIN0056 | 3789 | 2010-09-22 | LNrc | 2013-06-01 | Mitchell Lehigh Portland | Bedford 25th St | 1 | 69 |  | 100 | Reconductor 10.3 miles of 69kV - 6995 line with 477 ACSR | M10 | IN | 10.3 |  | Planned | 3016000 | Engr |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1895 | 2010-09-22 | AMIN0418 | 3791 | 2010-09-22 | LN | 2013-06-04 | Brownsburg | Avon East | 1 | 138 |  | 306 | Brownsburg to Avon East 138kV Reconductor 2.9 miles of 138kV line with 954 ACSR - AFTER 138KV CONVERSION | M9 | IN | 2.9 |  | Planned | 1433226.94 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | DEM | 1896 | 2008-01-10 | 504H6988 | 3792 | 2009-06-23 | LNup | 2012-06-01 | Connersville 138 sub | Connersville 30th St | 1 | 69 |  | 53 | Uprate to 100C 4/0 acsr sections – 1.2 miles - 6981 ckt | M10 | IN | 1.2 |  | Planned | 16493 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1897 | 2008-01-10 | 604B5492 | 3793 | 2009-02-18 | LNrc | 2012-06-01 | Deedsville | Macy | 1 | 69 |  | 100 | Reconductor Deedsville to Macy section of 6957 circuit with 477ACSR approx 2.5 miles; and replace Macy #1 and #2 - 600A line switches (1955 vintage) with 1200A | M9 | IN | 2.5 |  | Planned | 921919.1 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1899 | 2008-01-10 | 604B5493 | 3795 | 2011-06-23 | LNrc | 2013-12-31 | Macy | Rochester Metals Jct | 1 | 69 |  | 100 | Reconductor Macy to Rochester Metals Jct section of 6957 circuit with 477ACSR - approx 9.1 miles | M9 | IN | 9.1 |  | Planned | 3102711.45 | Engineering |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1901 | 2008-10-01 | 504G6707 | 3797 | 2009-02-18 | LNrc | 2013-06-01 | Noblesville Gen Sta | Noblesville Jct | 1 | 69 |  | 245 | Reconductor 69kV - 6984 & 6916 ckt. Noblesville Plant to Noblesville 8th St. to Noblesville Jct with 954ACSS @ 200C (5.47 miles) | M9 | IN | 5.47 |  | Planned | 1510945.57 | Engr |  |  |  |  | NT | A
A in MTEP08 | Central | DEM | 1902 | 2008-01-10 | 504G6708 | 3799 | 2010-06-25 | LNrc | 2012-06-01 | Zionsville | Zionsville 96th St | 1 | 69 |  | 153 | Reconductor .32 miles of the 69kV - 69155 line from Zionsville 69 sub to Zionsville 96th Jct with 954ACSR conductor; replace/upgrade 69kV switches, jumpers and bus at Zionsvile 69 sub for a min. capacity of 152MVA (502G6709) | M9 | IN | 0.32 |  | Planned | 309475 | Engineering |  |  |  |  | NT | A
A in MTEP07 | Central | DEM | 852 | 2009-01-21 | 604F6348 | 2995 | 2009-06-26 | LN | 2013-06-01 | Linden Ethanol Jct | Tipmont Concord Jct |  | 138 |  | 306 | 13819 reconductor with 954ACSR 100C | L9 | IN | 7.15 |  | Planned | 3567892 | Engineering |  |  | Y |  | Y | A
A in MTEP07 | Central | DEM | 852 | 2009-01-21 | 604F6348 | 1979 | 2009-06-26 | LN | 2013-06-01 | Crawfordsville | Linden Ethanol Jct |  | 138 |  | 306 | 13819 reconductor with 954ACSR 100C | L9 | IN | 10.28 |  | Planned | 5351838 | Engr |  |  | Y |  | Y | A
A in MTEP06 | Central | DEM | 851 | 2005-07-11 | 604F6347 | 826 | 2009-02-18 | LNrc | 2013-06-01 | Lafayette Cumberland Ave | Laf AE Staley | 1 | 138 |  | 306 | 13806 reconductor with 954ACSR 100C 604F6347 | L9 | IN | 1.3 |  | Planned | 349357.4 | Engineering |  |  |  |  | Y | A
A in MTEP06 | Central | DEM | 853 | 2005-07-11 | 604F6352 | 828 | 2007-06-30 | LNrc | 2015-06-01 | West Lafayette | Cumberland Ave | 1 | 138 |  | 306 | 13806 reconductor with 954ACSR 100C 604F6352 | L9 | IN | 2 |  | Planned | 706921.48 | Engineering |  |  |  |  | Y | A
A in MTEP06 | Central | DEM | 1244 | 2006-03-27 | 602G6558 | 1946 | 2009-02-18 | TEQ | 2013-06-01 | Frankfort 23013 Wave Trap | Cayuga |  | 230 |  | 797 | Replace 1600A wave trap with a 2000A wave trap. Increase line rating of the Cayuga to Frankfort 23013 line. |  | IN |  |  | Planned | 98827 | Engineering |  |  |  |  | Y | A
A in MTEP06 | Central | DEM | 1244 | 2006-03-27 | 802G6557 | 1945 | 2009-02-18 | TEQ | 2013-06-01 | Cayuga 23013 Wave Trap | Frankfort |  | 230 |  | 797 | Replace 1600A wave trap with a 2000A wave trap. Increase line rating of the Cayuga to Frankfort 23013 line. |  | IN |  |  | Planned | 68733 | Engineering |  |  |  |  | Y | A
A in MTEP10 | Central | HE | 3080 | 2009-09-15 |  | 5360 | 2011-01-11 | LN | 2011-06-01 | HE Rocklane | DEI | 1 | 69 |  | 72MVA | New Construction |  | IN |  | 3 | Planned | 3000000 | Engineering |  |  |  |  | Y | A
A in MTEP08 | Central | HE | 1927 | 2008-01-10 |  | 3806 | 2011-01-11 | SUB | 2010-09-01 | Hubbell Primary |  | 1 | 138 |  | 2000 AMP | Rebuild |  | IN |  |  | Planned | 3000000 | [5 empty] | Y | A
A in MTEP08 | Central | HE | 1928 | 2008-01-10 |  | 3807 | 2011-01-11 | SUB | 2011-09-01 | Fairview Primary |  | 1 | 138 |  | 2000 AMP | Rebuild |  | IN |  |  | Planned | 1500000 | [5 empty] | Y | A
A in MTEP08 | Central | HE | 1929 | 2008-01-10 |  | 3808 | 2011-01-11 | SUB | 2012-09-01 | Georgetown Primary |  | 1 | 138 |  | 2000 AMP | Rebuild |  | IN |  |  | Planned | 1250000 | [5 empty] | Y | A
A in MTEP08 | Central | HE | 2082 | 2008-02-15 | 803 | 3978 | 2011-01-11 | LN | 2009-09-01 | Shelbyville Intel Park Tapline | Shelbyville Intel Park | 1 | 138 |  |  | New Construction |  | IN |  | 1 | Planned | 250000 | [5 empty] | Y | A
A in MTEP08 | Central | HE | 2082 | 2008-02-15 | 903 | 3979 | 2011-01-11 | SUB | 2009-09-01 | Shelbyville Intel Park |  | 1 | 138 | 12.5 | 2000 AMP | New Construction |  | IN |  |  | Planned | 750000 | [5 empty] | Y | A
A in MTEP08 | Central | HE | 2083 | 2008-02-15 | 913 | 3981 | 2011-01-11 | SUB | 2009-09-01 | Wayne County Indust Park |  | 1 | 69 | 12.5 | 2000 AMP | New Construction |  | IN |  |  | Planned | 500000 | [5 empty] | NT | A
A in MTEP08 | Central | HE | 2083 | 2008-02-15 | 813 | 3980 | 2011-01-11 | LN | 2009-09-01 | Wayne County Indust Park Tap | Wayne County Indust Park | 1 | 69 |  |  | New Construction |  | IN |  | 1 | Planned | 250000 | [5 empty] | NT | A
A in MTEP10 | Central | IPL | 2900 | 2009-09-14 | New3 | 5073 | 2010-01-06 | LN | 2011-06-01 | Northwest | Southwest | 1 | 138 |  | 382 | Increase line rating from 242 to 382 MVA |  | IN | 4.75 |  | Planned | 1500000 | Planning |  |  |  |  | Y | A
A in MTEP09 | Central | IPL | 2053 | 2010-04-05 |  | 5341 | 2010-04-05 | CB | 2012-06-01 | Petersburg | 138 kV breakers |  | 138 |  |  | 6 138 kV Breakers and disconnect switches |  | IN |  |  | Planned | 2000000 | Planning |  |  | N |  | Y | A
A in MTEP09 | Central | IPL | 2053 | 2010-04-05 |  | 3940 | 2010-04-05 | TX | 2012-06-01 | Petersburg | West Autotransformer | W | 345 | 138 |  | Replace autotransformer and 345 kV breaker |  | IN |  |  | Planned | 6700000 | Planning |  |  | Y |  | Y | A
A in MTEP09 | Central | IPL | 2053 | 2010-04-05 |  | 3939 | 2010-04-05 | TX | 2012-06-01 | Petersburg | East Autotransformer | E | 345 | 138 |  | Replace autotransformer and 345 kV breaker |  | IN |  |  | Planned | 6700000 | Planning |  |  | Y |  | Y | A
A in MTEP08 | Central | IPL | 1639 | 2010-04-05 |  | 3301 | 2010-04-05 | CAP | 2013-06-01 | Various Locations | capacitors |  |  |  |  | Add capacitors to IPL General Distribution System |  | IN |  |  | Planned | 50000 | [5 empty] | NT | A
A in MTEP08 | Central | SIPC | 1778 | 2008-08-01 |  | 2871 | 2008-01-10 | LN | 2008-07-01 | Hamilton (SIPC) | Norris (Ameren) |  | 138 |  |  | Construct a 138KV line connecting SIPC Hamilton Substation to Ameren Norris City Substation. This project includes the construction of 18 miles of 138KV line. |  | IL |  |  | Planned | 5000000 | [5 empty] | Y | A
A in MTEP03 | Central | SIPC | 81 | 2011-04-22 |  | 5339 | 2010-12-06 | LN | 2012-09-01 | Carrier Mills | 161/69 kV transformer |  | 161 | 69 |  | New 161/69kV substation located north of Carrier Mills, IL |  | IL |  |  | Planned | 1000000 | [5 empty] | Y | A
A in MTEP09 | Central | Vectren | 2461 | 2011-06-29 | SIGE2 | 4425 | 2011-03-28 | SUB | 2014-06-01 | Dubois Sub Z84 terminals |  | 84 | 138 |  |  | Add 1 new 138kV terminal to existing sub to avoid 3 term line | L11 | IN |  |  | Planned | 1000000 | Budgetary |  |  |  |  | Y | A
A in MTEP09 | Central | Vectren | 2465 | 2011-06-29 | SIGE6 | 4429 | 2011-06-29 | SUB | 2011-10-01 | Leibert Rd 138/12kV Substation |  | 1 | 138 | 12.47 | 16/20 | New 138/12kV Substation for load growth | L11 | IN |  |  | Planned | 2622781 | Detailed eng. Est |  |  |  |  | NT | A
A in MTEP09 | Central | Vectren | 2466 | 2008-10-31 | SIGE7 | 4430 | 2008-10-31 | SUB | 2013-06-01 | Roesner Rd 138/12kV Substation |  | 1 | 138 | 12.47 | 16/20 | New 138/12kV Substation for load growth | L11 | IN |  |  | Planned | 3000000 | Budgetary |  |  |  |  | NT | A
A in MTEP08 | Central | Vectren | 1002 | 2010-04-05 | 6.3 | 1566 | 2011-06-29 | LN | 2012-06-01 | Northeast | Oak Grove | 77 | 138 |  | 287/287 | new line | L11 | IN |  | 5 | Under Construction | 4368926 | Detailed eng. Est |  |  |  |  | Y | A
A in MTEP08 | Central | Vectren | 1782 | 2010-04-05 |  | 3572 | 2011-06-29 | SUB | 2014-12-31 | Northeast Sub Bus reconfig | Substation | 1 | 138 |  |  | Rebuild existing straight bus with more reliable breaker and half scheme | L11 | IN |  |  | Planned | 7000000 | Budgetary |  |  |  |  | Y | A
A in MTEP08 | Central | Vectren | 1784 | 2008-01-10 |  | 3574 | 2011-06-29 | SUB | 2016-06-01 | Jasper#3 Sub Exp-Victory Line | Victory | 1 | 69 |  |  | Extend existing Victory line to new term at existing sub | L11 | IN |  |  | Planned | 3625000 | Budgetary |  |  |  |  | NT | A
A in MTEP08 | Central | Vectren | 1785 | 2010-04-05 |  | 3575 | 2011-03-28 | SUB | 2012-12-31 | Z83 Upgrade NE | Z83 Upgrade NW | 83 | 138 |  |  | Upgrade terminal equipment at NE and NW. | L11 | IN |  |  | Planned | 100000 | [5 empty] | Y | A
A in MTEP08 | Central | Vectren | 1787 | 2008-01-10 |  | 3577 | 2011-01-10 | SUB | 2014-06-01 | Dale Sub | Santa Clause Sub | 75 | 69 |  |  | New 69kV line from Dale Sub to Santa Clause Sub | L11 | IN |  |  | Planned | 5000000 | [5 empty] | NT | A
A in MTEP08 | Central | Vectren | 1788 | 2008-01-10 |  | 3578 | 2011-01-10 | SUB | 2014-06-01 | St. Wendel Sub | Mohr Rd Sub | 34 | 69 |  |  | New 69kV line from St. Wendel Sub to Mohr Rd Sub | L11 | IN |  |  | Planned | 2750000 | [5 empty] | NT | A
A in MTEP08 | Central | Vectren | 1789 | 2008-01-10 |  | 3579 | 2011-03-28 | SUB | 2014-06-01 | Boonville Sub | Boonville Pioneer Sub | 56 | 69 |  |  | New 69kV line from Boonville Sub to Boonville Pioneer Sub | L11 | IN |  |  | Planned | 1400000 | [5 empty] | NT | A
A in MTEP08 | Central | Vectren | 1790 | 2008-01-10 |  | 3580 | 2011-01-10 | SUB | 2014-06-01 | NE Sub | Elliott Sub | 52 | 69 |  |  | Rebuild/Reconductor existing Y52 and loop into Sunbeam | L11 | IN |  |  | Planned | 2550000 | [5 empty] | NT | A
A in MTEP08 | Central | Vectren | 1791 | 2008-01-10 |  | 3581 | 2008-01-10 | SUB | 2012-06-01 | Angel Mound Sub | East Side Sub | 66 | 69 |  |  | Uprate term equipment to increase capacity for Y66-2 | L11 | IN |  |  | Planned | 300000 | [5 empty] | NT | A
A in MTEP06 | Central | Vectren | 1257 | 2010-04-05 | 8.4 8.5 | 1973 | 2011-06-29 | LN | 2012-06-01 | AB Brown | Reid (BREC) | 17 | 345 |  | 1430/1430 | new line | L11 | IN/KY |  | 25.7 | Under Construction | 46284114 | Detailed eng. Est |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 2918 | 2009-09-14 |  | 5087 | 2009-09-14 | CB | 2012-12-31 | Breaker Replacement Program 2012 | Throughout System |  | 345 | 120 |  |  |  | MI |  |  | Planned | 6000000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2919 | 2009-09-14 |  | 5088 | 2009-09-14 | RLY | 2012-12-31 | NERC Relay Loadability Compliance 2012 | Throughout system |  | 345 | 120 |  | Upgrade relay throught system |  | MI |  |  | Planned | 2400000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2920 | 2009-09-14 |  | 5089 | 2009-09-14 | PT | 2012-12-31 | Potential Device Replacement 2012 | Throughout System |  | 345 | 120 |  | Replace aging potential devices |  | MI |  |  | Planned | 300000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2921 | 2009-09-14 |  | 5090 | 2009-09-14 | RLY | 2012-12-31 | Relay Betterment Program 2012 | Throughout System |  | 345 | 120 |  |  |  | MI |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2922 | 2009-09-14 |  | 5091 | 2011-06-30 | LNrb | 2012-12-31 | Wood Pole Replacement 2012 | Throughout System |  | 120 |  |  | Replace deteriorating wood pole |  | MI |  |  | Planned | 4800000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2923 | 2009-09-14 |  | 5092 | 2009-09-14 | CAP | 2012-12-31 | Capacitor Replacement 2012 | Throughout System |  | 120 |  |  | Replace capacitor banks |  | MI |  |  | Planned | 600000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2925 | 2009-09-14 |  | 5094 | 2009-09-14 | Dist | 2011-12-31 | Blanket for Customer Interconnections 2011 | Throughout system |  | 120 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2000000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2926 | 2009-09-14 |  | 5095 | 2009-09-14 | Dist | 2012-12-31 | Blanket for Customer Interconnections 2012 | Throughout system |  | 120 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2000000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2927 | 2009-09-14 |  | 5096 | 2009-09-14 | Dist | 2013-12-31 | Blanket for Customer Interconnections 2013 | Throughout system |  | 120 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2000000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2928 | 2009-09-14 |  | 5097 | 2009-09-14 | Dist | 2014-12-31 | Blanket for Customer Interconnections 2014 | Throughout system |  | 120 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2000000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2929 | 2010-01-06 |  | 5099 | 2010-01-06 | LNup | 2012-12-30 | Ariel (formerly Holland) | Wheeler | 1 | 120 |  |  | Distribution Interconnection to add two new 120/13.2kV transformers at Ariel (formerly Holland). Connects to the Wheeler to Troy 120kV circuit. |  | MI |  | 0.1 | Planned | [6 empty] | Y | A
A in MTEP10 | East | ITC | 2929 | 2010-01-06 |  | 5100 | 2010-01-06 | LNup | 2012-12-30 | Ariel (formerly Holland) | Troy | 1 | 120 |  |  | Distribution Interconnection to add two new 120/13.2kV transformers at Ariel (formerly Holland). Connects to the Wheeler to Troy 120kV circuit. |  | MI | 0.73 | 0.1 | Planned | [6 empty] | Y | A
A in MTEP10 | East | ITC | 2929 | 2010-01-06 |  | 5098 | 2010-01-06 | LN | 2012-12-30 | Ariel (formerly Holland) | Holland | 1 | 120 |  |  | Distribution Interconnection to add two new 120/13.2kV transformers at Ariel (formerly Holland). Connects to the Wheeler to Troy 120kV circuit. |  | MI |  |  | Planned | 2800000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 2930 | 2009-09-14 |  | 5101 | 2009-12-11 | LN | 2015-12-30 | Evergreen | Warren | 1 | 120 |  |  | Upper Rouge to Tap Evergreen Warren 120 kV circuit. Rebuild 0.65 mile of six-wired 477 ACSR Warren-Evergreen 120 kV circuit. |  | MI | 0.65 |  | Planned | 1900000 | [5 empty] | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5581 | 2010-09-16 | LNup | 2013-12-31 | Baker (formerly Reese) | Hampton | 1 | 345 |  |  | Tap the Pontiac to Hampton 345 kV circuit at new Baker site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5984 | 2010-09-16 | LN | 2013-12-31 | Baker (formerly Reese) | Hampton | 2 | 345 |  |  | Tap the Hampton to Thetford 345 kV circuit at new Baker site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5582 | 2010-09-16 | LNup | 2013-12-31 | Baker (formerly Reese) | Pontiac | 1 | 345 |  |  | Tap the Pontiac to Hampton 345 kV circuit at new Baker site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5577 | 2010-09-16 | SUB | 2013-12-31 | Baker (formerly Reese) | switching station |  | 345 |  |  | New Switching Station |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5584 | 2010-09-16 | LNup | 2013-12-31 | Baker (formerly Reese) | Thetford | 1 | 345 |  |  | Tap the Tittabawassee to Thetford (via Manning) 345 kV circuit at new Baker site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5983 | 2010-09-16 | LN | 2013-12-31 | Baker (formerly Reese) | Thetford | 2 | 345 |  |  | Tap the Hampton to Thetford 345 kV circuit at new Baker site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5583 | 2010-09-16 | LNup | 2013-12-31 | Baker (formerly Reese) | Tittabawassee (via Manning) | 1 | 345 |  |  | Tap the Tittabawassee to Thetford (via Manning) 345 kV circuit at new Baker site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5596 | 2010-09-16 | LNup | 2015-12-31 | Fitz (formerly Saratoga) | Belle River | 1 | 345 |  |  | Tap the three ended Belle River to Greenwood to Pontiac 345 kV circuit at new Fitz site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5597 | 2010-09-16 | LNup | 2015-12-31 | Fitz (formerly Saratoga) | Belle River | 2 | 345 |  |  | Tap the Belle River to Blackfoot 345 kV circuit at new Fitz site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5598 | 2010-09-16 | LNup | 2015-12-31 | Fitz (formerly Saratoga) | Blackfoot | 1 | 345 |  |  | Tap the Belle River to Blackfoot 345 kV circuit at new Fitz site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5595 | 2010-09-16 | LNup | 2015-12-31 | Fitz (formerly Saratoga) | Pontiac | 1 | 345 |  |  | Tap the three ended Belle River to Greenwood to Pontiac 345 kV circuit at new Fitz site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5587 | 2010-09-16 | SUB | 2015-12-31 | Fitz (formerly Saratoga) | switching station |  | 345 |  |  | New Switching Station |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5592 | 2010-09-16 | LNup | 2015-12-31 | Greenwood | Fitz (formerly Saratoga) | 1 | 345 |  |  | Tap the three ended Belle River to Greenwood to Pontiac 345 kV circuit at new Fitz site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5593 | 2010-09-16 | LN | 2015-12-31 | Greenwood | Fitz (formerly Saratoga) | 2 | 345 |  |  | New 345 kV circuit |  | MI |  | 19 | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5594 | 2010-09-16 | LN | 2015-12-31 | Greenwood | Fitz (formerly Saratoga) | 3 | 345 |  |  | New 345 kV circuit |  | MI |  | 19 | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5588 | 2010-09-16 | SUB | 2015-12-31 | Greenwood | sub expansion |  | 345 |  |  | Add two new rows to existing Greenwood 345 kV substation |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5585 | 2010-09-16 | LN | 2013-12-31 | Rapson (formerly Wyatt) | Baker (formerly Reese) | 1 | 345 |  |  | New 345 kV circuit |  | MI |  | 56 | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5586 | 2010-09-16 | LN | 2013-12-31 | Rapson (formerly Wyatt) | Baker (formerly Reese) | 2 | 345 |  |  | New 345 kV circuit |  | MI |  | 56 | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5589 | 2010-09-16 | LN | 2015-12-31 | Rapson (formerly Wyatt) | Greenwood | 1 | 345 |  |  | New 345 kV circuit |  | MI |  | 65 | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5590 | 2010-09-16 | LN | 2015-12-31 | Rapson (formerly Wyatt) | Greenwood | 2 | 345 |  |  | New 345 kV circuit |  | MI |  | 65 | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5986 | 2010-09-16 | LN | 2013-12-31 | Rapson (formerly Wyatt) | Harbor Beach | 1 | 120 |  |  | Tap the Wyatt to Harbor Beach 120 kV circuit at new Rapson site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 6104 | 2010-09-16 | LN | 2013-12-31 | Rapson (formerly Wyatt) | Seaside | 1 | 120 |  |  | Tap the Wyatt to Seaside 120 kV circuit at new Rapson site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5988 | 2010-09-01 | Tap | 2013-12-31 | Rapson (formerly Wyatt) | Seaside | 1 | 120 |  |  | Tap the Wyatt to Seaside 120 kV circuit at new Rapson site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5578 | 2010-09-16 | SUB | 2013-12-31 | Rapson (formerly Wyatt) | switching station |  | 345 | 120 |  | New Switching Station |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 6101 | 2010-09-16 | LN | 2013-12-31 | Rapson (formerly Wyatt) | Wyatt | 1 | 120 |  |  | Tap the Wyatt to Harbor Beach 120 kV circuit at new Rapson site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5985 | 2010-09-01 | Tap | 2013-12-31 | Rapson (formerly Wyatt) | Wyatt | 1 | 120 |  |  | Tap the Wyatt to Harbor Beach 120 kV circuit at new Rapson site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5987 | 2010-09-16 | LN | 2013-12-31 | Rapson (formerly Wyatt) | Wyatt | 2 | 120 |  |  | Tap the Wyatt to Seaside 120 kV circuit at new Rapson site |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5579 | 2010-09-16 | TX | 2013-12-31 | Rapson (formerly Wyatt) 345 kV | Rapson (formerly Wyatt) 120 kV | 1 | 345 | 120 |  | New 345/120 kV transformer |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5580 | 2010-09-16 | TX | 2013-12-31 | Rapson (formerly Wyatt) 345 kV | Rapson (formerly Wyatt) 120 kV | 2 | 345 | 120 |  | New 345/120 kV transformer |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5591 | 2010-09-01 | TX | 2015-12-31 | Sandusky 345 kV | Sandusky 120 kV | 1 | 345 | 120 |  | New 345/120 kV transformer |  | MI |  |  | Planned |  |  |  |  | Y | Y | Y | A
A in MTEP10 | East | ITC | 3168 | 2011-07-18 | 13 MVPP1 | 5599 | 2010-09-16 | LN | 2015-12-31 | Total project cost estimate | [5 empty] | Costs from ITC report to Michigan Wind Zones Board and the Michigan Public Service Commission dated November 30, 2009 |  | MI |  |  | Planned | 510000000 |  |  |  | Y | Y | Y | A
A in MTEP09 | East | ITC | 1872 | 2008-12-09 |  | 3763 | 2011-06-30 | LNup | 2013-06-01 | ScioTP | Spruce | 1 | 120 |  | 313 MVA | Scio Taps the Lark-Spruce 120kV circuit |  | MI |  |  | Planned | [6 empty] | Y | A
A in MTEP09 | East | ITC | 1872 | 2008-12-09 |  | 3764 | 2011-06-30 | LN | 2013-06-01 | ScioTP | Scio | 1 | 120 |  | 343 MVA | Scio Taps the Lark-Spruce 120kV circuit |  | MI |  |  | Planned | 3000000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 1872 | 2008-12-09 |  | 3762 | 2011-06-30 | LNup | 2013-06-01 | ScioTP | Lark | 1 | 120 |  | 249 MVA | Scio Taps the Lark-Spruce 120kV circuit |  | MI |  |  | Planned | [6 empty] | Y | A
A in MTEP09 | East | ITC | 2519 | 2008-12-09 |  | 4526 | 2008-10-31 | CB | 2011-12-31 | Breaker Replacement Program 2011 | Throughout System | [6 empty] | MI |  |  | Planned | 5650000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2520 | 2008-12-09 |  | 4527 | 2008-10-31 | TEQ | 2011-12-31 | Cable Termination Replacement 2011 | Throughout System | [6 empty] | MI |  |  | Planned | 3000000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2521 | 2008-12-09 |  | 4528 | 2008-10-31 | RLY | 2011-12-31 | Relay Betterment Program 2011 | Throughout System | [6 empty] | MI |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2525 | 2008-12-09 |  | 4531 | 2008-10-31 | CAP | 2011-12-31 | Capacitor Replacement 2011 | Throughout System |  |  |  |  | Replace capacitor banks |  | MI |  |  | Planned | 565000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2528 | 2008-12-09 |  | 4534 | 2008-10-31 | PT | 2011-12-31 | Potential Device Replacement 2011 | Throughout System |  |  |  |  | Replace aging potential devices |  | MI |  |  | Planned | 300000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2531 | 2008-12-09 |  | 4537 | 2008-10-31 | Sub | 2011-12-31 | Power Plant Control Relocation 2011 | Throughout System |  |  |  |  | Relocate substation controls currently located in power plants control rooms |  | MI |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2534 | 2008-12-09 |  | 4540 | 2011-06-30 | LNrb | 2011-12-31 | Wood Pole Replacement 2011 | Throughout System |  |  |  |  | Replace deteriorating wood pole |  | MI |  |  | Planned | 9000000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2537 | 2008-12-09 |  | 4543 | 2008-10-31 | Sync | 2011-12-31 | Synchronizing Sites 2011 | Throughout System |  |  |  |  | New 120kV synchronizing sites |  | MI |  |  | Planned | 565000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2539 | 2008-12-09 |  | 4545 | 2008-10-31 | RLY | 2011-12-31 | NERC Relay Loadability Compliance 2011 | Throughout system |  | 120 |  |  | Upgrade relay throught system |  | MI |  |  | Planned | 2250000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2541 | 2008-12-09 |  | 4547 | 2011-06-30 | INS | 2011-07-22 | Hunters Creek - Robin - Wabash |  |  | 120 |  |  | Install double shield wire |  | MI |  |  | Under Construction | 2400000 | [5 empty] | Y | A
A in MTEP09 | East | ITC | 2545 | 2008-10-31 |  | 4552 | 2009-05-27 | RLY | 2011-09-01 | Navarre |  |  | 120 |  |  | Relay modifications |  | MI |  |  | Planned | 640000 | [5 empty] | Y | A
A in MTEP08 | East | ITC | 1870 | 2008-08-04 |  | 3757 | 2011-06-30 | LNup | 2013-06-01 | ClydeTP | Placid | 1 | 120 |  | 343 MVA | Clyde taps the Placid-Durant 120kV circuit |  | MI | 11.5 |  | Planned | [6 empty] | Y | A
A in MTEP08 | East | ITC | 1870 | 2008-08-04 |  | 3758 | 2011-06-30 | LNup | 2013-06-01 | ClydeTP | Durant | 1 | 120 |  | 343 MVA | Clyde taps the Placid-Durant 120kV circuit |  | MI | 6.6 |  | Planned | [6 empty] | Y | A
A in MTEP08 | East | ITC | 1870 | 2008-08-04 |  | 3759 | 2011-06-30 | LN | 2013-06-01 | ClydeTP | Clyde | 1 | 120 |  | 343 MVA | Clyde taps the Placid-Durant 120kV circuit |  | MI |  | 3.3 | Planned | 2750000 | [5 empty] | Y | A
A in MTEP08 | East | ITC | 1873 | 2008-01-10 |  | 3765 | 2011-03-28 | LN | 2013-05-31 | Tahoe | Wixom | 1 | 120 |  | 351 MVA | Creates at new Tahoe-Wixom 120kV;constructs 2.6 miles of 120 kV line circuit |  | MI |  | 2.6 | Planned | 2800000 | [5 empty] | Y | A
A in MTEP06 | East | ITC | 1308 | 2008-10-01 | ITC30 | 2141 | 2011-06-30 | PAR | 2011-09-30 | Bunce Creek PAR |  | 1 | 220 |  |  |  | N7 | MI |  |  | Planned | 25000000 | [5 empty] | Y | A
A in MTEP06 | East | ITC | 1310 | 2008-10-01 | ITC31 | 2159 | 2011-06-30 | CB | 2011-09-30 | St. Clair 120 kV pos. HS | circuit breaker |  | 120 |  |  | CB replacement | O7 | MI |  |  | Planned | 150000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2502 | 2009-09-25 |  | 4502 | 2009-09-25 | IND | 2011-12-31 | McGulpin |  |  | 138 |  |  | Install 15 MVAR shunt reactor at McGulpin |  | MI |  |  | Planned | 3000000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2903 | 2009-09-14 |  | 5380 | 2009-12-01 | BAT | 2012-12-31 | Various | [5 empty] | Replace batteries and chargers |  | MI |  |  | Planned | 300000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2904 | 2009-09-14 |  | 5381 | 2009-12-01 | CB | 2012-12-31 | Various | [5 empty] | Breaker replacement |  | MI |  |  | Planned | 6000000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2905 | 2009-09-14 |  | 5382 | 2009-12-01 | RLY | 2012-12-31 | Various | [5 empty] | Relay loadability |  | MI |  |  | Planned | 2400000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2906 | 2009-09-14 |  | 5383 | 2009-12-01 | RLY | 2012-12-31 | Various | [5 empty] | Potential device replacement |  | MI |  |  | Planned | 300000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2907 | 2009-09-14 |  | 5384 | 2009-12-01 | Sub | 2012-12-31 | Various | [5 empty] | Plant control relocation |  | MI |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2908 | 2009-09-14 |  | 5385 | 2009-12-01 | RLY | 2012-12-31 | Various | [5 empty] | Relay replacement |  | MI |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2909 | 2009-09-14 |  | 5078 | 2009-09-14 | LNup | 2012-12-31 | Sag clearance 2012 | Throughout system |  | 345 | 138 |  | Review and correct NESC code violations |  | MI |  |  | Planned | 3600000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2910 | 2009-09-14 |  | 5079 | 2011-06-30 | LNrb | 2012-12-31 | Wood Pole Replacement 2012 | Throughout system |  | 138 |  |  | Replace deteriorating wood pole |  | MI |  |  | Planned | 4800000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2912 | 2009-09-14 |  | 5081 | 2010-09-28 | Dist | 2011-12-31 | Blanket for Customer Interconnections 2011 | Throughout system |  | 138 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2500000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2913 | 2009-09-14 |  | 5082 | 2010-09-28 | Dist | 2012-12-31 | Blanket for Customer Interconnections 2012 | Throughout system |  | 138 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2500000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2914 | 2009-09-14 |  | 5083 | 2011-01-11 | Dist | 2013-12-31 | Blanket for Customer Interconnections 2013 | Throughout system |  | 138 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2500000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2915 | 2009-09-14 |  | 5084 | 2010-09-28 | Dist | 2014-12-31 | Blanket for Customer Interconnections 2014 | Throughout system |  | 138 |  |  | Connect interconnecting entities as requested |  | MI |  |  | Planned | 2500000 | [5 empty] | Y | A
A in MTEP10 | East | METC | 2916 | 2010-07-21 |  | 5085 | 2011-06-30 | LN | 2012-06-01 | Livingston | Vanderbilt |  | 138 |  |  | Rebuild 9.7 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. |  | MI | 9.7 |  | Planned | 12734400 |  |  |  | Y |  | Y | A
A in MTEP10 | East | METC | 2917 | 2009-09-14 |  | 5086 | 2011-06-30 | LN | 2011-11-30 | David Jct | Bingham |  | 138 |  |  | Improve sag clearance by replacing 16 wood poles with 138 kV FDC steel poles. |  | MI |  |  | Planned | 1216860 | [5 empty] | Y | A
A in MTEP10 | East | METC | 3073 | 2011-01-10 | 3073 | 5437 | 2010-09-28 | BUS | 2011-12-31 | TC East Substation | TC East Substation |  | 138 |  |  | New 3 breaker switching station and 0.25 mile 954 ACSR line |  | MI |  |  | Planned | 4913791 |  |  |  | N |  | Y | A
A in MTEP09 | East | METC | 646 | 2010-04-03 | 86 | 1329 | 2010-06-28 | LNcnv | 2011-12-01 | Edenville J. | Warren | 1 | 138 |  |  | Replace poles on half of the Edenville Jct.-Warren 138kV line, prebuilt to 230kV | M6 | MI | 7.8 |  | Planned | 6000000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 646 | 2010-04-03 | 86 | 4967 | 2010-06-28 | LNcnv | 2012-12-01 | Edenville J. | Warren | 1 | 138 |  |  | Replace poles on half of the Edenville Jct.-Warren 138kV line, prebuilt to 230kV | M6 | MI | 7 |  | Planned | 6500000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 |  | 3596 | 2011-06-30 | LNup | 2013-06-01 | Weeds Lake | N_AVE |  | 138 |  |  | line extention on MILHAM to N_AVE circuit N_AVE side |  | MI |  |  | Planned | 5010000 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 |  | 3593 | 2011-06-30 | LNup | 2013-06-01 | Weeds Lake | BRONCO |  | 138 |  |  | line extention on BRONCO 12th ST circuit BRONCO side |  | MI |  |  | Planned | 5010000 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 |  | 3592 | 2011-06-30 | TX | 2013-06-01 | Weeds lake 345/138 kV | Transformer |  | 345 | 138 |  | transformer |  | MI |  |  | Planned | 23365447 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 |  | 3595 | 2011-06-30 | LNup | 2013-06-01 | Weeds Lake | 12th ST |  | 138 |  |  | line extention on BRONCO to 12th ST circuit 12TST side |  | MI |  |  | Planned | 5010000 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 |  | 3594 | 2011-06-30 | LNup | 2013-06-01 | Weeds Lake | MILHAM |  | 138 |  |  | line extention on MILHAM to N_AVE circuit MILHAM side |  | MI |  |  | Planned | 5010000 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 | 117 | 1350 | 2011-06-30 | SwSta | 2013-06-01 | Weeds Lake 138 kV | BRONCO to 12th ST |  | 138 |  |  | tapping BRONCO to 12TST circuit into Weeds Lake | M7 | MI |  |  | Planned | 810505 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 662 | 2009-07-16 |  | 3597 | 2011-06-30 | SwSta | 2013-06-01 | Weeds Lake Jct | MILHAM to N_AVE |  | 345 |  |  | tapping MILHAM to N_AVE circuit into weeds lake |  | MI |  |  | Planned | 810505 |  |  |  | Y |  | Y | A
A in MTEP09 | East | METC | 1810 | 2009-06-26 |  | 3634 | 2010-09-28 | LNrc | 2011-12-31 | East Tawas | Iosco | 1 | 138 |  |  | Rebuild 12 miles of 138kV to 954 ACSR. |  | MI | 80 |  | Planned | 9818854 | [5 empty] | Y | A
A in MTEP09 | East | METC | 1833 | 2008-12-09 |  | 2880 | 2008-10-31 | LNup | 2011-12-31 | Sag clearance 2011 | Throughout system | [6 empty] | MI |  |  | Planned | 3400000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2475 | 2008-10-31 |  | 4461 | 2010-01-06 | SwSta | 2015-06-01 | Doans | Beals | 1 | 138 |  |  | New 138kV switching station at Titus Lake junction. |  | MI |  |  | Planned | 2100000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2475 | 2008-10-31 |  | 4462 | 2010-01-06 | SwSta | 2015-06-01 | Doans | Hazelwood | 1 | 138 |  |  | New 138kV switching station at Titus Lake junction. |  | MI |  |  | Planned | 2100000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2478 | 2010-09-28 |  | 4466 | 2011-03-28 | TAP | 2012-05-31 | Capital Ave | Battle Creek | 1 | 138 |  |  | Capital Ave taps the Battle Creek-Verona 138kV circuit #2. |  | MI |  |  | Planned | 89094 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2478 | 2010-09-28 |  | 4467 | 2011-03-28 | TAP | 2012-05-31 | Capital Ave | Battle Creek | 1 | 138 |  |  | Capital Ave taps the Battle Creek-Verona 138kV circuit #2. |  | MI |  |  | Planned | 89094 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2481 | 2008-12-09 |  | 4470 | 2009-09-25 | TAP | 2012-06-01 | Forest Grove | Campbell | 1 | 138 |  |  | Forest Grove taps the Campbell-Hudsonville (toward Ransom) 138kV circuit |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2481 | 2008-12-09 |  | 4471 | 2009-09-25 | TAP | 2012-06-01 | Forest Grove | Hudsonville | 1 | 138 |  |  | Forest Grove taps the Campbell-Hudsonville (toward Ransom) 138kV circuit |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2482 | 2008-10-31 |  | 4472 | 2011-03-28 | TAP | 2013-05-31 | Hawthorne | Four Mile | 1 | 138 |  |  | Hawthorne taps the Four Mile-Pingree (toward Blendon) 138kV circuit |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2482 | 2008-10-31 |  | 4473 | 2011-03-28 | TAP | 2013-05-31 | Hawthorne | Pingree | 1 | 138 |  |  | Hawthorne taps the Four Mile-Pingree (toward Blendon) 138kV circuit |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2483 | 2008-10-31 |  | 4474 | 2011-03-28 | TAP | 2012-05-31 | Maines Road | Marshall | 1 | 138 |  |  | Maines Road taps the Marshall-Blackstone 138kV circuit |  | MI |  |  | Planned | 88193 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2483 | 2008-10-31 |  | 4475 | 2011-03-28 | TAP | 2012-05-31 | Maines Road | Blackstone | 1 | 138 |  |  | Maines Road taps the Marshall-Blackstone 138kV circuit |  | MI |  |  | Planned | 88193 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2484 | 2008-10-31 |  | 4476 | 2011-03-28 | TAP | 2012-05-31 | Scenic Lake | Cornell | 1 | 138 |  |  | Scenic Lake taps the Cornell-Tihart 138kV circuit |  | MI |  |  | Planned | 88193 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2484 | 2008-10-31 |  | 4477 | 2011-03-28 | TAP | 2012-05-31 | Scenic Lake | Tihart | 1 | 138 |  |  | Scenic Lake taps the Cornell-Tihart 138kV circuit |  | MI |  |  | Planned | 88193 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2485 | 2008-12-09 |  | 4478 | 2011-03-28 | RLY | 2013-06-01 | Ransom | Buck Creek | 1 | 138 |  |  | Relay modifications |  | MI |  |  | Planned | 12000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2486 | 2008-10-31 |  | 4479 | 2011-03-28 | TAP | 2014-05-31 | Haakwood | Rondo | 1 | 138 |  |  | Haakwood taps the Rondo-Vanderbilt section of the Riggsville-Livingston 138kV line. |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2486 | 2008-10-31 |  | 4480 | 2011-03-28 | TAP | 2014-05-31 | Haakwood | Vanderbilt | 1 | 138 |  |  | Haakwood taps the Rondo-Vanderbilt section of the Riggsville-Livingston 138kV line. |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2487 | 2008-12-09 |  | 4482 | 2008-10-31 | TAP | 2012-06-30 | Birchwood | Kraft | 1 | 138 |  |  | Birchwood taps the Spaulding-Kraft section of the Spaulding-Plaster Creek 138kV circuit |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2487 | 2008-12-09 |  | 4481 | 2008-10-31 | TAP | 2012-06-30 | Birchwood | Spaulding | 1 | 138 |  |  | Birchwood taps the Spaulding-Kraft section of the Spaulding-Plaster Creek 138kV circuit |  | MI |  |  | Planned | 85000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2489 | 2010-04-03 |  | 4485 | 2011-06-30 | TEQ | 2011-09-30 | Tippy | terminal equipment |  | 138 |  |  | Terminal equipment upgrade at Tippy on the Tippy-Keystone 138kV line. |  | MI |  |  | Planned | 60215 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2492 | 2008-12-09 |  | 4490 | 2008-10-31 | TEQ | 2013-06-01 | Battle Creek |  |  | 138 |  |  | Terminal equipment upgrade |  | MI |  |  | Planned | 100000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2492 | 2008-12-09 |  | 4491 | 2008-10-31 | TEQ | 2013-06-01 | Verona |  |  | 138 |  |  | Terminal equipment upgrade |  | MI |  |  | Planned | 100000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2496 | 2008-12-09 |  | 4943 | 2009-06-26 | TEQ | 2013-06-01 | Bullock | Tittabawassee |  | 138 |  |  | Terminal equipment upgrade at Bullock |  | MI |  |  | Planned | 220000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2496 | 2008-12-09 |  | 4496 | 2008-10-31 | TEQ | 2013-06-01 | Tittabawassee |  |  | 138 |  |  | Terminal equipment upgrade |  | MI |  |  | Planned | 140000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2498 | 2008-12-09 |  | 4800 | 2008-12-05 | CB | 2011-12-31 | Breaker replacement program | 2011 | [6 empty] | MI |  |  | Planned | 5650000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2499 | 2008-12-09 |  | 4827 | 2008-12-10 | CB | 2011-12-31 | Relay Betterment Program 2011 | Throughout system | [6 empty] | MI |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2501 | 2008-12-09 |  | 4500 | 2011-03-28 | CAP | 2012-06-01 | Keystone | [5 empty] | Install 50.4 MVAR capacitor |  | MI |  |  | Planned | 740323 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2501 | 2008-12-09 |  | 4501 | 2011-03-28 | CAP | 2012-06-01 | Plum | [5 empty] | Install 25.2 MVAR capacitor |  | MI |  |  | Planned | 435484 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2501 | 2008-12-09 |  | 4499 | 2011-03-28 | CAP | 2012-06-01 | New site (Wexford prime) | [5 empty] | Install 25.2 MVAR capacitor |  | MI |  |  | Planned | 1524194 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2507 | 2009-06-26 |  | 4510 | 2009-06-26 | LNcnv | 2013-06-01 | Alcona | Mio | 1 | 138 |  |  | Rebuild the Twining-Mio 138kV line to 954 ACSR future-double-circuit (pre-built to 230kV) |  | MI | 20 |  | Planned | 24500000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2510 | 2008-12-09 |  | 4513 | 2011-06-30 | LNrb | 2011-12-31 | Wood Pole Replacement 2011 | Throughout system |  | 138 |  |  | Replace deteriorating wood pole |  | MI |  |  | Planned | 6000000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2515 | 2009-06-26 |  | 4518 | 2010-09-28 | LNrb | 2011-08-01 | Oakland | Dean | 1 | 138 |  |  | Replace wood structures |  | MI |  |  | Planned | 3774325 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2515 | 2009-06-26 |  | 4521 | 2010-09-28 | LNrb | 2011-08-01 | Latson | Tihart | 1 | 138 |  |  | Replace wood structures |  | MI |  |  | Planned | 11804805 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2515 | 2009-06-26 |  | 4522 | 2010-09-28 | LNrb | 2011-08-01 | Genoa | Latson (METC side) | 1 | 138 |  |  | Replace wood structures |  | MI |  |  | Planned | 1124267 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2515 | 2009-06-26 |  | 4520 | 2010-09-28 | LNrb | 2011-08-01 | Dean | Latson | 1 | 138 |  |  | Replace wood structures |  | MI |  |  | Planned | 2168230 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2517 | 2008-10-31 |  | 4524 | 2008-10-31 | RLY | 2011-12-31 | NERC Relay Loadability Compliance 2011 | Throughout system |  | 138 |  |  | Upgrade relay throught system |  | MI |  |  | Planned | 2250000 | [5 empty] | Y | A
A in MTEP09 | East | METC | 2522 | 2010-04-03 |  | 4801 | 2010-09-28 | Sub | 2011-12-31 | Power Plant Control Relocation 2011 | Throughout System |  |  |  |  | Relocate substation controls currently located in power plants control rooms |  |  |  |  | Planned | 1200000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1448 | 2006-10-25 | 196 | 2452 | 2010-04-03 | Dist | 2016-06-01 | Simpson 138kV |  |  | 138 | 12.5 |  | Install a second distribution transformer at Simpson (Simpson) |  | MI |  |  | Planned | 2200000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1655 | 2007-10-26 |  | 3406 | 2011-03-28 | CB | 2011-12-31 | Weadock 138kV | Breaker 500 |  | 138 |  |  |  |  | MI |  |  | Planned | 160000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1655 | 2007-10-26 |  | 3404 | 2011-03-28 | CB | 2011-12-31 | Weadock 138kV | Breaker 388 |  | 138 |  |  |  |  | MI |  |  | Planned | 160000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1655 | 2007-10-26 |  | 3403 | 2011-03-28 | CB | 2011-12-31 | Weadock 138kV | Breaker 288 |  | 138 |  |  |  |  | MI |  |  | Planned | 160000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1796 | 2008-08-04 |  | 3605 | 2010-09-28 | LNrc | 2011-12-31 | Twining | Almeda | 1 | 138 |  |  | Reconductor |  | MI | 22 |  | Planned | 22819200 |  |  |  | Y |  | Y | A
A in MTEP08 | East | METC | 1814 | 2008-01-10 |  | 3648 | 2011-06-30 | LNrc | 2012-12-31 | Tippy | Chase | 1 | 138 |  |  | Reconductor |  | MI | 30 |  | Planned | 26970000 |  |  |  | Y |  | Y | A
A in MTEP08 | East | METC | 1820 | 2008-08-04 |  | 2872 | 2011-03-28 | RLY | 2011-12-31 | METC Communication and Relaying Upgrade | Throughout system | [6 empty] | MI |  |  | Planned | 10000000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1834 | 2008-01-10 |  | 3695 | 2009-06-26 | LN | 2011-12-15 | Tirrell Road | Battle Creek | 1 | 138 |  |  | Tirrel Rd. taps the Battle Creek-Cochran 138kV circuit |  | MI |  |  | Planned | 100000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1834 | 2008-01-10 |  | 3696 | 2009-06-26 | LN | 2011-12-15 | Tirrell Road | Cochran Jct. | 1 | 138 |  |  | Tirrel Rd. taps the Battle Creek-Cochran 138kV circuit |  | MI |  |  | Planned | 100000 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1841 | 2008-08-04 |  | 3709 | 2011-03-28 | LN | 2012-05-31 | Eagles Landing | East Tawas | 1 | 138 |  |  | Eagles Landing Taps the Cottage Grove - East Tawas 138kV circuit |  | MI |  |  | Planned | 89094 | [5 empty] | Y | A
A in MTEP08 | East | METC | 1841 | 2008-08-04 |  | 3708 | 2011-03-28 | LN | 2012-05-31 | Eagles Landing | Cottage Grove | 1 | 138 |  |  | Eagles Landing Taps the Cottage Grove - East Tawas 138kV circuit |  | MI |  |  | Planned | 89094 | [5 empty] | Y | A
A in MTEP06 | East | METC | 988 | 2010-01-06 | 120 | 1551 | 2011-06-30 | LN | 2011-12-31 | Simpson | Batavia | 1 | 138 |  |  |  |  | MI |  | 30 | Planned | 37100000 |  |  |  | Y |  | Y | A
A in MTEP06 | East | METC | 1408 | 2008-12-09 | 158 | 2411 | 2011-06-30 | RTU | 2013-06-30 | RTU/SCADA upgrades | Throughtout System |  | 345 | 138 |  | Install and/or upgrade numerous RTU/SCADA points |  | MI |  |  | Under Construction | 801000 | [5 empty] | Y | A
A in MTEP06 | East | METC | 1434 | 2006-10-25 | 182 | 2438 | 2010-04-03 | SUB | 2014-06-01 | Spaulding 138kV |  |  | 138 |  |  | Install bulk substation served from the Spaulding 138kV ring bus (Five Mile) |  | MI |  |  | Planned | 750000 | [5 empty] | Y | A
A in MTEP06 | East | METC | 1445 | 2006-10-25 | 193 | 2449 | 2010-04-03 | Dist | 2016-12-31 | Emmet 138kV | distribution |  | 138 |  |  | Install a second distribution transformer at Emmet (Emmet) |  | MI |  |  | Planned | 2750000 | [5 empty] | Y | A
A in MTEP06 | East | METC | 1447 | 2006-10-25 | 195 | 2451 | 2008-06-30 | SUB | 2012-06-01 | Eureka 138kV | Vestaburg 138kV | 1 | 138 |  |  | Install bulk substation served from the Eureka-Deja-Vestaburg 138kV Line (Horseshoe Creek/Deja) |  | MI |  |  | Planned | 2200000 | [5 empty] | Y | A
A in MTEP10 | East | MPPA | 3073 | 2011-01-10 | 17-2 | 5377 | 2011-01-10 | BUS | 2012-12-31 | TC East Substation | TC East Substation |  | 138 | 69 | 90/150 MVA | New 138/69kV substation interconnection |  | MI |  |  | Planned | 3500000 |  |  |  | N |  | Y | A
A in MTEP10 | East | MPPA | 3074 | 2011-01-10 | 17-3 | 5378 | 2011-01-10 | LNrc | 2012-12-31 | TC East Substation | Parsons Sub |  | 69 |  | 108/140 MVA | New 69kV line construction |  | MI |  | 4.1 | Planned | 1600000 | [5 empty] | Y | A
A in MTEP10 | East | NIPS | 2322 | 2009-09-14 | 71C7407 | 4248 | 2010-09-15 | TX | 2011-06-01 | Green Acres | Transformer |  | 345 | 138 | 560 | Install a 560 MVA 345/138 kV transformer, (1) 345 kV and (1) 138 kV circuit breaker and associated equipment at Green Acres Substation. |  | IN |  |  | Planned | 7417000 | 09, Engineering |  |  | Y |  | Y | A
A in MTEP08 | East | NIPS | 1996 | 2009-09-14 | 9326166 | 2786 | 2010-09-15 | LNrb | 2012-12-01 | Angola | Switch #644 | 1 | 69 |  | 81 | Circuit 6980 - Reconductor 2/0 CU to 336.4kcm ACSR |  | IN | 12 |  | Under Construction | 2465948 | Engineering |  |  |  |  | Y | A
A in MTEP08 | East | NIPS | 1997 | 2009-04-01 | X7L6304 | 2787 | 2010-06-28 | LNrc | 2015-12-01 | Goshen Junction | Model Tap | 1 | 69 |  | 81 | Circuit 6977 - Reconductor 4/0 CU to 336.4kcm ACSR |  | IN | 1.5 |  | Planned | 357000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3060 | 2011-01-11 | Morley Cap. Bank | 5335 | 2011-01-11 | CAP | 2020-12-31 | Morley | Capacitor Bank |  | 69 |  |  | Install a Capacitor Bank |  | MI |  |  | Planned | 260000 | 2009$ |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3061 | 2009-11-20 | Tremaine Tap | 5337 | 2011-01-11 | TAP | 2012-06-01 | Tremaine | Lowell Junction | 1 | 69 |  |  | Tremaine taps the Portland to Burnips Circuit near Lowell Junction - Install a tap pole and disconnect switches |  | MI |  |  | Planned | 100000 | Planning |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3061 | 2009-11-20 | Tremaine Tap | 5336 | 2011-01-11 | TAP | 2012-06-01 | Portland | Tremaine | 1 | 69 |  |  | Tremaine taps the Portland to Burnips Circuit near Lowell Junction - Install a tap pole and disconnect switches |  | MI |  |  | Planned | 100000 | Planning |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3062 | 2009-11-20 | Blendon Xfmr | 5326 | 2009-11-20 | TX | 2013-12-31 | Blendon 138kV | Blendon 69kV | 1 | 138 | 69 | 150MVA | Replace with a 90MVA Transformer |  | MI |  |  | Planned | 3750000 | Planning |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3063 | 2011-03-17 | RW-BB | 5327 | 2011-06-23 | LNrb | 2011-12-31 | Redwood | Baseline | 1 | 69 |  | 143.4MVA | Rebuild to 795ACSS |  | MI | 6.12 |  | Under Construction | 2500000 | 2010$ |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3068 | 2011-01-11 | S. Boardman Cap. Bank | 5332 | 2011-01-11 | CAP | 2014-12-31 | South Boardman | Capacitor Bank |  | 69 |  |  | Install a Capacitor Bank |  | MI |  |  | Planned | 260000 | 2009$ |  |  |  |  | Y | A
A in MTEP10 | EAST | WPSC | 3069 | 2011-01-11 | Weidman Cap. Bank | 5333 | 2011-01-11 | CAP | 2020-12-31 | Weidman | Capacitor Bank |  | 69 |  |  | Install a Capacitor Bank |  | MI |  |  | Planned | 260000 | 2009$ |  |  |  |  | Y | A
A in MTEP09 | East | WPSC | 2735 | 2010-01-06 | AB-WW | 4756 | 2010-09-10 | LNrb | 2013-12-31 | Alba | Mancelona | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line |  | MI | 4.51 |  | Planned | 1900000 | 2010$ |  |  |  |  | Y | A
A in MTEP09 | East | WPSC | 2735 | 2010-01-06 | AB-WW | 4757 | 2010-09-10 | LNrb | 2013-12-31 | Mancelona | Westwood | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line |  | MI | 6.7 |  | Planned | 2900000 | 2010$ |  |  |  |  | Y | A
A in MTEP09 | East | WPSC | 2736 | 2010-01-06 | EB-SB | 4758 | 2010-09-10 | LNrb | 2014-12-31 | East Bay | South Boardman Distribution | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line |  | MI | 15.93 |  | Planned | 6500000 | 2010$ |  |  |  |  | Y | A
A in MTEP09 | East | WPSC | 2770 | 2009-02-03 |  | 4832 | 2010-06-22 | TAP | 2012-06-01 | Hersey | Gilmore | 1 | 69 |  |  | Gilmore Taps the Hersey to Vestaburg 69kV circuit |  | MI |  |  | Planned | 100000 | Planning |  |  |  |  | Y | A
A in MTEP09 | East | WPSC | 2770 | 2009-02-03 |  | 4833 | 2010-06-22 | TAP | 2012-06-01 | Gilmore | Vestaburg | 1 | 69 |  |  | Gilmore Taps the Hersey to Vestaburg 69kV circuit |  | MI |  |  | Planned | 100000 | Planning |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1222 | 2011-06-23 | LC Upgrade | 1917 | 2011-06-23 | Bus | 2011-12-31 | Lake County | Bus Upgrade |  | 69 |  |  | Convert Single Bus to Ring Bus |  | MI |  |  | Under Construction | 2550000 | 2009$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1222 | 2011-06-23 | LC Upgrade | 2129 | 2011-06-23 | LN | 2011-12-31 | Lake County 138 | Lake County 69 |  | 138 | 69 | 150MVA | Add 168MV transformer |  | MI |  |  | Under Construction | 3500000 | Planning |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1274 | 2010-01-06 | BQ-OF | 1996 | 2010-09-10 | LNrb | 2012-12-31 | Allendale | Blendon |  | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 2.11 |  | Planned | 900000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1274 | 2010-01-06 | BQ-OF | 3257 | 2011-01-11 | LNrb | 2014-12-31 | Allendale | Osipoff | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 14.53 |  | Planned | 6500000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1311 | 2010-01-06 | GN-CH | 2167 | 2011-01-11 | LNrb | 2012-12-31 | Grawn | Karlin |  | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 6.61 |  | Planned | 3000000 | 2009$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1311 | 2010-01-06 | GN-CH | 2166 | 2011-01-11 | LNrb | 2014-12-31 | Copemish | Karlin |  | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 13.59 |  | Planned | 6100000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1313 | 2010-01-06 | PJ-HY | 2168 | 2011-01-11 | LNrb | 2012-12-31 | Baldwin | Plains X |  | 69 |  | 143.4MVA | Rebuild Overloaded line (Off peak case) |  | MI | 6.94 |  | Planned | 2900000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1313 | 2010-01-06 | PJ-HY | 3850 | 2011-01-11 | LNrb | 2015-12-31 | Hersey | Lincoln X | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line (Off peak case) |  | MI | 3.05 |  | Planned | 1400000 | 2009$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1313 | 2010-01-06 | PJ-HY | 3851 | 2011-01-11 | LNrb | 2015-12-31 | Lincoln X | Baldwin | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line (Off peak case) |  | MI | 16.47 |  | Planned | 7150000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1581 | 2010-01-06 | AB-AD | 3233 | 2010-09-10 | LNrb | 2011-12-31 | East Jordan X | Graves X | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 7.14 |  | Planned | 2900000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1581 | 2010-01-06 | AB-AD | 3134 | 2010-09-10 | LNrb | 2011-12-31 | Alba | Graves X | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 4.72 |  | Planned | 1900000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1581 | 2010-01-06 | AB-AD | 3852 | 2011-01-11 | LNrb | 2012-12-31 | Advance | Advance Dist. | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line |  | MI | 0.91 |  | Planned | 500000 | Planning |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1581 | 2010-01-06 | AB-AD | 3853 | 2011-01-11 | LNrb | 2012-12-31 | Advance Dist. | East Jordan X | 1 | 69 |  | 143.4MVA | Rebuild Overloaded Line |  | MI | 4.66 |  | Planned | 2000000 | Planning |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1586 | 2011-03-17 | GY-AD | 3143 | 2011-01-11 | LNrb | 2015-12-31 | Elmira | Advance | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line |  | MI | 16.26 |  | Planned | 7200000 | 2010$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1967 | 2009-01-26 | WD-PD | 3862 | 2011-01-11 | LNrb | 2020-12-31 | Sebewa | Portland | 1 | 69 |  | 143.4MVA | Rebuild Line (Poles have reached the end of their useful life) |  | MI | 6.85 |  | Planned | 2400000 | 2009$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1967 | 2009-01-26 | WD-PD | 3858 | 2011-01-11 | LNrb | 2020-12-31 | Wayland | Middleville X | 1 | 69 |  | 143.4MVA | Rebuild Line (Poles have reached the end of their useful life) |  | MI | 10.69 |  | Planned | 3800000 | 2009$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1967 | 2009-01-26 | WD-PD | 3860 | 2011-01-11 | LNrb | 2020-12-31 | Superior | Odessa | 1 | 69 |  | 143.4MVA | Rebuild Line (Poles have reached the end of their useful life) |  | MI | 0.06 |  | Planned | 50000 | 2009$ |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1967 | 2009-01-26 | WD-PD | 3859 | 2011-01-11 | LNrb | 2020-12-31 | Middleville X | Superior | 1 | 69 |  | 143.4MVA | Rebuild Line (Poles have reached the end of their useful life) |  | MI | 19.73 |  | Planned | 7092000 | Planning |  |  |  |  | Y | A
A in MTEP08 | East | WPSC | 1967 | 2009-01-26 | WD-PD | 3861 | 2011-01-11 | LNrb | 2020-12-31 | Odesa | Sebewa | 1 | 69 |  | 143.4MVA | Rebuild Line (Poles have reached the end of their useful life) |  | MI | 3.37 |  | Planned | 1200000 | 2009$ |  |  |  |  | Y | A
A in MTEP06 | East | WPSC | 1272 | 2010-09-28 | RW 2nd xfmr | 1994 | 2009-01-26 | TX | 2012-12-31 | Redwood 138 | Redwood 69 |  | 138 | 69 | 65MVA | Add 75MV transformer |  | MI |  |  | Planned | 3000000 | 2008$ |  |  |  |  | Y | A
A in MTEP10 | West | ATC LLC | 2451 | 2010-04-30 |  | 4396 | 2010-04-30 | LNrb | 2012-03-01 | Brodhead | Spring Grove | 1 | 69 |  | 80 MVA | Rebuild Brodhead- S Monroe 69kV line with T2 477 kcmil ACSR |  | WI | 3.1 |  | Planned | 11800000 | [5 empty] | Y | A
A in MTEP10 | West | ATC LLC | 2819 | 2010-09-15 | F2604 | 4957 | 2011-08-24 | TR | 2011-12-27 | Bluemound | transformer | 3 | 230 | 138 | 400 MVA | Replace Bluemound 230/138kV transformer T3 with a 400 MVA unit |  | WI |  |  | Planned | 8000000 | eng |  |  |  |  | Y | A
A in MTEP10 | West | ATC LLC | 3122 | 2010-02-01 |  | 5473 | 2010-04-30 | LN | 2012-06-19 | Dam Heights | Okee Tap | 1 | 69 |  | 73 MVA | Reconductor 1.94 mi of 3-0 and 336 ACSR line conductor with T-2 4-0 ACSR keeping the T-2 3-0 ACSR for the DHT-Okee Tap section of line Y-8, replace 26 1919 vintage lattice towers and 4 wood poles |  | WI | 8.88 |  | Planned | 2177421 | eng |  |  |  |  | Y | A
A in MTEP09 | West | ATC LLC | 2452 | 2010-04-30 | G706 | 4394 | 2011-03-18 | GEN | 2011-12-31 | Glacier Hills Wind 2 | generator | W | 0.69 |  | 150 MW | H012 Glacier Hills 2 Wind Farm |  | WI |  |  | Planned |  |  | Generator |  |  |  | Y | A
A in MTEP09 | West | ATC LLC | 2452 | 2010-04-30 | G706 | 4416 | 2011-03-18 | GEN | 2011-12-31 | Glacier Hills Wind 1 | generator | W | 0.69 |  | 99 MW | G706 Glacier Hills 1 Wind Farm |  | WI |  |  | Planned |  |  | generator |  |  |  | Y | A
A in MTEP08 | West | ATC LLC | 356 | 2011-08-24 | newgrp6 | 897 | 2010-04-30 | SUB | 2013-06-01 | Rockdale/Albion | 345 kV bus modification at Rockdale/new 345 kV switching station at Albion |  | 345 |  |  | 345 kV bus modification at Rockdale/new 345 kV switching station at Albion | K7 | WI |  |  | Planned | 15020589.89 | Engineering |  |  | Y | Y | Y | A
A in MTEP08 | West | ATC LLC | 356 | 2011-08-24 | newgrp6 | 488 | 2010-04-30 | TX | 2013-06-01 | Cardinal (formerly West Middleton) 345/138 | transformer | 1 | 345 | 138 | 500 |  | K7 | WI |  |  | Planned | 4986995.2 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | West | ATC LLC | 356 | 2011-08-24 | newgrp6 | 486 | 2010-04-30 | LN | 2013-06-01 | Cardinal (formerly West Middleton) | Rockdale/Albion | 1 | 345 |  | 1195 MVA SE |  | K7 | WI |  | 35 | Planned | 174094863 | Engineering |  |  | Y | Y | Y | A
A in MTEP08 | West | ATC LLC | 356 | 2011-08-24 | newgrp6 | 3383 | 2010-04-30 | TX | 2013-06-01 | Cardinal (formerly West Middleton) 345/138 | transformer, backup | 2 | 345 | 138 | 500 |  |  | WI |  |  | Planned | 4986995.2 |  |  |  | Y |  | Y | A
A in MTEP08 | West | ATC LLC | 356 | 2011-08-24 | newgrp6 | 3384 | 2011-08-24 | SUB | 2013-06-01 | Cardinal (formerly West Middleton) | substation |  | 345 |  |  | new 345 substation |  | WI |  |  | Planned | 20035429 |  |  |  | Y | Y | Y | A
A in MTEP08 | West | ATC LLC | 574 | 2010-09-15 | PRF934D | 1370 | 2011-08-24 | TX | 2014-06-01 | Council Creek 161-138 kV | transformer | 1 | 161 | 138 | 210 | New Council Creek Transformer | J6 | WI |  |  | Planned | 5404000 | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | ATC LLC | 574 | 2010-09-15 | PRF934D | 1269 | 2011-08-24 | LN | 2014-06-01 | Monroe County (XEL) | Council Creek (ATC) | 1 | 161 |  | 445 | Install new T2-556 ACSR, OH-ATC-161-DC, 17.3 mi | J6 | WI |  | 17.3 | Planned | 25296000 | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | ATC LLC | 574 | 2010-09-15 | PRF934D | 858 | 2011-08-24 | LNup | 2014-06-01 | Council Creek | Petenwell | 1 | 138 |  | 191 | Uprated Petenwell substation to 191 MW CT limit | J6 | WI | 30.3 |  | Planned |  | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | ATC LLC | 574 | 2010-09-15 | PRF934D | 6329 | 2011-08-24 | LNup | 2014-06-01 | Council Creek | Transformer | 1 | 138 | 69 | 100 | Replace relaying to uprate transformer as part of Project ID: 574 (Monroe County-Council Ck 161 kV line) |  | WI |  |  | Planned | 4003000 | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | ATC LLC | 1683 | 2007-11-07 |  | 3458 | 2011-01-11 | LNrb | 2012-03-01 | Sunset Point | Pearl Ave | 1 | 69 |  | 57 MVA | Rebuild 2.37 miles of 69 kV from Sunset Point-Pearl Ave with 477 ACSR |  | WI | 2.37 |  | Planned | 4128701.46 | [5 empty] | Y | A
A in MTEP08 | West | DPC | 1957 | 2008-01-10 | ECP2 | 3841 | 2011-03-24 | LN | 2012-06-01 | new sub | Burnswick | 1 | 69 |  | 84 MVA | Construct 69 kV line from new substation to DPC Brunswick Substation |  | WI |  |  | Planned | 0 | [5 empty] | NT | A
A in MTEP08 | West | DPC | 1957 | 2008-01-10 | ECP2 | 3840 | 2011-03-24 | LN | 2012-06-01 | new sub | Union (DPC) | 1 | 69 |  | 84 MVA | Construct 69 kV line from new substation to DPC Union Substation |  | WI |  |  | Planned | 0 | [5 empty] | NT | A
A in MTEP10 | West | GRE | 1018 | 2009-11-19 | 20386 | 640 | 2010-09-15 | LNup | 2012-11-30 | Little Falls | CWP Little Falls | 1 | 115 |  | 196 | 115 kv line operated at 34.5 | H5 | MN | 4 |  | Planned | 1705513.76 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2564 | 2009-09-14 | 20564 | 4566 | 2011-07-01 | LN | 2012-10-28 | Sartell | Le Sauk | 1 | 115 |  |  | Sartell Disribution Sub, 795 ACSS 115 kV radial line and switch |  | MN |  | 3 | Planned | 1385861.12 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2565 | 2009-09-14 | 20279 | 4567 | 2011-07-01 | LN | 2012-11-05 | Tower | Frazer Bay | 1 | 69 |  |  | New Distribution |  | MN |  | 15 | Under Construction | 8783373.12 | Planning |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2565 | 2009-09-14 | 20279 | 4584 | 2011-07-01 | LN | 2012-11-05 | Tower | Transformer | 1 | 115 | 69 | 70 | New Substation |  | MN |  | 0 | Planned | 2005882.18 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2565 | 2009-09-14 | 20279 | 4585 | 2011-07-01 | LN | 2012-11-05 | Cook | Frazer Bay | 1 | 69 |  |  | 477 ACSR, 69 kV |  | MN |  | 12 | Planned | 8485843.87 | Planning |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2566 | 2009-09-14 | 20294 | 4569 | 2011-07-01 | LN | 2011-10-14 | Potato Lake | Potato Lake Tap | 1 | 115 |  |  | New distribution built 115 (op 34.5) |  | MN |  | 7 | Under Construction | 4401144.26 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2567 | 2009-09-14 | 20311 | 4572 | 2011-07-01 | LN | 2012-10-31 | Northport | Northport Tap | 1 | 115 |  |  | New Distribution |  | MN |  | 1 | Planned | 1149664 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2570 | 2009-09-14 | 20197 | 4581 | 2011-07-01 | SUB | 2014-06-02 | Ravenna | Ravenna Tap | 1 | 161 |  |  | New Distribution |  | MN |  | 0 | Planned | 821206.11 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2574 | 2009-09-14 | 20285 | 4586 | 2011-03-28 | SUB | 2017-05-01 | St. Lawrence | St. Lawrence Tap | 1 | 115 |  |  | St. Lawrence 69 kV 3-way switch |  | MN |  | 0.5 | Planned | 374182.3301 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2576 | 2009-09-14 | 20310 | 4587 | 2011-07-01 | LN | 2011-11-01 | Pokegama | Pokegama Tap | 1 | 115 |  |  | New Distribution |  | MN |  | 8 | Under Construction | 4079992.7128 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2577 | 2009-09-14 | 20312 | 4588 | 2011-03-28 | SUB | 2012-06-01 | Elmcrest | Elmcrest Tap | 1 | 69 |  |  | New Distribution |  | MN |  | 0 | Planned | 140000 | Planning |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2579 | 2010-09-15 | 20273 | 4590 | 2011-07-01 | SUB | 2015-05-29 | Foster Lake | Foster Lake Tap | 1 | 69 |  |  | New Distribution |  | MN |  | 0 | Planned | 140000 | Planning |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2589 | 2009-11-19 | 20328 | 4600 | 2011-07-01 | LN | 2014-03-25 | Rich Valley | Rich Valley Tap | 1 | 69 |  |  | New Distribution |  | MN |  | 2 | Planned | 115001 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2605 | 2009-09-14 | 20344 | 4616 | 2011-07-01 | SUB | 2012-04-30 | Bunker Lake Bulk | Substation | 1 | 69 |  |  | New Distribution |  | MN |  | 0 | Planned | 208449.71 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2621 | 2009-11-19 | 20371 | 4628 | 2011-07-01 | LN | 2013-11-01 | Effie | Big Fork | 1 | 69 |  | 108 | Effie-Big Fork 69 kV line, Wirt Tap 3-way switch, Jessie Lake 3-way switch, Big Fork 3-way switch |  | MN |  | 19 | Planned | 8107919 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2621 | 2009-11-19 | 20371 | 4627 | 2011-07-01 | TX | 2013-11-01 | Effie | transformer | 1 | 230 | 69 | 60 |  |  | MN |  |  | Planned | 2420000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2624 | 2009-09-14 | 20374 | 4631 | 2011-07-01 | LN | 2012-02-29 | Hudson | Hudson Tap | 1 | 115 |  | 141.6 |  |  | MN | 0.5 |  | Under Construction | 381006.42 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2630 | 2009-09-14 | 20383 | 4640 | 2011-07-01 | LNup | 2013-04-24 | Big Fork | Wirt Tap | 1 | 69 |  | 35 | Resag |  | MN | 7.16 |  | Planned | 572621.9988 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2630 | 2009-09-14 | 20383 | 4641 | 2011-07-01 | LNup | 2013-04-24 | Wirt Tap | Jessie Lake | 1 | 69 |  | 35 | Resag |  | MN | 8.97 |  | Planned | 717377.0012 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2631 | 2009-09-14 | 20384 | 4642 | 2011-07-01 | LNup | 2013-04-24 | Deer River | Jessie Lake | 1 | 69 |  | 58.8 | Resag |  | MN | 16.52 |  | Planned | 1339996 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2667 | 2009-09-14 | 20429 | 4684 | 2011-07-01 | LN | 2011-09-30 | Rush City | Adrian Robinson | 1 | 69 |  | 58.8 | Rush City distribution retemp |  | MN | 3.15 |  | Planned | 299001.17 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2670 | 2010-09-15 | 20446 | 4687 | 2011-07-01 | TX | 2020-04-14 | Schuster Lake | transformer | 1 | 115 | 41.6 | 70 | North Perham land acquisition and 115/41.6 kV source |  | MN |  |  | Planned | 4480714.28 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2671 | 2009-09-14 | 20447 | 4634 | 2011-07-01 | LNup | 2011-12-30 | Ham Lake | Soderville | 1 | 69 |  | 75.8 | Retemp |  | MN | 0.38 |  | Planned | 125000 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2671 | 2009-09-14 | 20447 | 4633 | 2011-07-01 | LNup | 2011-12-30 | Ham Lake | Johnsville | 1 | 69 |  | 75.8 | Retemp |  | MN | 5.8 |  | Planned | 157809 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2672 | 2009-09-14 | 20448 | 4688 | 2011-07-01 | TX | 2011-11-01 | Rush City | transformer | 1 | 230 | 69 | 112 | Bunker Lake transformer moved to Rush City |  | MN |  |  | Planned | 300000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2672 | 2009-09-14 | 20448 | 4689 | 2011-07-01 | TX | 2012-06-01 | Bear Creek | transformer | 1 | 230 | 69 | 84 | Rush City move to Bear Creek |  | MN |  |  | Planned | 200000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2731 | 2010-09-15 | 20553 | 4750 | 2010-09-15 | LN | 2012-09-03 | Blomkest | Lake Lillian Tap | 1 | 69 |  |  | New Distribution |  | MN |  | 2 | Planned | 1140342.35 | Engineering |  |  |  |  | NT | A
A in MTEP10 | West | GRE | 2833 | 2009-09-04 | 20568 | 4979 | 2011-07-01 | Line | 2013-10-21 | South Haven | Lake Caroline | 1 | 69 |  | 68 | New Line |  | MN |  | 1 | Planned | 675000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 2834 | 2009-09-04 | 200811 | 4980 | 2011-07-01 | Line | 2013-09-10 | Paynesville | Hawick | 1 | 69 |  | 85 | New Line |  | MN |  | 5 | Planned | 5138000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | GRE | 3106 | 2009-12-29 | G619-20595 | 5441 | 2011-07-01 | SUB | 2012-09-03 | Tamarac | Substation | 1 | 115 |  |  | Breaker for G619 plant wind farm connection |  | MN |  |  | Planned | 728000 | Engineer | Network |  | Y |  | Y | A
A in MTEP09 | West | GRE | 2562 | 2010-04-05 | 20561 | 6513 | 2011-07-01 | Sub | 2012-03-30 | Pleasant Valley |  |  |  | 161 |  | 161 kV bus work. 161 kV Breaker and half scheme. |  | MN |  |  | Planned | 1006364.75 | [5 empty] | Y | A
A in MTEP09 | West | GRE | 2563 | 2010-04-05 | 20555 | 4579 | 2011-07-01 | LN | 2012-11-30 | Martin Lake | Athens | 1 | 69 |  | 135.9 | System upgrades and permitting |  | MN |  | 10 | Planned | 6234719.2725 | [5 empty] | NT | A
A in MTEP05 | West | GRE | 599 | 2010-04-05 | 20152 | 753 | 2011-07-01 | LN | 2013-06-01 | Crooked Lake | Enterprise Park | 1 | 115 |  | 316 | New 115 kV line | TC det | MN |  | 4 | Planned | 8616068.62 | [5 empty] | Y | A
A in MTEP05 | West | GRE | 600 | 2010-04-05 | 20113 | 1078 | 2011-07-01 | LN | 2012-06-01 | Scearcyville | Southdale | 1 | 115 |  | 196 | New line | H5 | MN |  | 9 | Under Construction | 5845969.38 | [5 empty] | Y | A
A in MTEP08 | West | GRE, OTP | 1033 | 2010-04-05 | 20395 | 587 | 2011-07-01 | TX | 2011-10-28 | Silver Lake 230/41.6 kV | transformer | 1 | 230 | 41.6 | 50 |  | G5 | MN |  |  | Under Construction | 3230626 | [5 empty] | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 2976 | 2011-07-01 | TX | 2011-12-15 | Quarry (St. Cloud) | 345/115 transformer | 1 | 345 | 115 | 448 | new transformer and terminal works | G5 | MN |  |  | Planned | 7367000 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 2640 | 2011-07-01 | LN | 2011-12-15 | Waite Park (Quarry) | Monticello | 1 | 345 |  | 2085 | Add a new 345 kV line from Waite Park to Monticello substation and terminal works | G5 | MN |  | 35 | Planned | 84972000 | Engineering |  | Y | Y | Y | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 6328 | 2011-07-01 | TX | 2011-12-15 | Monticello | substation | 1 | 345 | 115 |  | Improvements to the existing Monticello substation to accommodate new CAPX Fargo 345 kV line |  | MN |  |  | Planned | 9755500 | [5 empty] | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 1104 | 2011-07-01 | LN | 2013-05-07 | Alexandria SS | Waite Park (Quarry) | 1 | 345 |  | 2085 | Add a new 345 kV line from Alexandria Switching Station to Waite Park and terminal works | G5 | MN |  | 55 | Planned | 133666500 | Engineering |  | Y | Y | Y | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 2641 | 2011-07-01 | TX | 2013-05-07 | Alexandria SS | Transformer | 1 | 345 | 115 | 448 | new transformer and terminal works | G5 | MN |  |  | Planned | 6500000 | Engineering |  | Y | Y |  | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 1105 | 2011-07-01 | LN | 2015-03-31 | Bison | Alexandria SS | 1 | 345 |  | 2085 | Add a new 345 kV line from Maple River to Alexandria Switching Station substation and terminal works | F4 | MN/ND |  | 135 | Planned | 288050000 | Engineering |  | Y | Y | Y | Y | A
A in MTEP08 | West | GRE, XEL, OTP, MP, MRES | 286 | 2011-07-01 | CAPX Fargo-Alex-Monti | 6514 | 2011-07-01 | TX | 2015-03-31 | Bison | substation | 1 | 345 | 230 | 448 | New substation |  | ND |  |  | Planned | 34436000 | [5 empty] | Y | A
A in MTEP10 | West | ITCM | 3046 | 2009-09-14 | SW CR 69kV Upgrade | 5262 | 2010-06-28 | SUB | 2012-12-31 | Beverly 161kV | Main and Line Breakers |  | 69 |  | 143 MVA | Add main breaker and 2 line breakers |  | IA | 0 | 0 | Planned | 1500000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3046 | 2009-09-14 | SW CR 69kV Upgrade | 5263 | 2010-06-28 | LN | 2012-12-31 | 26th Jct | Beverly T4 | 1 | 69 |  | 140 MVA | Open 26th Jct to Viola's Corner line and extend 26th Jct to open point into the Beverly substation |  | IA | 0 | 0.1 | Planned | 150000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3046 | 2009-09-14 | SW CR 69kV Upgrade | 5264 | 2010-06-28 | LN | 2012-12-31 | Viola's Corner | Beverly T4 | 1 | 69 |  | 140 MVA | Open 26th Jct to Viola's Corner line and extend Viola's Corner to open point into the Beverly substation |  | IA | 0 | 0.1 | Planned | 150000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3047 | 2009-09-14 | IA Falls Ind TRF | 5265 | 2011-07-01 | TX | 2011-08-30 | Iowa Falls Industrial | transformer | 1 | 161 | 69 | 112 MVA | Upgrade the IA Falls Ind 115/69kV TRF with a dual high side (161-115kV)/69kV TRF. |  | IA | 0 | 0 | Planned | 1980000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3048 | 2009-09-14 | Jeff-Perlee | 5266 | 2011-07-01 | LN | 2013-12-31 | Jefferson Co | Perlee | 1 | 69 | 69 | 57 MVA | Rebuild Jefferson Co-Perlee line |  | IA | 7.378 | 0 | Planned | 2700000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3049 | 2009-09-14 | Huxley Terminal | 5300 | 2010-04-04 | CB | 2012-12-31 | Huxley Industrial Park | Breaker | 1 | 161 | 161 | 335 MVA | Add a 161kV line terminal to tie to the rerouted Boone Jct-Huxley Park Ind 161kV line (CIPCO project). |  | IA | 0 | 0 | Planned | 750000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3050 | 2009-09-14 | Alden-Buckeye | 5272 | 2010-06-28 | LN | 2011-12-31 | CBPC Alden | new Alden-Buckeye | 1 | 69 | 69 |  | Build a 3 mile 69kV tap to the new Alden-Buckeye sub. |  | IA | 0 | 3 | Planned | 1080000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3052 | 2009-09-14 | Wash Sub | 5271 | 2009-09-14 | SUB | 2011-12-31 | Washington | Substation | 1 | 69 | 69 |  | Upgrade Washington 69kV sub & add bus tie breaker. |  | IA | 0 | 0 | Planned | 2400000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3053 | 2010-06-28 | Keokuk Hydro-Carbide 69kV Dbl Ckt | 5297 | 2011-07-01 | LN | 2013-12-31 | Commercial | Carbide | 1 | 69 | 69 | 100 MVA | Rebild to doulbe ckt 69kV |  | IA |  |  | Planned | 540000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3053 | 2010-06-28 | Keokuk Hydro-Carbide 69kV Dbl Ckt | 5295 | 2011-07-01 | LN | 2013-12-31 | Keokuk Hydro | Messenger | 1 | 69 | 69 | 100 MVA | Rebild to doulbe ckt 69kV |  | IA |  |  | Planned | 540000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3053 | 2010-06-28 | Keokuk Hydro-Carbide 69kV Dbl Ckt | 5296 | 2011-07-01 | LN | 2013-12-31 | Messenger | Commercial | 1 | 69 | 69 | 100 MVA | Rebild to doulbe ckt 69kV |  | IA |  |  | Planned | 540000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3053 | 2010-06-28 | Keokuk Hydro-Carbide 69kV Dbl Ckt | 5294 | 2011-07-01 | LN | 2013-12-31 | Keokuk Hydro | Carbide | 1 | 69 | 69 | 100 MVA | Build a new Keokuk Hydro-Carbide 69 kV line. |  | IA |  |  | Planned | 1620000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3054 | 2009-09-14 | Swisher SS | 5270 | 2011-07-01 | LN | 2011-12-31 | Amana | Amana T | 1 | 69 | 69 |  | Close N.O. Amana-Amana T line. |  | IA | 0 | 0 | Planned | 0 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3054 | 2009-09-14 | Swisher SS | 5268 | 2011-07-01 | LN | 2011-12-31 | Swisher | Swisher REC | 1 | 69 | 69 |  | Close N.O. Swisher-Swisher REC line. |  | IA | 0 | 0 | Planned | 352000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3054 | 2009-09-14 | Swisher SS | 5267 | 2011-07-01 | SUB | 2011-12-31 | Tharp (Swisher) | Breaker Station | 1 | 69 | 69 |  | Build a new 3 terminal breaker station. |  | IA | 0 | 0 | Planned | 1800000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3054 | 2009-09-14 | Swisher SS | 5269 | 2011-07-01 | LN | 2011-12-31 | North Liberty | North Liberty REC | 1 | 69 | 69 |  | Close N.O. North Liberty-North Liberty REC line. |  | IA | 0 | 0 | Planned | 0 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5280 | 2009-09-14 | LN | 2011-12-31 | Marion | Collins | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 2.5 |  | Planned | 700000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5281 | 2009-09-14 | LN | 2011-12-31 | Collins | Hiawatha | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 1 |  | Planned | 700000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5288 | 2011-07-01 | SUB | 2012-12-31 | Downtown Network | Substation | 1 | 161 | 161 |  | New 115kV/dist sub |  | IA |  |  | Planned | 2160000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5286 | 2011-07-01 | LN | 2012-12-31 | Downtown Network | PCI | 1 | 161 | 161 |  | Rebuild 34kV to 161kV |  | IA | 5 |  | Planned | 2100000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5285 | 2011-07-01 | LN | 2012-12-31 | Downtown Industrial | Downtown Network | 1 | 161 | 161 |  | Rebuild 34kV to 161kV |  | IA | 2 |  | Planned | 2100000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5283 | 2010-06-28 | LN | 2013-12-31 | Oak Hill | Marion | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 8 |  | Planned | 1010000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5278 | 2011-07-01 | LN | 2013-12-31 | Emerald Isle | Cargil West | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 4 |  | Planned | 810000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5282 | 2010-06-28 | LN | 2013-12-31 | PCI | Oak Hill | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 5 |  | Planned | 1010000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5277 | 2011-07-01 | LN | 2013-12-31 | Emerald Isle | Louisa | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 3 |  | Planned | 740000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5276 | 2011-07-01 | LN | 2013-12-31 | Marion | Emerald Isle | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 3 |  | Planned | 740000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5279 | 2011-07-01 | LN | 2013-12-31 | Cargil West | PCI | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) |  | IA | 6 |  | Planned | 810000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5289 | 2009-09-14 | TX | 2013-12-31 | Marion | transformer | 1 | 161 | 69 | 100 MVA | Add a 161/69kV TRF at Marion |  | IA |  |  | Planned | 3240000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5293 | 2009-09-14 | SUB | 2013-12-31 | Oak Hill | Substation | 1 | 69 |  |  | New 69kV/dist sub |  | IA |  |  | Planned | 2160000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5291 | 2009-09-14 | SUB | 2014-12-31 | Cargil West | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 2160000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5290 | 2009-09-14 | SUB | 2014-12-31 | Collins | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 2160000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3055 | 2009-09-14 | CR 34kV Plan | 5292 | 2009-09-14 | SUB | 2014-12-31 | Emerald Isle | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 2160000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3056 | 2009-09-14 | Grundy-Hicks 34kV | 5298 | 2010-04-04 | LN | 2012-12-31 | Grundy Center | Reinbeck | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 12 | 0 | Planned | 4320000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3056 | 2009-09-14 | Grundy-Hicks 34kV | 5299 | 2010-04-04 | LN | 2012-12-31 | Reinbeck | Hicks tap | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 4 | 0 | Planned | 1440000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5303 | 2011-03-30 | LN | 2013-12-31 | Moscow Tap | Magmet T | 1 | 69 | 69 |  | Tap the Muscatine Switch Station to Magmet T69kV line for new tap to Moscow. |  | IA | 0 | 0 | Planned | 0 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5304 | 2011-03-30 | LN | 2013-12-31 | New Liberty | New Liberty Tap | 1 | 69 | 69 | 77 MVA | Build a new 2 mile 69kV tap to New Liberty & retire 9.4 mile 34kV tap. |  | IA | 0 | 2 | Planned | 700000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5302 | 2011-03-30 | LN | 2013-12-31 | Muscatine Switch Station | Moscow Tap | 1 | 69 | 69 |  | Tap the Muscatine Switch Station to Magmet T69kV line for new tap to Moscow. |  | IA | 0 | 0 | Planned | 0 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5301 | 2011-03-30 | LN | 2013-12-31 | Moscow | Moscow Tap | 1 | 69 | 69 | 77 MVA | Build a new 3.75 mile 69kV tap to Moscow & retire 7 mile 34kV tap. |  | IA | 0 | 3.75 | Planned | 1313000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 6419 | 2011-02-15 | LN | 2013-12-31 | New Liberty | New Liberty Tap | 1 | 34 | 34 |  | Retire the New Liberty 34kV 9.4 mile tap |  | IA |  |  | Planned | 282000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 6418 | 2011-02-15 | LN | 2013-12-31 | Moscow Tap | Moscow | 1 | 34 | 34 |  | Retire the Moscow 34kV 7 mile tap |  | IA |  |  | Planned | 210000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5319 | 2009-09-14 | SUB | 2011-12-31 | Shady Grove REC | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5310 | 2009-09-14 | LN | 2011-12-31 | Quasqueton Tap | Quasqueton REC | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 4 | 0 | Planned | 1440000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5309 | 2009-09-14 | LN | 2011-12-31 | Brandon | Shady Grove REC | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 4.5 | 0 | Planned | 1980000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5320 | 2009-09-14 | SUB | 2011-12-31 | Quasqueton REC | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5318 | 2009-09-14 | SUB | 2011-12-31 | Brandon | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5307 | 2011-07-01 | LN | 2012-12-31 | Shellsburg | Palo | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 4 | 0 | Planned | 1620000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5311 | 2011-07-01 | LN | 2012-12-31 | Troy Mills | Walker REC | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 6.55 |  | Planned | 2358000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5322 | 2011-07-01 | SUB | 2012-12-31 | Lafayette | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5315 | 2009-09-14 | TX | 2012-12-31 | Vinton | transformer | 1 | 161 | 69 | 100 MVA | Add a 161/69kV TRF at Vinton |  | IA |  |  | Planned | 3250000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5316 | 2011-07-01 | SUB | 2012-12-31 | Palo | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5317 | 2011-07-01 | SUB | 2012-12-31 | Shellsburg | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5314 | 2009-09-14 | LN | 2012-12-31 | Lafayette | Hiawatha | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 6 |  | Planned | 2160000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5323 | 2011-07-01 | SUB | 2013-12-31 | Urbana | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5308 | 2011-07-01 | LN | 2013-12-31 | Palo | Todville REC | 1 | 69 | 69 |  | New 69kV |  | IA | 0 | 4.5 | Planned | 1260000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5312 | 2011-07-01 | LN | 2013-12-31 | Vinton | Shellsburg | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 11 |  | Planned | 4320000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5313 | 2011-07-01 | LN | 2013-12-31 | Walker REC | Urbana | 1 | 69 | 69 |  | Rebuild 34kV to 69kV |  | IA | 10 |  | Planned | 3600000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3058 | 2009-09-14 | Vinton 34kV Plan | 5321 | 2011-07-01 | SUB | 2013-12-31 | Walker REC | Substation | 1 | 69 | 69 |  | New 69kV/dist sub |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3059 | 2009-09-14 | WB &WL SS | 5325 | 2011-07-01 | SUB | 2011-12-31 | West Liberty | Breaker Station | 1 | 69 | 69 | 140 MVA | Build a new 3 terminal breaker station. |  | IA | 0 | 0 | Planned | 1560000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | ITCM | 3059 | 2009-09-14 | WB &WL SS | 5324 | 2009-09-14 | SUB | 2011-12-31 | West Branch | Breaker Station | 1 | 69 | 69 | 140 MVA | Build a new 3 terminal breaker station. |  | IA | 0 | 0 | Planned | 1560000 | Planning |  |  |  |  | Y | A
A in MTEP09 | West | ITCM | 2339 | 2008-12-01 | ITCM-08-009 | 4286 | 2011-07-01 | LNrb | 2011-09-30 | Ames | Fernald | 1 | 161 |  | 446 MVA | Rebuild 115kV to 161kV line |  | IA | 6 |  | Under Construction | 4200000 | Planning |  |  | Y |  | Y | A
A in MTEP09 | West | ITCM | 2339 | 2008-12-01 | ITCM-08-009 | 4285 | 2011-07-01 | LNrb | 2011-11-30 | Boone Junction | Ames | 1 | 161 |  | 446 MVA | Rebuild 115kV to 161kV line |  | IA | 8.4 |  | Under Construction | 5880000 | Planning |  |  | Y |  | Y | A
A in MTEP09 | West | ITCM | 2339 | 2008-12-01 | ITCM-08-009 | 4284 | 2010-06-28 | LNrb | 2012-05-30 | Boone | Boone Junction | 1 | 161 |  | 446 MVA | Rebuild 115kV to 161kV line |  | IA | 5.2 |  | Planned | 3640000 | Planning |  |  | Y |  | Y | A
A in MTEP09 | West | ITCM | 2340 | 2008-12-16 | ITCM-08-006 | 4296 | 2011-02-15 | LNrb | 2011-12-31 | Grand Junction | Grand Junction City | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 2.75 |  | Planned | 639200 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2340 | 2008-12-16 | ITCM-08-006 | 4297 | 2011-02-15 | LNrb | 2011-12-31 | Grand Junction City | Grand Junction North | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 2 |  | Planned | 464327 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2341 | 2009-04-01 | ITCM-08-014 | 4331 | 2011-03-30 | LNrb | 2011-09-01 | Amber | Monticello Industrial | 1 | 69 |  | 77/77 MVA | Rebuild 34kV to 69kV |  | IA | 8.51 |  | Under Construction | 2291032 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2341 | 2009-04-01 | ITCM-08-014 | 4332 | 2011-03-30 | CB | 2011-09-01 | Amber | breakers |  | 69 |  |  | Add two 69kV breakers at the Amber Creamery sub. |  | IA |  |  | Under Construction | 185000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2341 | 2009-04-01 | ITCM-08-014 | 4333 | 2011-03-30 | CB | 2011-09-01 | Sand Springs | breaker |  | 69 |  |  | Add a Sand Springs 69kV breaker and operate the Sand Springs-Monticello Industrial-Amber line at 69kV. |  | IA |  |  | Under Construction | 340000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2341 | 2009-04-01 | ITCM-08-014 | 4334 | 2011-03-30 | CB | 2011-09-01 | Monticello Industrial | breaker |  | 69 |  |  | Add a Monticello Industrial 69kV bus tie breaker and 69kV line breakers on the Sand Springs and Amber Creamery 69kV lines. |  | IA |  |  | Under Construction | 364000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2341 | 2009-04-01 | ITCM-08-014 | 4335 | 2010-09-28 | LNrb | 2011-10-30 | Lovell REC Tap | Lovell REC Junction | 1 | 34 |  | 39/39 MVA | Rebuild the remaning 2.21 miles of the 4.14 mile Lovell REC Tap-Lovell Junction 34kV line to 69kV standards. This line section will continue operation at 34kV. Monticello Industrial-Lovell REC 34kV line N.O. |  | IA | 2.21 |  | Under Construction | 594968 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2342 | 2009-09-25 | ITCM-08-019 | 4303 | 2011-07-01 | LNrb | 2011-12-31 | Ridgeport REC | Boone Junction | 1 | 34 |  | 39/39 MVA | Rebuild 6 miles of 34kV to 69kV (operated 34kV) from the Ridgeport REC sub south towards Boone Jct. |  | IA | 6 |  | Under Construction | 1588515 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2342 | 2009-09-25 | ITCM-08-019 | 4301 | 2011-07-01 | LNrb | 2011-12-31 | Stanhope | Stratford REC Tap | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 5 |  | Under Construction | 1323762 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2342 | 2009-09-25 | ITCM-08-019 | 4302 | 2011-07-01 | LNrb | 2011-12-31 | Stratford REC Tap | Ridgeport REC | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 5 |  | Under Construction | 1323762 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2342 | 2009-09-25 | ITCM-08-019 | 4300 | 2011-07-01 | LNrb | 2011-12-31 | Jewell | Stanhope | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 9.25 |  | Under Construction | 2448961 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | 4307 | 2010-09-28 | LNrb | 2011-12-31 | Mid-America Pump Tap | IA Valley Milling Tap | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 0.5 |  | Planned | 302891 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | 4304 | 2010-09-28 | LNrb | 2011-12-31 | West Branch | Mid-America Storage | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 2 |  | Planned | 550710 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | 4308 | 2010-09-28 | LNrb | 2011-12-31 | IA Valley Milling Tap | IA Valley Milling Sub | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 1.1 |  | Planned | 137678 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | 4305 | 2010-09-28 | LNrb | 2011-12-31 | Mid-America Storage | Mid-America Pump Tap | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 2 |  | Planned | 550710 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | 4309 | 2010-09-28 | LNrb | 2011-12-31 | IA Valley Milling Tap | West Liberty | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 8.21 |  | Planned | 2260667 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2343 | 2009-09-25 | ITCM-08-020 | 4306 | 2010-09-28 | LNrb | 2011-12-31 | Mid-America Pump Tap | Mid-America Pump Station | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 1.25 |  | Planned | 344194 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2344 | 2009-04-01 | ITCM-08-022 | 4311 | 2011-07-01 | LNrb | 2012-12-31 | Dome Pipeline | Oxford Mills | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 5 |  | Planned | 1675000 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2344 | 2009-04-01 | ITCM-08-022 | 4310 | 2011-07-01 | LNrb | 2012-12-31 | Wyoming | Dome Pipeline | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 2.3 |  | Planned | 770500 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2344 | 2009-04-01 | ITCM-08-022 | 4312 | 2011-07-01 | LNrb | 2012-12-31 | Oxford Mills | Massilon | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 4.7 |  | Planned | 1574500 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4326 | 2011-07-01 | LNrb | 2012-12-31 | Union | Whitten | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 5.25 |  | Under Construction | 1521822 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4313 | 2011-07-01 | SUB | 2012-12-31 | Otter Creek (Eldora North) | new switching station |  | 69 |  |  | Construct a new 4-terminal 69kV switching station along the Corn Belt 69kV line. Switch station will be named Otter Creek. |  | IA |  |  | Under Construction | 1658000 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4330 | 2011-07-01 | LNrb | 2012-12-31 | Beaman | Gladbrook T | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 3.5 |  | Under Construction | 1014550 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4329 | 2011-07-01 | LNrb | 2012-12-31 | Conrad distribution | Beaman | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 2.25 |  | Under Construction | 652210 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4328 | 2011-07-01 | LNrb | 2012-12-31 | Conrad 69/34kV | Conrad distribution | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 5.05 |  | Under Construction | 1463848 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4327 | 2011-07-01 | LNrb | 2012-12-31 | Whitten | Conrad 69/34kV | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 4.8 |  | Under Construction | 1391380 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4325 | 2011-07-01 | LNrb | 2012-12-31 | CBPC Union | Union | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 1.5 |  | Under Construction | 434806 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4324 | 2011-07-01 | LNrb | 2012-12-31 | Airport East Tap | CBPC Union | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 4.29 |  | Under Construction | 1243546 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4323 | 2011-07-01 | LNrb | 2012-12-31 | New Eldora North Switching | Airport East Tap | 1 | 34 |  | 39/39 MVA | Rebuild 34kV to 69kV (operated 34kV) |  | IA | 4.5 |  | Under Construction | 1304419 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4322 | 2011-07-01 | SUB | 2012-12-31 | IPL Radcliffe Sub | substation |  | 34 |  |  | Retire IPL Garden City Sub |  | IA |  |  | Under Construction | 0 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4314 | 2011-07-01 | LNcv | 2012-12-31 | CBPC Radcliffe Switch Station | Hubbard Rural | 1 | 69 |  | 77/77 MVA | Operate at 69kV (already built to 69kV standards) |  | IA |  |  | Under Construction | 0 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4320 | 2011-07-01 | SUB | 2012-12-31 | IPL Radcliffe 34kV/dist Sub | substation |  | 34 |  |  | Retire IPL Radcliffe Sub |  | IA |  |  | Under Construction | 0 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4319 | 2011-07-01 | SUB | 2012-12-31 | CBPC Enron | substation |  | 34 |  |  | CBPC Enron Sub 34 to 69kV converion |  | IA |  |  | Under Construction | 0 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4318 | 2011-07-01 | SUB | 2012-12-31 | IPL Hubard Rural 69kV/dist Sub | substation |  | 34 |  |  | IPL Hubbard Rural Sub 34 to 69kV converion |  | IA |  |  | Under Construction | 0 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4317 | 2011-07-01 | LNrb | 2012-12-31 | Eldora City Sub | New Eldora North Switching | 1 | 69 |  | 77/77 MVA | Rebuild 34kV to 69kV |  | IA | 2 |  | Under Construction | 579755 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4316 | 2011-07-01 | LNrb | 2012-12-31 | Enron Tap | Eldora City Sub | 1 | 69 |  | 77/77 MVA | Rebuild 34kV to 69kV |  | IA | 14.5 |  | Under Construction | 4203129 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4315 | 2011-07-01 | LNrb | 2012-12-31 | Hubbard Rural | Enron Tap | 1 | 69 |  | 77/77 MVA | Rebuild 34kV to 69kV |  | IA | 3.6 |  | Under Construction | 1043535 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2345 | 2009-09-25 | ITCM-08-039 | 4321 | 2011-07-01 | SUB | 2012-12-31 | IPL Hubbard 34kV/dist. Sub | substation |  | 34 |  |  | Retire IPL Hubbard Sub |  | IA |  |  | Under Construction | 0 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2348 | 2009-09-25 | ITCM-08-025 | 4341 | 2011-07-01 | SUB | 2011-12-31 | Beaver Rock | new switching station | 1 | 69 |  |  | Construct a new 3-terminal 69kV switching station along the Beaver Channel-Rock Creek 69kV line. |  | IA |  |  | Under Construction | 1553178 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2348 | 2009-09-25 | ITCM-08-025 | 4340 | 2011-07-01 | LN | 2011-12-31 | Beaver Rock | Beaver Channel | 1 | 69 |  | 103/103 MVA | Tap Beaver Channel-Rock Creek 69kV for new switching station. |  | IA |  |  | Under Construction | 20000 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2348 | 2009-09-25 | ITCM-08-025 | 4338 | 2011-07-01 | LN | 2011-12-31 | Beaver Rock | Comanche Tap | 1 | 69 |  | 77/77 MVA | Tie new CIPCO 69kV line from Comanche REC to Beaver Rock. |  | IA |  | 0.75 | Under Construction | 0 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2348 | 2009-09-25 | ITCM-08-025 | 4339 | 2011-07-01 | LN | 2011-12-31 | Beaver Rock | Rock Creek | 1 | 69 |  | 130/130 MVA | Tap Beaver Channel-Rock Creek 69kV for new switching station. The Rock Creek-Beaver Rock 69kV line will be N.O. |  | IA |  |  | Under Construction | 20000 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2353 | 2009-09-25 | ITCM-08-031 | 4344 | 2010-09-28 | SUB | 2011-12-31 | Big River Breaker(Hunt Woods) Station | new switching station |  | 69 |  |  | Construct a new 3-terminal 69kV switching station where the Big River REC line taps the Agency-Sawyer 69kV line. |  | IA |  |  | Planned | 1666427 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | 4389 | 2011-07-01 | SUB | 2013-12-31 | Fairbank | new switching station | 1 | 69 |  |  | Construct a new 3-terminal 69kV switching station, at the existing Fairbank substation. |  | IA |  |  | Planned | 1522187 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | 4390 | 2011-07-01 | LNrb | 2013-12-31 | Fairbank Tap | Fairbank Switching station | 1 | 69 |  | 77/77 MVA | Rebuild the 2.9 mile tap from the new Fairbank SS-Fairbank Tap to double circuit.. |  | IA | 2.9 |  | Planned | 1370000 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | 4391 | 2011-07-01 | LN | 2013-12-31 | Fairbank Switching Station | Hazleton | 1 | 69 |  | 77/77 MVA | Build new 69kV line from the Fairbank sub to the existing Hazleton-Oelwein 69kV line. |  | IA |  | 5 | Planned | 2262198 | Engineering |  |  |  |  | NT | A
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | 6417 | 2011-07-01 | SUB | 2013-12-31 | Tripoli | substation |  | 69 |  |  | Reset the existing 69kV relays at Tripoli |  | IA |  |  | Planned | 10000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | 6416 | 2011-07-01 | SUB | 2013-12-31 | Hazleton | substation |  | 69 |  |  | Upgrade the Hazleton 69kV terminal |  | IA |  |  | Planned | 500000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | West | ITCM | 2357 | 2010-06-28 | 0050-01 | 6415 | 2011-07-01 | LN | 2013-12-31 | Hazleton | Oelwein |  | 69 |  |  | Retire portion of the Hazleton-Oelwein 69kV line not needed after theFairbankk 69kV loop is created. |  | IA |  |  | Planned | 67000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | West | ITCM | 2358 | 2008-12-01 | 0011-1 | 4352 | 2011-07-01 | LNrb | 2013-12-31 | Hazleton | Blackhawk | 1 | 161 |  | 326/326 MVA | Rebuild existing line |  | IA | 12 |  | Planned | 5400000 | Planning |  |  | Y |  | Y | A
A in MTEP09 | West | ITCM | 2363 | 2010-06-28 | 0045-01 | 4385 | 2011-07-01 | SUB | 2011-08-30 | Glenworth 161/69kV | new substation | 1 | 161 | 69 |  | Construct a new Glenville 161/69kV 100 MVA substation near the junction of the Hayward-Worth County 161kV line and the DPC Hayward-Twin Lakes 69kV line. |  | MN |  |  | Under Construction | 7240605 | Engineering |  |  |  |  | Y | A
A in MTEP09 | West | ITCM | 2364 | 2009-04-01 | 0046-01 | 4386 | 2011-07-01 | LNrb | 2011-12-31 | Bricelyn | Thompson | 1 | 69 |  | 77/77 MVA | Rebuild 2 miles of the N.O. 69kV Bricelyn tap-Thompson tap to double circuit 69kV line to allow for 2 separate circuits. |  | IA | 2 |  | Planned | 230000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2364 | 2009-04-01 | 0046-01 | 4904 | 2011-07-01 | LNrb | 2011-12-31 | Lincoln REC Tap (DPC) | Golden Oval (DPC) | 1 | 69 |  | 18 MVA | Rebuild 2 miles of the N.O. 69kV Bricelyn tap-Thompson tap to double circuit 69kV line to allow for 2 separate circuits. |  | IA |  | 2 | Planned | 230000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4366 | 2010-09-28 | LNrb | 2013-12-31 | Stuart Muni Tap | Dexter | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 4.75 |  | Planned | 1187500 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4365 | 2010-09-28 | LNrb | 2013-12-31 | Stuart REC Tap | Stuart Muni Tap | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 1.6 |  | Planned | 400000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4368 | 2010-09-28 | LNrb | 2013-12-31 | Diamondhead REC | Redfield | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 2.55 |  | Planned | 637500 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4364 | 2010-09-28 | LNrb | 2013-12-31 | Menlo | Stuart REC Tap | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 4.28 |  | Planned | 1070000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4363 | 2010-09-28 | LNrb | 2013-12-31 | Thompson | Menlo | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 5.5 |  | Planned | 1375000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4362 | 2010-09-28 | LNrb | 2013-12-31 | Anita-Wiota | Adair | 1 | 34 |  | 39/39 MVA | Rebuild 1.2 miles of the Anita-Wiota-Adair line. |  | IA | 1.2 |  | Planned | 300000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4367 | 2010-09-28 | LNrb | 2013-12-31 | Dexter | Diamondhead REC | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 3.2 |  | Planned | 800000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4360 | 2010-09-28 | LNrb | 2013-12-31 | Anita 161kV | Exira REC | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 5 |  | Planned | 1250000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4361 | 2010-09-28 | LNrb | 2013-12-31 | Anita 161kV | Anita-Wiota | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 3.5 |  | Planned | 875000 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4372 | 2011-07-01 | LNrb | 2013-12-31 | Walford | Norway Tap | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 3.3 |  | Planned | 855100 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4379 | 2011-07-01 | LNrb | 2013-12-31 | Conroy Junction | Williamsburg 115kV | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 2.5 |  | Planned | 647805 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4378 | 2011-07-01 | LNrb | 2013-12-31 | Marengo REC | Conroy Junction | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 5 |  | Planned | 1295608 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4376 | 2011-07-01 | LNrb | 2013-12-31 | Pioneer Tap | Marengo South | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 0.25 |  | Planned | 64780 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4373 | 2011-07-01 | LNrb | 2013-12-31 | Walford | Marengo North Tap | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 8.22 |  | Planned | 2129980 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4374 | 2011-07-01 | LNrb | 2013-12-31 | Marengo North Tap | Marengo East | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 0.57 |  | Planned | 147700 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4371 | 2011-07-01 | LNrb | 2013-12-31 | Fairfax REC | Walford | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 4.5 |  | Planned | 1166047 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4370 | 2011-07-01 | LNrb | 2013-12-31 | Fairfax dist. | Fairfax REC | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 0.5 |  | Planned | 129560 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4369 | 2011-07-01 | LNrb | 2013-12-31 | Fairfax 161kV | Fairfax dist. | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 0.5 |  | Planned | 129560 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4375 | 2011-07-01 | LNrb | 2013-12-31 | Marengo East | Pioneer Tap | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 0.3 |  | Planned | 77735 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2369 | 2009-09-25 | ITCM-08-007 | 4377 | 2011-07-01 | LNrb | 2013-12-31 | Marengo South | Marengo REC | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 1 |  | Planned | 259125 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2370 | 2009-09-25 | ITCM-08-012 | 4381 | 2010-09-28 | LNrb | 2011-12-31 | Monmouth Tap | Monmouth dist | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 0.4 |  | Planned | 96475 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2370 | 2009-09-25 | ITCM-08-012 | 4382 | 2010-09-28 | LNrb | 2011-12-31 | Monmouth Tap | Monmouth REC | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 1.6 |  | Planned | 385910 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2370 | 2009-09-25 | ITCM-08-012 | 4380 | 2010-09-28 | LNrb | 2011-12-31 | Andrew Tap | Andrew dist | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). |  | IA | 5.75 |  | Planned | 1386865 | [5 empty] | NT | A
A in MTEP09 | West | ITCM | 2371 | 2009-09-25 | ITCM-08-041 | 4383 | 2011-02-15 | SUB | 2013-12-31 | Marengo | new switching station | 1 | 69 |  |  | Construct a new 3-terminal 69kV switching station at the existing Marengo 34kV sub. This work needs to be completed for 69kV operation. |  | IA |  |  | Planned | 1900000 | Engineering |  |  |  |  | NT | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 2973 | 2011-02-15 | TEQ | 2012-12-31 | Hazelton | 345 termination |  | 345 |  | 1195 | Expand ring bus to a five breaker ring bus (min 2000 amp). Add one 345kV CB . Extend existing single dead-end tower to double dead-end tower. Four existing 345kV switches rated 1600 amps replaced with 2000 amp switches. | J7 | IA |  |  | Planned | 1080000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 2974 | 2011-02-15 | TEQ | 2012-12-31 | Salem | 345 termination |  | 345 |  | 1195 | Expand ring bus to a five breaker ring bus (min 2000 amp). Add one 345kV CB. Extend existing single dead-end tower to double dead-end tower. Four existing 345kV switches rated 1600 amps replaced with 2000 amp switches. | J7 | IA |  |  | Planned | 2280000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 4906 | 2011-02-15 | TX | 2012-12-31 | Salem | Transformer | 2 | 345 | 161 | 448 | Upgrade Salem 345 sub & add 2nd 345/161kV transformer | J7 | IA |  |  | Planned | 5650000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 5390 | 2011-02-15 | LN | 2012-12-31 | Liberty | Lore | 1 | 161 |  |  | Rebuild a portion of the 161kV line to 326 MVA capacity and install OPWG shield wire the entire distance. | J7 | IA | 10.8 |  | Planned |  | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 5389 | 2011-02-15 | LN | 2012-12-31 | Dundee | Liberty | 1 | 161 |  | 326 MVA | Rebuild the 161kV line to 326 MVA capacity. | J7 | IA | 1.94 |  | Planned |  | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 5388 | 2011-02-15 | LN | 2012-12-31 | Hazleton | Dundee | 1 | 161 |  | 326 MVA | Rebuild the 161kV line to 326 MVA capacity. | J7 | IA | 18.05 |  | Planned |  | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1340 | 2010-06-28 | ITCM-08-037 | 4905 | 2011-02-15 | LN | 2012-12-31 | Salem | Hazleton | 1 | 345 |  | 1195 | Construct a new 345-161kV dbl ckt line(54 miles) and all new ROW for 27 miles of new single ckt 345kV. | J7 | IA |  | 81 | Planned | 110000000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1618 | 2009-09-25 |  | 2720 | 2011-07-01 | LNrb | 2013-06-01 | Heron Lake | Lakefield Jct | 1 | 161 |  | 446/446 MVA | Rebuild |  | MN | 17 |  | Planned | 14000000 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | West | ITCM | 1619 | 2009-09-25 | 333906GMnd | 2725 | 2011-07-01 | Remove | 2011-12-31 | East Calamus T | Maquoketa | 1 | 161 |  |  | remove model branch |  | IA |  |  | Planned | [6 empty] | Y | A
A in MTEP08 | West | ITCM | 1619 | 2009-09-25 | 333906GMnd | 2723 | 2011-07-01 | LN | 2011-12-31 | East Calamus | Grand Mound | 1 | 161 |  | 200/200 MVA | New 161kV line |  | IA |  |  | Planned | [6 empty] | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2751 | 2011-07-01 | TX | 2011-08-30 | Iowa Falls Industrial | transformer | 1 | 115 | 69 | 35 MVA | REMOVE transformer branch |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2737 | 2010-06-28 | LNrb | 2011-12-31 | Iowa Falls | Nuthatch | 1 | 161 |  | 446 MVA | Rebuild 115kV to 161kV line |  | IA | 2.65 | 0 | Planned | 1000000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2753 | 2010-06-28 | TX | 2011-12-31 | Iowa Falls | transformer | 2 | 115 | 34 | 20 MVA | REMOVE transformer branch |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2735 | 2010-06-28 | LNrb | 2011-12-31 | Iowa Falls Industrial | Iowa Falls | 1 | 161 |  | 446 MVA | Rebuild old IA Falls-IA Falls Industrial Tap 115kV to 161kV line. (operate at 115 kV until 2013 conversion completion) (1.54 miles IA Falls Ind Tap-IA Falls Ind already built to 161kV. |  | IA | 2.75 | 0 | Planned | 580000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2752 | 2010-06-28 | TX | 2011-12-31 | Iowa Falls | transformer | 1 | 115 | 34 | 20 MVA | REMOVE transformer branch |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2734 | 2010-06-28 | LNrb | 2012-12-31 | Eldora | Iowa Falls Industrial | 1 | 161 |  | 326/326 MVA | Rebuild Eldora-IA Falls Ind Tap 115kV to 161kV line.(operate at 115 kV until 2013 conversion completion) Build a new completely separate ROW 2 mile 161kV line section from the approximate IA Falls Ind Tap location to the IA Falls Industrial sub. |  | IA | 10.7 | 2 | Planned | 6000000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2745 | 2008-10-01 | TX | 2013-12-31 | Eldora | transformer | 1 | 161 | 34 | 20 MVA | Retire Eldora Sub |  | IA |  |  | Planned | 100000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2742 | 2008-10-01 | Remove | 2013-12-31 | Iowa Falls Industrial Tap | Iowa Falls Industrial | 1 | 115 |  |  | REMOVE model branch |  | IA | 1.54 | 0 | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2739 | 2008-10-01 | Remove | 2013-12-31 | Wellsburg | Eldora | 1 | 115 |  |  | REMOVE model branch |  | IA | 11.5 | 0 | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2741 | 2008-10-01 | Remove | 2013-12-31 | Iowa Falls Industrial Tap | Iowa Falls | 1 | 115 |  |  | REMOVE model branch |  | IA | 11.59 | 0 | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2754 | 2008-10-01 | TX | 2013-12-31 | Wellsburg | transformer | 1 | 115 | 69 | 50 MVA | REMOVE transformer branch |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2736 | 2010-06-28 | Remove | 2013-12-31 | Iowa Falls Industrial Tap | 3-terminal line | 1 | 161 |  | 262/262 MVA | Iowa Falls Industrial Tap bus (3-terminal line) will be eliminated. |  | IA | 0 | 0 | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2740 | 2008-10-01 | Remove | 2013-12-31 | Eldora | Iowa Falls Industrial Tap | 1 | 115 |  |  | REMOVE model branch |  | IA | 1.21 | 0 | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2749 | 2010-06-28 | TX | 2013-12-31 | Wellsburg | transformer | 1 | 161 | 69 | 100 MVA | Upgrade 115kV xfmr to 161kV |  | IA |  |  | Planned | 1500000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2750 | 2008-10-01 | TX | 2013-12-31 | Eldora | transformer | 1 | 115 | 34 | 20 MVA | REMOVE transformer branch |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2733 | 2010-06-28 | LNrb | 2013-12-31 | Wellsburg | Eldora | 1 | 161 |  | 326/326 MVA | Rebuild Wellsburg-Eldora 115kV to 161kV line.(operate at 115 kV until 2013 conversion completion) |  | IA | 11 | 0 | Planned | 5500000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2732 | 2010-06-28 | LNrb | 2013-12-31 | Marshalltown | Wellsburg | 1 | 161 |  | 326/326 MVA | Rebuild 115kV to 161kV line (operate at 115 kV until 2013 conversion completion) |  | IA | 23.8 | 0 | Planned | 6900000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1640 | 2008-10-01 | MtwnFnkln161 | 2738 | 2008-10-01 | Remove | 2013-12-31 | Marshalltown | Wellsburg | 1 | 115 |  |  | REMOVE model branch |  | IA | 27 | 0 | Planned | 0 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1645 | 2009-09-25 | LeonCap | 2759 | 2010-09-28 | CAP | 2011-12-31 | Leon | Cap Bank | 1 | 69 |  | 7.2 MVAR | new 69kV Cap Bank |  | IA |  |  | Planned | 2511808 | Planning |  |  |  |  | NT | A
A in MTEP08 | West | ITCM | 1744 | 2009-09-25 | GM-MAQ | 3546 | 2010-09-28 | LNrc | 2016-12-31 | Maquoketa | Grand Mound | 1 | 161 |  | 326/326 MVA | Reconductor |  | IA | 14.5 |  | Planned | 10150000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1747 | 2009-09-25 | WORTH | 3554 | 2011-07-01 | TX | 2011-05-31 | Elk | transformer | 1 | 161 | 69 | 100 MVA | Upgrade transformer |  | MN |  |  | Under Construction | 3049198 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1747 | 2009-09-25 | WORTH | 5534 | 2011-07-01 | SUB | 2011-12-31 | Elk | substation |  | 161 | 69 |  | Add a 161kV Elk bus tie breaker and 161kV breaker on the line to Brewster and add new control building. |  | MN |  |  | Under Construction | 900000 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 1747 | 2009-09-25 | WORTH | 3555 | 2011-07-01 | TX | 2011-12-31 | Elk | transformer | 2 | 161 | 69 | 100 MVA | Upgrade transformer |  | MN |  |  | Under Construction | 3049198 | Planning |  |  |  |  | Y | A
A in MTEP08 | West | ITCM | 2108 | 2009-09-25 | G358 | 2821 | 2011-02-15 | SUB | 2011-10-31 | G358 GSU Substation | new switching station | 1 | 161 | 34.5 |  | Facilities, excluding the Transmission Owner Interconnection Facilities, required for a 4 terminal, 3 breaker switching station |  | MN |  |  | Planned | 3600000 | Planning | Network |  | Y |  | Y | A
A in MTEP08 | West | ITCM | 2108 | 2009-09-25 | G358 | 2822 | 2011-02-15 | LN | 2011-10-31 | Winnebago | WinnCo | 1 | 161 |  |  | Transmission line taps to new 161 kV switching station. |  | MN |  |  | Planned | 250000 | Planning | Network |  | Y |  | Y | A
A in MTEP08 | West | ITCM | 2108 | 2009-09-25 | G358 | 4030 | 2011-02-15 | COM | 2011-10-31 | Microwave communication network | [5 empty] | Upgrade Transmission Owner's microwave communication network |  | MN |  |  | Planned | 200000 | Planning | Network |  | Y |  | Y | A
A in MTEP08 | West | ITCM | 2108 | 2009-09-25 | G358 | 2824 | 2011-02-15 | RLY | 2011-10-31 | WinnCo | substation | 1 | 161 |  |  | Upgrade Winnebago Junction substation relays and carrier to accommodate the new switching station |  | MN |  |  | Planned | 56848 | Planning | Network |  | Y |  | Y | A
A in MTEP08 | West | ITCM | 2108 | 2009-09-25 | G358 | 2823 | 2011-02-15 | RLY | 2011-10-31 | Winnebago Junction | substation | 1 | 161 |  |  | Upgrade Winnebago Junction substation relays and carrier to accommodate the new switching station |  | MN |  |  | Planned | 110000 | Planning | Network |  | Y |  | Y | A
A in MTEP06 | West | ITCM | 1289 | 2009-04-01 | 11 | 2120 | 2011-07-01 | LNrb | 2012-03-30 | Belle Plaine | Stoney Point | 1 | 115 |  | 233/233 | Rebuild | I8 | IA | 27 |  | Under Construction | 8208000 | Planning |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1289 | 2009-04-01 | 11 | 6411 | 2011-07-01 | TEQ | 2013-12-31 | Belle Plaine | terminal equipment |  | 161 |  |  | Replace BKRs 1420 & 1430 |  | IA |  |  | Planned | 580000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1289 | 2009-04-01 | 11 | 6412 | 2011-07-01 | TEQ | 2013-12-31 | Stoney Point | terminal equipment |  | 161 |  |  | Replace BKRs 1410, 3250, & 3630 |  | IA |  |  | Planned | 2200000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1289 | 2009-04-01 | 11 | 6413 | 2011-07-01 | TEQ | 2013-12-31 | Marshalltown | terminal equipment |  | 161 |  |  | Replace BKR postion 1450 |  | IA |  |  | Planned | 365000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1289 | 2009-04-01 | 11 | 6414 | 2011-07-01 | TEQ | 2013-12-31 | Toledo | terminal equipment |  | 161 |  |  | Add BKRs |  | IA |  |  | Planned | 2300000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1342 | 2009-04-01 | 3 | 5632 | 2011-07-01 | SUB | 2014-12-31 | Lewis Fields | new 161-115 kV Substation | 1 | 161 |  | 558 MVA | Add breakers & associated equipment(bus, control building, relays, etc.) for the new 161-115 kV Lewis Fields substation. | J8 | IA |  |  | Planned | 4300000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1342 | 2009-04-01 | 3 | 2209 | 2011-07-01 | TX | 2014-12-31 | Lewis Fields | transformer | 1 | 161 | 115 | 250/250 MVA | new transformer | J8 | IA |  |  | Planned | 6200000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1342 | 2009-04-01 | 3 | 4902 | 2011-07-01 | TEQ | 2014-12-31 | Hiawatha | new 161 kV line terminal | 1 | 161 |  | 558 MVA | Add 161 kV breaker & associated equipment for the new 161 kV line terminal to Lewis Fields. | J8 | IA |  |  | Planned | 500000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1342 | 2009-04-01 | 3 | 2208 | 2011-07-01 | LN | 2014-12-31 | Lewis Fields | Hiawatha | 1 | 161 |  | 326/326 MVA | new line | J8 | IA |  | 8.5 | Planned | 8151600 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1342 | 2009-04-01 | 3 | 5633 | 2011-07-01 | TX | 2014-12-31 | Lewis Fields | Transformer | 1 | 161 | 115 | 250 MVA | Install new 161-115 kV transformer | J8 | IA |  |  | Planned | 1900000 | Engineering |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1344 | 2009-09-25 |  | 5391 | 2011-07-01 | LN | 2014-12-31 | Arnold | Morgan Valley | 1 | 161 |  | 326 MVA | Tap the Arnold-Fairfax 161kV line for in and out at Morgan Valley | J7 | IA |  |  | Planned | 150000 | Planning |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1344 | 2009-09-25 |  | 5392 | 2011-07-01 | LN | 2014-12-31 | Morgan Valley | Fairfax | 1 | 161 |  | 326 MVA | Tap the Arnold-Fairfax 161kV line for in and out at Morgan Valley | J7 | IA |  |  | Planned | 150000 | Planning |  |  |  |  | Y | A
A in MTEP06 | West | ITCM | 1344 | 2009-09-25 | 5 | 2212 | 2011-07-01 | TX | 2014-12-31 | Morgan Valley | transformer | 1 | 345 | 161 | 335 | new substation | J8 | IA |  |  | Planned | 8750000 | [5 empty] | Y | A
A in MTEP06 | West | ITCM | 1344 | 2009-09-25 | 5 | 2211 | 2011-07-01 | LN | 2014-12-31 | Morgan Valley | Beverly | 1 | 161 |  | 335 | new line | J8 | IA |  | 7.9 | Planned | 5530000 | [5 empty] | Y | A
A in MTEP09 | West | MDU | 1355 | 2006-10-15 |  | 2242 | 2011-07-01 | SUB | 2011-09-30 | Heskett | Additional 230/115 kV Switchyard |  | 230 | 115 | 200 MVA | Switchyard in parallel w/ existing Heskett switchyard | D4 | ND |  |  | Planned | 9500000 |  |  |  | Y |  | Y | A
A in MTEP09 | West | MDU | 1355 | 2006-10-15 |  | 2241 | 2010-06-28 | CAP | 2014-12-31 | Heskett | Capacitor |  | 115 |  | 30 MVAr |  | D4 | ND |  |  | Planned | 1500000 |  |  |  | Y |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 4558 | 2011-06-24 | SUB | 2012-06-30 | Essar steel plant sub (McCarthy Lake) | Substation Equipment |  | 230 | 14 | 166 | Essar Substation high side equipment |  | MN |  |  | Under Construction | 3700000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 4559 | 2011-06-24 | SUB | 2012-06-30 | Essar Mine Sub (Calumet) | Substation Equipment |  | 230 | 14 | 166 | Essar Substation high side Equipment |  | MN |  |  | Under Construction | 4000000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 4560 | 2011-06-24 | LN | 2012-06-30 | Essar Mine Sub (Calumet) | Essar steel plant sub (McCarthy Lake) | 1 | 230 |  | 465 | Essar new Line |  | MN |  | 2.5 | Planned | 2200000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 4556 | 2011-06-24 | LN | 2012-06-30 | Essar Steel Sub (McCarthy Lake) | Shannon | 1 | 230 |  | 423 | Essar 94L Line reroute |  | MN |  | 8 | Planned | 4100000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 4555 | 2011-06-24 | LN | 2012-06-30 | Boswell | Essar Mine Sub (Calumet) | 1 | 230 |  | 423 | Essar Line 94L Line reroute |  | MN |  | 16 | Planned | 6100000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 4557 | 2011-06-24 | LN | 2014-07-30 | Blackberry | Essar Steel Sub (McCarthy Lake) | 1 | 230 |  | 465 | Essar new Line and new bay at McCarthy Lake (facility #4558) |  | MN |  | 16 | Planned | 12900000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2547 | 2009-12-08 | Essar | 5438 | 2011-06-24 | SUB | 2014-07-30 | Blackberry | Substation Equipment |  | 230 | 14 | 465 | line entrance & breaker |  | MN |  |  | Planned | 1100000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2761 | 2009-11-13 | Dunka Rd | 4780 | 2011-01-11 | SUB | 2012-12-30 | Dunka Road | Substation Equipment |  | 115 | 14 | 15 | Substation Equipment & Transformer |  | MN |  |  | Planned | 3000000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2762 | 2009-11-13 | Airpark | 4776 | 2011-01-11 | SUB | 2012-12-16 | Airpark | Substation Equipment |  | 115 | 34.5 | 39 | Substation Equipment & Transformer |  | MN |  |  | Under Construction | 2100000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MP | 2762 | 2009-11-13 | Airpark | 4778 | 2011-06-24 | SUB | 2013-06-30 | Airpark | Substation Equipment |  | 115 | 14 | 39 | Substation Equipment & Transformer |  | MN |  |  | Under Construction | 2005000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | west | MP | 3091 | 2009-12-08 | 28L reroute | 5409 | 2011-03-25 | line | 2012-05-30 | Boswell | Nashwaulk | 1 | 115 |  | 144 | reroute existing MP Line #28 |  | MN |  | 7.5 | planned | 3190000 | planning |  |  |  |  | Y | A
A in MTEP09 | West | MP | 2552 | 2009-11-13 | Skibo | 4554 | 2011-01-11 | LN | 2012-12-01 | Skibo | Hoyt Lakes | 1 | 138 |  | 202 | new line |  | MN |  | 3 | Planned | 2540000 | planning |  |  |  |  | Y | A
A in MTEP09 | West | MP | 2759 | 2009-11-13 | Laskin | 4782 | 2011-03-25 | SUB | 2012-06-01 | Laskin | Substation Equipment |  | 115 | 46 | 28 | Substation Transformer |  | MN |  |  | Planned | 500000 | Engineering |  |  |  |  | Y | A
A in MTEP09 | West | MP | 2763 | 2009-11-13 | LSPI | 4779 | 2011-06-24 | SUB | 2011-08-30 | LSPI | Substation Equipment |  | 115 | 34.5 | 30 | Substation Equipment & Transformer |  | MN |  |  | Under Construction | 600000 | Engineering |  |  |  |  | Y | A
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | 2663 | 2010-09-22 | SUB | 2012-07-01 | Swatara 230/115 kV | transformer |  | 230 | 115 |  | New 230/115 kV Swatara Substation |  | MN |  |  | Planned | 8817640 |  | Network |  | Y |  | Y | A
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | 2659 | 2010-09-22 | CB | 2012-07-01 | Blackberry 230 |  |  | 230 |  |  | Blackberry Sub: 3 each-230 kV circuit breakers, 9 each-230 kV air break switches, structural steel, bus work and control equipment |  | MN |  |  | Planned | 3163583 |  | Network |  | Y |  | Y | A
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | 2661 | 2010-09-22 | LN | 2012-07-01 | Swatara 230 | Riverton 230 |  | 230 |  |  | Swatara to Riverton 33.2 Miles |  | MN |  |  | Planned | 24878937 |  | Network |  | Y |  | Y | A
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | 2662 | 2010-09-22 | SUB | 2012-07-01 | Blackberry 230 kV sub |  |  | 230 |  |  | 230 kV Bus Position for Boswell-Riverton Line at Boswell |  | MN |  |  | Planned | 3017108 |  | Network |  | Y |  | Y | A
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | 2664 | 2010-09-22 | SUB | 2012-07-01 | Riverton 230 kV sub |  |  | 230 |  |  | 230 kV Bus Position for Boswell-Riverton Line at Riverton |  | MN |  |  | Planned | 2372682 |  | Network |  | Y |  | Y | A
A in MTEP07 | West | MP | 1025 | 2009-11-13 | G519 | 2660 | 2010-09-22 | LN | 2012-07-01 | Boswell 230 | Swatara 230 |  | 230 |  |  | Boswell to Swatara 34.6 Miles |  | MN |  |  | Planned | 34069591 |  | Network |  | Y |  | Y | A
A in MTEP05 | West | MP | 600 | 2010-04-05 |  | 2943 | 2011-06-24 | SwSta | 2012-02-28 | Scearcyville | switching station |  | 115 |  |  | new switching station | H5 | MN |  |  | Under Construction | 2200000 | Engineering |  |  |  |  | Y | A
A in MTEP10 | West | MPC, XEL, OTP, MP | 3156 | 2010-04-05 | Cass Lake -Nary-Helga -Bemidji | 5540 | 2010-04-05 | LN | 2013-12-31 | Helga 115 kV | Bemidji 115 kV | 1 | 115 | 115 | 144 | Structural Improvements |  | MN | 7.67 |  | Planned | 66000 | Planning |  |  | Y |  | Y | A
A in MTEP10 | West | MPC, XEL, OTP, MP | 3156 | 2010-04-05 | Cass Lake -Nary-Helga -Bemidji | 5537 | 2010-04-05 | LN | 2013-12-31 | Cass Lake 115 kV | Nary 115 kV | 1 | 115 | 115 | 200 | Reconductor 115 kV transmission line |  | MN | 11.05 |  | Planned | 3900000 | Planning |  |  | Y |  | Y | A
A in MTEP10 | West | MPC, XEL, OTP, MP | 3156 | 2010-04-05 | Cass Lake -Nary-Helga -Bemidji | 5539 | 2010-04-05 | LN | 2013-12-31 | Nary 115 kV | Helga 115 Kv | 1 | 115 | 115 | 144 | Structural Improvements |  | MN | 4.96 |  | Planned | 33000 | Planning |  |  | Y |  | Y | A
A in MTEP06 | West | MPC, XEL, OTP, MP | 279 | 2008-10-01 | Bemidji-Grand Rapids | 1098 | 2011-07-01 | LN | 2012-12-31 | Boswell | Wilton | 1 | 230 |  | 495 | Add a new 230 kV line between Boswell and Wilton | H4 | MN |  | 72 | Planned | 98530747 | Planning |  |  | Y |  | Y | A
A in MTEP10 | West | MPC,XEL,OTP,MP | 3156 | 2010-04-05 | Cass Lake -Nary-Helga -Bemidji | 3584 | 2011-07-01 | TX | 2012-12-31 | Cass Lake 230 kV | Cass Lake 115 kV | 1 | 230 | 115 | 187 MVA | Add a 230/115 kV Transformer at Cass Lake |  | MN |  |  | Planned | 6400000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | MPW | 2934 | 2010-09-21 | MPW-SS | 5106 | 2010-09-21 | TX | 2014-06-01 | South 161/69 kV | transformer | 1 | 161 | 69 | 134 | Replace 75 MVA transformer |  | IA |  |  | Planned | 5400000 | Planning |  |  |  |  | Y | A
A in MTEP10 | West | NWE | 3092 | 2009-11-16 | 2012-02 | 5410 | 2009-11-16 | LNrb | 2011-06-01 | Lake 26 | Webb Lake |  | 69 |  | 15 | Rebuild 34.5KV line to Webb Lake at 69KV with horizontal post construction and #4/0 ACSR |  | WI | 2.6 | 0 | Planned | 425000 | [5 empty] | Y | A
A in MTEP08 | West | NWE | 2011 | 2009-11-16 | 2009-03 | 3992 | 2009-11-16 | LNrb | 2011-06-01 | Frederic | Lewis |  | 69 |  | 31 | Rebuild the 34.5Kv system between Frederic and Lewis sub at 69KV with 477ASCR and horizontal post construction. |  | WI | 2.8 | 0 | Planned | 350000 | [5 empty] | Y | A
A in MTEP08 | West | NWE | 2012 | 2009-11-16 | 2010-01 | 3993 | 2009-11-16 | LNrb | 2011-09-01 | Falun | Penta |  | 69 |  | 47 | Rebuild the 34.5Kv system between Falun and Penta sub at 69KV with 477ASCR and horizontal post construction. |  | WI | 4.3 | 0 | Under Construction | 538000 | [5 empty] | Y | A
A in MTEP08 | West | NWE | 2013 | 2009-11-16 | 2010-02 | 3994 | 2009-11-16 | LNrb | 2011-06-01 | Penta | Siren Tap |  | 69 |  | 15 | Rebuild the 34.5Kv system between Penta sub and Siren Tap at 69KV with 477ASCR and horizontal post construction. |  | WI | 1.4 | 0 | Planned | 175000 | [5 empty] | Y | A
A in MTEP08 | West | NWE | 2016 | 2009-11-16 | 2011-02 | 3997 | 2009-11-16 | LNrc | 2012-01-01 | Frederic | Coffee Cup |  | 69 |  | 84 | Reconductor 69KV line with 477ACSR |  | WI | 2 | 0 | Planned | 100000 | [5 empty] | Y | A
A in MTEP08 | West | NWE | 2018 | 2009-11-16 | 2012-01 | 3999 | 2009-11-16 | LN, SUB | 2011-06-01 | Eureka Tap | Centuria |  | 69 | 12.47 |  | Build new 69KV line to Centuria and build Distribution Sub |  | WI | 0 | 4 | Planned | 1200000 | [5 empty] | Y | A
A in MTEP09 | West | OTP | 2751 | 2009-11-18 | New Perham 115/12.5 kV Substation | 4774 | 2011-01-01 | SUB | 2013-12-31 | New Perham | distribution sub |  | 115 | 12.5 | 14 MVA | Build New 115/12.5 kV Substation at Perham to Serve as a Back-up Source for Outage of Primary Source |  | MN |  |  | Planned | 400000 | Proposed |  |  |  |  | Y | A
A in MTEP10 | West | OTP, MPC | 2826 | 2010-04-05 | Enbridge Load Expansion Support | 4966 | 2010-04-05 | CAP | 2015-12-31 | Thief River Falls 115 kV | 15 MVAR capacitor bank |  | 115 |  | 15 MVAR | Install Capacitor Bank on 115 kV at Thief River Falls. One 15 MVAR. Add second bank to existing bank. |  | ND |  |  | Planned | 950000 | Proposed |  |  |  |  | Y | A
A in MTEP10 | West | OTP,MPC | 2826 | 2010-04-05 | Enbridge Load Expansion Support | 4965 | 2011-01-05 | CAP | 2012-12-31 | Karlstad 115 kV | 14 MVAR capacitor bank |  | 115 |  | 14 MVAR | Install Capacitor Bank on 115 kV at Karlstad. One 14 MVAR. |  | ND |  |  | Planned | 950000 | Proposed |  |  |  |  | Y | A
A in MTEP10 | West | SMP | 2166 | 2011-02-25 | St Peter Area | 4005 | 2011-06-30 | LN | 2011-12-01 | Tap Existing Area Line | New Load Serving Sub at St Peter | 1 | 69 | 69 | 72 MVA | Add 7.0 Miles 69kV line and construct new load serving substation at St Peter |  | MN |  | 7 | Under Construction | 6000000 | [5 empty] | NT | A
A in MTEP10 | West | SMP | 2167 | 2011-02-25 | Redwood Falls Area | 4006 | 2011-02-25 | LN | 2011-12-01 | Tap Existing Area Line | New Load Serving Sub at Redwood Falls | 1 | 115 | 115 | 142 MVA | Add 5.2 Miles 115kV line and construct load serving substation at Redwood Falls |  | MN |  | 4 | Planned | 4000000 | [5 empty] | NT | A
A in MTEP10 | West | SMP | 2171 | 2009-11-13 |  | 2992 | 2011-02-25 | GEN | 2011-08-01 | Mora | generator |  | 12.47 |  | 3 MW | additional 3 MW of landfill gas |  | MN |  |  | Under Construction | 3700000 | [5 empty] | Y | A
A in MTEP09 | West | SMP | 2178 | 2008-07-15 | G362 | 4970 | 2011-02-25 | LN | 2011-12-01 | Byron | Line termination |  | 161 |  | 161kV | Byron - Pleasant Valley161 kV Line Terminal Improvements |  | MN |  |  | Under Construction | 715181 |  | Network |  | Y |  | Y | A
A in MTEP10 | West | XEL | 2767 | 2009-12-09 |  | 4795 | 2008-12-01 | TX | 2012-01-01 | Fenton | Transformer | 1 | 115 | 69 | 47 | new transformer |  | MN |  |  | Planned | 2143430 | [5 empty] | Y | A
A in MTEP10 | West | XEL | 2767 | 2009-12-09 |  | 4794 | 2008-12-01 | LN | 2012-01-01 | Fenton | in and out between Chandler tap and Lake Wilson | 1 | 69 |  |  | new line |  | MN |  | 3 | Planned | 1566570 | [5 empty] | Y | A
A in MTEP10 | West | XEL | 3097 | 2011-01-11 |  | 5424 | 2011-01-11 | TX | 2012-06-01 | Monroe County | Transformer | 2 | 161 | 69 | 70 | Install 2nd 70 MVA transformer at Monroe County substation |  | WI |  |  | Planned | 3680000 |  |  |  | N |  | Y | A
A in MTEP10 | West | XEL | 3100 | 2009-11-19 |  | 5431 | 2009-12-09 | TX | 2012-06-01 | Westgate | Transformer | 2 | 115 | 69 | 70 | upgrade to70 MVA |  | MN |  |  | Planned | 2070000 |  |  |  | N |  | Y | A
A in MTEP09 | West | XEL | 1952 | 2008-01-10 |  | 3833 | 2009-07-17 | CAP | 2011-12-01 | Plato Cap Bank | Cap Bank |  | 69 |  | 10 MVAR | New 10 MVAR cap bank at Lester Prairie |  | MN |  |  | Planned | 700000 | MISO |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2157 | 2008-04-07 |  | 2966 | 2011-06-29 | TX | 2011-11-01 | Douglas Co | Transformer | 2 | 115 | 69 | 70 | 2nd 115/69 kV transformer at |  | MN |  |  | Planned | 4435000 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2158 | 2008-04-07 |  | 2968 | 2011-06-29 | LNrc | 2011-09-30 | West Union | Osakis | 1 | 69 |  | 84 | upgrade using lower impedance line |  | MN |  | 5.8 | Planned | 1740000 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2158 | 2008-04-07 |  | 2967 | 2011-06-29 | LNrc | 2011-09-30 | Sauk Center | West Union | 1 | 69 |  | 84 | upgrade using lower impedance line |  | MN |  | 9 | Planned | 2774000 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2160 | 2008-04-07 |  | 2970 | 2009-02-10 | TX | 2012-06-01 | Park Falls | Transformer | 1 | 115 | 34.5 | 47 | Upgrade the transformer to higher rating |  | WI |  |  | Planned | 1677900 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2160 | 2008-04-07 |  | 2971 | 2009-02-10 | TX | 2012-06-01 | Park Falls | Transformer | 2 | 115 | 34.5 | 47 | Upgrade the transformer to higher rating |  | WI |  |  | Planned | 1677900 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2178 | 2008-07-15 | RIGO | 4021 | 2009-07-15 | LN | 2012-06-01 | Pleasant Valley | Byron | 1 | 161 |  | 447 MVA | new 161 kV line from PV to Byron |  | MN |  | 25 | Planned | 9292000 | Scoping estimate |  |  | Y |  | Y | A
A in MTEP09 | West | XEL | 2307 | 2008-10-01 | St. Cloud Loop | 4225 | 2009-02-10 | LN | 2012-06-01 | Benton Co | Mayhew Lake | 1 | 115 |  | 361 MVA | Convert double circuit 115 kV line from Benton Co to St. Cloud tap to bifurcated single circuit, build additional 4 miles of 115 kV line from St. Cloud tap to Mayhew Lake substation. |  | MN |  | 4 | Planned | 3000000 | Indicative |  |  | Y |  | Y | A
A in MTEP09 | West | XEL | 2307 | 2008-10-01 | St. Cloud Loop | 4226 | 2009-02-10 | LN | 2012-06-01 | St. Cloud | Granite City | 1 | 115 |  | 194 MVA | Convert 1 mile of double circuit from St. Cloud tap to Granite City to bifurcated single circuit. |  | MN |  |  | Planned | 100000 | Indicative |  |  | Y |  | Y | A
A in MTEP09 | West | XEL | 2307 | 2008-10-01 | St. Cloud Loop | 4227 | 2009-02-10 | LN | 2012-06-01 | Sauk River | W St. Cloud | 1 | 115 |  | 361 MVA | Upgrade line to 361 MVA |  | MN | 1.4 |  | Planned | 1000000 | Indicative |  |  | Y |  | Y | A
A in MTEP09 | West | XEL | 2307 | 2008-10-01 | St. Cloud Loop | 4228 | 2009-02-10 | SUB | 2012-06-01 | Mayhew Lake substation | Breakers |  | 115 |  |  | Upgrade to 115 kV ring bus |  | MN |  |  | Planned | 2000000 | Indicative |  |  | Y |  | Y | A
A in MTEP09 | West | XEL | 2308 | 2008-10-01 |  | 4236 | 2011-06-29 | LN | 2011-09-01 | Lowry tap | Glenwood (XCEL) | 1 | 69 |  | 100 MVA | Upgrade to 477 ACSR |  | MN | 0.04 |  | Planned | 17058 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2308 | 2008-10-01 |  | 4235 | 2011-06-29 | LN | 2011-09-01 | Glenwood (GRE) | Lowry tap | 1 | 69 |  | 100 MVA | Upgrade to 477 ACSR |  | MN | 2.8 |  | Planned | 11941126 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2308 | 2008-10-01 |  | 4234 | 2011-06-29 | LN | 2011-09-01 | Sedan | Glenwood (GRE) | 1 | 69 |  | 100 MVA | Upgrade to 477 ACSR |  | MN | 5 |  | Planned | 2132344 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2308 | 2008-10-01 |  | 4233 | 2011-06-29 | LN | 2011-09-01 | Grove Lake | Sedan | 1 | 69 |  | 100 MVA | Upgrade to 477 ACSR |  | MN | 5.3 |  | Planned | 2260284 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2309 | 2009-05-11 |  | 4229 | 2009-05-11 | LN | 2012-06-01 | Maple Lake | Annandale | 1 | 69 |  | 100 MVA | Upgrade to 477 ACSR |  | MN | 6 |  | Planned | 2487000 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL | 2772 | 2009-02-10 | South Minneapolis | 4838 | 2011-01-11 | SUB | 2012-06-01 | Midtown | Sidtribution Substation |  | 115 | 13.8 |  | New distribution substation |  | MN |  |  | Planned | 11120000 | [5 empty] | Y | A
A in MTEP09 | West | XEL | 2772 | 2009-02-10 | South Minneapolis | 4836 | 2011-01-11 | SUB | 2012-06-01 | Hiawatha | Distribution Substation |  | 115 | 13.8 |  | New distribution substation Between Elliot Park and Southtown |  | MN |  |  | Planned | 14270000 | [5 empty] | Y | A
A in MTEP09 | West | XEL | 2772 | 2009-02-10 | South Minneapolis | 4837 | 2011-01-11 | LN | 2012-06-01 | Hiawatha | Midtown | 1,2 | 115 |  | ~360 | Double Circuit 1.25 mile line |  | MN |  | 1.25 | Planned | 1500000 | [5 empty] | Y | A
A in MTEP08 | West | XEL | 675 | 2008-06-30 |  | 1364 | 2011-01-11 | LNup | 2014-06-01 | Westgate | Scott County | 1 | 115 |  | 194 MVA | upgrade line |  | MN | 20.1 |  | Planned | 14000000 | [5 empty] | Y | A
A in MTEP08 | West | XEL | 1487 | 2006-10-15 |  | 2306 | 2009-06-26 | LN | 2011-12-31 | Somerset | Stanton | 1 | 69 |  | 84 | New 69 kV line |  | WI |  |  | Planned | 9247500 | [5 empty] | NT | A
A in MTEP08 | West | XEL | 1549 | 2007-04-10 | ECL-HYD 161 kV conversion | 2638 | 2011-03-25 | LNrc | 2011-09-01 | Wheaton | Eau Claire |  | 161 |  | 434 | Reconductor 4.3 Miles of 161 kV line with 795 ACSS conductor |  | WI | 4.3 |  | Planned | 645000 | [5 empty] | Y | A
A in MTEP08 | West | XEL | 1549 | 2007-04-10 | ECL-HYD 161 kV conversion | 2633 | 2011-01-11 | LNrb | 2011-12-01 | Eau Claire | Hallie |  | 161 |  | 434 | Rebuild 69 kV corridor to 161 kV, convert Hallie Substation to 161 kV |  | WI | 1.5 |  | Planned | 2425000 | [5 empty] | Y | A
A in MTEP08 | West | XEL | 1957 | 2008-01-10 | ECP2 | 3839 | 2009-06-26 | LNrb | 2012-06-01 | new sub | London - Madison tap | 1 | 69 |  | 84 MVA | Rebuild 69 kV line from London/Madison Tap to new substation |  | WI |  |  | Planned | 0 | [5 empty] | NT | A
A in MTEP08 | West | XEL | 1957 | 2008-01-10 | ECP2 | 3838 | 2009-06-26 | SUB | 2012-06-01 | Southwest of Eau Claire (new sub) | new sub | 1 | 161 | 69 |  | New 161/69 kV Substation southwest of Eau Claire where Alma – Elk Mound 161 kV line intersects with Shawtown – Naples 69 kV line |  | WI |  |  | Planned | 7080000 | [5 empty] | Y | A
A in MTEP08 | West | XEL | 1958 | 2008-01-10 | NWWLS | 3843 | 2008-10-01 | LNcnv | 2012-12-01 | Edge Water substation | upgrade to 161 kV |  | 161 |  |  | Convert the Edgewater 69 kV load to the new 161 kV line. Construct 161 kV facilities at Edgewater Substation |  | WI |  |  | Planned | 0 | [5 empty] | Y | A
A in MTEP08 | West | XEL | 1958 | 2008-01-10 | NWWLS | 3842 | 2009-06-26 | LN | 2012-12-01 | Stone Lake | Edge Water | 1 | 161 |  | 434 MVA | New 161 kV line from Stone Lake to Edgewater |  | WI |  |  | Planned | 26185641 | [5 empty] | Y | A
A in MTEP06 | West | XEL | 1458 | 2009-05-11 | G349 | 2496 | 2009-06-26 | LN | 2011-11-30 | Yankee | feeders |  | 34.5 |  |  | four new 50 MW underground feeder lines and all associated equipment |  | MN |  |  | Planned | 2202000 |  | Interconnection |  |  |  | NT | A
A in MTEP09 | West | XEL, GRE | 2156 | 2008-04-07 | N Mankato | 2964 | 2009-02-10 | SUB | 2011-06-01 | St. Thomas | substation | 1 | 115 | 69 | 112 | New 115/69 kV substation |  | MN |  |  | Planned | 5000000 | Scoping estimate |  |  |  |  | NT | A
A in MTEP09 | West | XEL, GRE | 2156 | 2008-04-07 | N Mankato | 2963 | 2009-02-10 | LN | 2011-06-01 | Helena | St. Thomas | 1 | 115 | 115 | 318 | New 6 mile 115 kV line |  | MN |  | 6 | Planned | 2750000 | Scoping estimate |  |  |  |  | Y | A
A in MTEP09 | West | XEL, GRE | 2156 | 2008-04-07 | N Mankato | 2962 | 2009-02-10 | SUB | 2011-06-01 | Helena | Transformer | 1 | 345 | 115 | 448 | New 345/115 kV transformer at Helena substation |  | MN |  |  | Planned | 7250000 | Scoping estimate |  |  |  |  | Y | A
A in MTEP09 | West | XEL, GRE | 2156 | 2008-04-07 | N Mankato | 2965 | 2009-02-10 | SwSta | 2011-06-01 | Lesueur Tap | substation |  | 69 |  |  | 69 kV switching station at LeSueur |  | MN |  |  | Planned | 2450000 | Scoping estimate |  |  |  |  | NT | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 1677 | 2010-07-12 | LN | 2012-12-15 | North Rochester | Northern Hills | 1 | 161 |  | 400 | new line and termial works | I6 | MN |  | 12.6 | Planned | 23068992 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 1675 | 2010-07-12 | TX | 2012-12-15 | North Rochester | Transformer | 1 | 345 | 161 | 448 | new transformer and terminal works | I6 | MN |  |  | Planned | 19346751 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 2984 | 2010-07-12 | SUB | 2012-12-15 | North Rochester | substation | 1 | 345 |  |  | new substation | I6 | MN |  |  | Planned | 6164382 | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 2983 | 2010-07-12 | SUB | 2013-03-31 | Hampton Corner and North Rochester | substation | 1 | 345 |  |  | new substation | I6 | MN |  |  | Planned | 9395227 | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 1676 | 2010-07-12 | TX | 2014-03-31 | North La Crosse | Transformer | 1 | 345 | 161 | 448 | new transformer and terminal works | J6 | WI |  |  | Planned | 11744034 | Engineering |  |  | Y |  | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 2647 | 2010-07-12 | LN | 2014-03-31 | North Rochester | North La Crosse | 1 | 345 |  | 2050 | new line and termial works | I6 | MN |  | 82 | Planned | 292987075 | Engineering |  |  | Y | Y | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 1678 | 2010-07-12 | SUB | 2015-03-30 | North Rochester | Chester | 1 | 161 |  | 400 | new line | I6 | MN |  | 14 | Planned | 11137053 | Engineering |  |  |  |  | Y | A
A in MTEP08 | West | XEL, RPU, SMPA, DPC, WPPI | 1024 | 2007-05-22 | CAPX TC-Roch-Lax | 1673 | 2010-07-12 | LN | 2015-09-30 | Hampton Corner | North Rochester | 1 | 345 |  | 2050 | new line | I6 | MN |  | 36 | Planned | 71156485 | Engineering |  |  |  |  | Y | A
B | Central | AmerenIL | 1234 | 2008-02-14 |  | 1933 | 2008-09-23 | LNup | 2014-06-01 | Havana, South | Mason City, West | 1 | 138 |  | 160 | Increase ground clearance on 18.4 miles | J9 | IL | 18.4 |  | Proposed | 642300 | Eng |  |  |  |  | Y | B
B | Central | AmerenIL | 1533 | 2008-02-14 |  | 2610 | 2009-09-14 | TEQ | 2013-12-01 | Washington Street | S. Bloomington | 1 | 138 |  | 255 | Replace terminal equipment at S. Bloomington | K9 | IL |  |  | Proposed | 137000 | [5 empty] | Y | B
B | Central | AmerenIL | 1537 | 2007-04-02 |  | 2614 | 2009-09-14 | TEQ | 2013-06-01 | Mt. Vernon, West | S. Centralia | 1 | 138 |  | 146 | Replace terminal equipment at S. Centralia | K11 | IL |  |  | Proposed | 200000 | [5 empty] | Y | B
B | Central | AmerenIL | 2114 | 2008-02-22 | IP03 | 2839 | 2011-07-05 | LN | 2009-09-30 | Mahomet Substation | Brokaw Substation | 1 | 138 |  |  | Tapping structures installed inline with line #1376: 138 XX Line Extension 477 MCM 30/7 ACSR, 138 YY Line Extension 477 MCM 30/7 ACSR | K9 | IL |  |  | Planned | 237000 |  | Network |  | Y |  | Y | B
B | Central | AmerenIL | 2114 | 2008-02-22 | IP03 | 2838 | 2011-07-05 | SUB | 2013-12-01 | Project IP03 Substation | substation | 1 | 138 |  |  | New (IP03) 138 kV Straight Bus Interconnection Substation, tap existing line #1376 Mahomet Substation to Brokaw Station. | K9 | IL |  |  | Planned | 1845000 |  | Network |  | Y |  | Y | B
B | Central | AmerenIL | 2117 | 2008-12-10 | IP08 | 2846 | 2011-07-05 | LN | 2014-06-01 | El Paso | CE Minok | 1 | 138 |  |  | Tapping structures installed inline with line #1382: 138 kV XX Line Extension 556.5 MCM 26/7 ACSS conductor and 7#8 Alumoweld shield wire, 138 kV YY Line Extension 556.5 MCM 26/7 ACSS conductor and 7#8 Alumoweld shield wire | K9 | IL |  |  | Planned | 230000 |  | Network |  | Y |  | Y | B
B | Central | AmerenIL | 2117 | 2008-12-10 | IP08 | 2845 | 2011-07-05 | SUB | 2014-06-01 | Project IP08 Substation | substation | 1 | 138 |  |  | New 138 kV Straight Bus Interconnection Substation, located north of the tap point to the Transmission Owner’s El Paso substation and south of the tap point to the Transmission Owner’s CE Minok substation on line #1382. | K9 | IL |  |  | Planned | 1661464 |  | Network |  | Y |  | Y | B
B | Central | AmerenIL | 2118 | 2008-12-10 | IP04, IP08 | 2848 | 2011-07-05 | LN | 2014-06-01 | Oglesby Substation | IP08 Substation | 1 | 138 |  |  | Line #1382 & #1384: Reconductor 477 MCM 30/7 ASCR with three phase 556.5 MCM 26/7 ACSS conductor. | K9 | IL |  | 33.3 | Planned |  |  | Network |  | Y |  | Y | B
B | Central | AmerenIL | 2280 | 2008-08-29 |  | 4196 | 2008-08-29 | LN | 2013-06-01 | LaSalle | Oglesby Main | 1 | 138 |  | 256 | Reconductor 477 kcmil ACSR and 336 kcmil ACSR to 1200 A summer emerg. | K8 | IL | 2.16 |  | Planned | 900000 | Engineering |  |  |  |  | Y | B
B | Central | AmerenMO | 2774 | 2009-12-10 | G578 | 4868 | 2011-07-05 | SUB | 2020-11-01 | Adair | Wind Farm | 1 | 161 |  |  | Connect Wind Farm to Adair Sub | I9 | MO |  |  | Proposed |  |  | Network |  | Y |  | Y | B
B | Central | DEM | 1521 | 2007-03-02 | AMIN0067 | 2597 | 2009-02-18 | TEQ | 2016-06-01 | Bloomington 230 (terminal equipment) | Bloomington NW |  | 138 |  | 191 | Replace the 600A 13836 bkr disconnect switches with 2000A switches. New limit 800A Wave Trap. |  | IN |  |  | Planned | 233455 | Engineering |  |  |  |  | Y | B
B | Central | DEM | 3381 | 2010-09-15 | AMOH0361 | 6254 | 2011-03-25 | GEN | 2013-12-31 | Meldahl Dam Gen. | Meldahl Dam Gen. 345kV I-connect Sub | 1 | 345 | 138 |  | Install interconnection substation for Meldahl Dam generator. Install 3-breaker 345kV ring bus, 345-138kV - 120 MVA transformer, loop Feeder 4545 through new substation. Connect independent generator per MISO requirements. |  | OH |  |  | Planned | 8949798 | Engineering 2010$ |  |  |  |  | Y | B
B | Central | DEM, IPL | 1558 | 2011-01-11 | Duke Econ 3 | 3109 | 2011-01-11 | LN | 2013-05-01 | Petersburg | Francisco | 1 | 345 |  | 1195 MVA | Upgrade to fix 1st contingency for the Wheatland breaker close |  | IN |  |  | Proposed | 6420000 | Planning |  |  |  |  | Y | B
B | Central | DEM, IPL | 1558 | 2011-01-11 | Duke Econ 3 | 3110 | 2011-01-11 | LN | 2013-05-01 | Petersburg | Thompson | 1 | 345 |  | 1195 MVA | Upgrade to fix 1st contingency for the Wheatland breaker close |  | IN |  |  | Proposed | 5015000 | Planning |  |  |  |  | Y | B
B | Central | IPL | 1557 | 2009-08-28 | FG14 | 3107 | 2009-08-28 | LN | 2014-01-01 | Pritchard | Franklin Twp | 1 | 345 |  | 956 | New |  | IN |  | 24 | Proposed | 24000000 | MISO per unit |  |  |  |  | Y | B
B | Central | IPL | 1557 | 2009-08-28 | FG14 | 3108 | 2009-08-28 | LN | 2014-01-01 | Franklin Twp | Hanna | 1 | 345 |  | 1386 | New |  | IN |  | 2.75 | Proposed | 2750000 | MISO per unit |  |  |  |  | Y | B
B | Central | IPL | 1557 | 2009-08-28 | FG14 | 3106 | 2009-08-28 | LN | 2014-01-01 | Bloomington | Pritchard | 1 | 345 |  | 1386 | New |  | IN |  | 15 | Proposed | 15000000 | MISO per unit |  |  |  |  | Y | B
B | East | ITC | 1850 | 2008-12-09 |  | 3732 | 2011-01-11 | LN | 2013-12-31 | Hancock | Wixom | 1 | 230 |  |  | New Line resulting from Quaker-Wixom cut into Hancock |  | MI |  |  | Proposed | [6 empty] | Y | B
B | East | ITC | 1850 | 2008-12-09 |  | 3733 | 2011-01-11 | LN | 2013-12-31 | Hancock | Quaker | 1 | 230 |  |  | New Line resulting from Quaker-Wixom cut into Hancock |  | MI |  |  | Proposed | [6 empty] | Y | B
B | East | ITC | 1850 | 2008-12-09 |  | 3734 | 2011-01-11 | TX | 2013-12-31 | Hancock 230/120 kV | Transformer | 1 | 230 | 120 |  | New Transformer |  | MI |  |  | Proposed | 9000000 | [5 empty] | Y | B
B | East | METC | 2809 | 2009-06-26 | 87 | 336 | 2009-06-26 | LNrc | 2014-06-01 | Garfiled | Hemphill | 1 | 138 |  |  | Reconductor | N7 | MI | 9.1 |  | Proposed | 11360000 | [5 empty] | Y | B
B | East | METC | 2809 | 2009-06-26 | 87 | 4453 | 2009-06-26 | LNrc | 2014-06-01 | Hemphill |  |  | 138 |  |  | Relay replacement | N7 | MI |  |  | Proposed | 380000 | [5 empty] | Y | B
B | East | METC | 2822 | 2009-07-24 | new | 5408 | 2009-07-26 | LNrc | 2016-12-01 | Edenville J. | Warren | 1 | 138 |  |  | Reconductor the Edenville-Warren 138kV line to 954 ACSR | M6 | MI | 14.8 |  | Proposed | 7000000 | [5 empty] | Y | B
B | East | NIPS | 3154 | 2010-04-04 | 71C7559 | 5535 | 2010-04-04 | SUB | 2012-12-01 | Sheffield | Reactor |  | 138 |  |  | Add 0.795 Ohm reactor on BP Whiting to Sheffield circuit |  | IN |  |  | Proposed | 807141 | Engineering |  |  |  |  | Y | B
B | West | ATC LLC | 544 | 2010-09-15 | p2-104, F2650 | 898 | 2011-08-24 | CAP | 2015-06-01 | Bluemound | Capacitor bank |  | 138 |  | 225 Mvar | Add 3x75 Cap Banks to 2 Bluemound buses | L7 | WI |  |  | Conceptual | 3463000 | Eng |  |  |  |  | Y | B
B | West | ATC LLC | 1269 | 2010-09-15 | PR04353 or PR03222 | 1988 | 2011-08-24 | TX | 2020-06-01 | Arcadian 345-138kV | transformer | 1 | 345 | 138 | 500 | replace Arcadian 345/138kV transformer #2 & #3 |  | WI |  |  | Conceptual | 3500000 | [5 empty] | Y | B
B | West | ATC LLC | 1270 | 2011-04-19 | PR04508 | 1990 | 2011-04-19 | LNup | 2016-06-01 | Arcadian | Waukesha | 1 | 138 |  | 504 | Rebuild Ck 1 of Arcadian to Waukesha 138 kV Line |  | WI | 4.06 |  | Proposed | 7293447.5 | [5 empty] | Y | B
B | West | ATC LLC | 1270 | 2011-04-19 | PR04508 | 1989 | 2011-04-19 | LNup | 2016-06-01 | Arcadian | Waukesha | 2 | 138 |  | 504 | Rebuild Ck 2 of Arcadian to Waukesha 138 kV Line |  | WI | 3.88 |  | Proposed | 7293447.5 | [5 empty] | Y | B
B | West | ATC LLC | 1284 | 2010-09-15 | 5, F2095 canceled? | 2110 | 2010-04-30 | LN | 2050-06-01 | Albers | Tie | 1 | 138 |  |  | tie 138kv buses at Albers |  | WI |  |  | Conceptual | [6 empty] | Y | B
B | West | ATC LLC | 1284 | 2010-09-15 | 5, F2095 canceled? | 2113 | 2010-04-30 | LN | 2050-06-01 | Albers | Somers | 1 | 138 |  | 347 MVA | albers-somers w/477-t2 |  | WI | 3.3 |  | Conceptual | [6 empty] | Y | B
B | West | ATC LLC | 1284 | 2010-09-15 | 5, F2095 canceled? | 2112 | 2010-04-30 | LN | 2050-06-01 | Racine | Somers | 1 | 138 |  | 347 MVA | somers-racine w/477-t2 |  | WI | 4.3 |  | Conceptual | [6 empty] | Y | B
B | West | ATC LLC | 1624 | 2010-09-15 | PR03203 | 3241 | 2010-06-18 | LNup | 2022-06-01 | Portage | Trienda | 2 | 138 |  | 277 | uprate X-67 |  | WI | 3.4 |  | Conceptual | [6 empty] | Y | B
B | West | ATC LLC | 1687 | 2010-09-15 | F1867 | 3463 | 2010-09-01 | TX | 2017-06-01 | Metomen | Transformer | 1 | 138 | 69 | 100 MVA | Replace the 138/69 kV transformer at Metomen substation to increase rating |  | WI |  |  | Planned | 4700000 | [5 empty] | Y | B
B | West | ATC LLC | 1946 | 2010-09-15 |  | 3825 | 2010-04-30 | TX | 2018-06-01 | Spring Green | transformer | 2 | 138 | 69 | 100 MVA | Install a 2nd Spring Green 138-69 kV Transformer |  | WI |  |  | Conceptual | 1400000 | [5 empty] | Y | B
B | West | ATC LLC | 2044 | 2010-09-15 |  | 3926 | 2010-04-30 | LNup | 2017-06-01 | A13(Quincy) | McKenna | 1 | 69 |  | 49 MVA | Increase line clearance to 200 deg F SN/SE |  | WI | 7.6 |  | Conceptual | 978010.9176 | [5 empty] | Y | B
B | West | ATC LLC | 2044 | 2010-09-15 |  | 3925 | 2010-04-30 | LNup | 2017-06-01 | Castle Rock | A13(Quincy) | 1 | 69 |  | 49 MVA | Increase line clearance to 200 deg F SN/SE |  | WI | 0.9 |  | Conceptual | 115817.0824 | [5 empty] | Y | B
B | West | ATC LLC | 2454 | 2009-11-19 | G590, G611, G773 | 4412 | 2011-02-24 | LN | 2012-05-01 | Melissa | Tayco | 1 | 138 |  | 160 MVA | Uprate terminal equip to achieve a 199 MVA SE rating |  | WI | 0.3 |  | Planned | 12260 | eng | Network |  |  |  | Y | B
B | West | ATC LLC | 2454 | 2009-11-19 | G590, G611, G773 | 4411 | 2011-02-24 | LN | 2012-05-01 | Meadows | Melissa | 1 | 138 |  | 169 MVA | Increase line clearance to achieve a 198 MVA SE rating |  | WI | 1.1 |  | Planned | 44960 | eng | Network |  |  |  | Y | B
B | West | ATC LLC | 2454 | 2009-11-19 | G590, G611, G773 | 4410 | 2011-02-24 | LN | 2012-05-01 | Kaukauna Central Tap | Meadows | 1 | 138 |  | 169 MVA | Increase line clearance to achieve a 198 MVA SE rating |  | WI | 7.8 |  | Planned | 318800 | eng | Network |  |  |  | Y | B
B | West | ATC LLC | 2454 | 2009-11-19 | G590 | 4406 | 2011-02-24 | GEN | 2012-05-01 | STNYBRK Wind | generator | W | 0.6 |  | 98.7 MW | G590 Stony Brook Wind Farm |  | WI |  |  | Planned |  |  | Generator |  |  |  | Y | B
B | West | ATC LLC | 2454 | 2009-11-19 | G590 | 4405 | 2011-02-24 | SUB | 2012-05-01 | STNYBRK Wind | substation | 1 | 138 |  |  | G-T Interconnection From Techumseh Rd 138 kV bus |  | WI |  |  | Planned | 1234700 | eng | Interconnection |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5398 | 2010-12-03 | LN | 2013-01-31 | Fitchburg | Syene | 1 | 69 |  | 83 MVA | Uprate Fitchburg-Syene-Nine Springs 69kV line to 275 deg F SE clearance |  | WI | 3.7 |  | Proposed | 4400000 | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5404 | 2010-12-03 | SUB | 2013-01-31 | Nine Springs | substation | 1 | 69 |  | 32.66 MVAR | Install 2-16.33Mvar cap banks at Nine Springs 69kV |  | WI |  |  | Proposed |  | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5403 | 2010-12-03 | LN | 2013-01-31 | Royster | AGA TP | 1 | 69 |  | 95 MVA | Move AGA load onto Femrite-Royster line creating Femrite-AGA TP-Royster 69kV |  | WI |  | 2 | Proposed |  | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5402 | 2010-12-03 | LN | 2013-01-31 | Femrite | AGA TP | 1 | 69 |  | 95 MVA | Move AGA load onto Femrite-Royster line creating Femrite-AGA TP-Royster 69kV |  | WI |  | 1.8 | Proposed |  | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5401 | 2010-12-03 | LN | 2013-01-31 | AGA TP | Pflaum | 1 | 69 |  | 82 MVA | Uprate Royster-AGA TP-Pflaum 69kV line to 275 deg F SE clearance |  | WI | 0.1 |  | Proposed |  | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5400 | 2010-12-03 | LN | 2013-01-31 | Royster | AGA Tap | 1 | 69 |  | 83 MVA | Uprate Royster-AGA TP-Pflaum 69kV line to 275 deg F SE clearance |  | WI | 1.9 |  | Proposed |  | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3089 | 2009-10-08 |  | 5399 | 2010-12-03 | LN | 2013-01-31 | Syene | Nine Springs | 1 | 69 |  | 82 MVA | Uprate Fitchburg-Syene-Nine Springs 69kV line to 275 deg F SE clearance |  | WI | 2.9 |  | Proposed |  | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3118 | 2010-01-15 | 3118 | 5468 | 2010-06-18 | LN | 2016-06-01 | South Lake Geneva | North Lake Geneva | 1 | 138 |  | 293 MVA | construct a new 138kV line from North Lake Geneva to South Lake Geneva |  | WI |  | 5 | Proposed | 14428632 | eng |  |  |  |  | Y | B
B | West | ATC LLC | 3118 | 2010-01-15 | 3118 | 1251 | 2010-04-30 | TX | 2016-06-01 | South Lake Geneva 138-69 kV | transformer | 1 | 138 | 69 | 100 MVA | Install new South Lake Geneva 138-69kV Transformer |  | WI |  |  | Proposed | 1973000 | MISO per unit |  |  |  |  | Y | B
B | West | GRE | 2098 | 2008-02-22 | G390 | 2993 | 2010-10-28 | LNup | 2013-04-01 | RDF | Daytonport | 1 | 69 |  | 78 MVA | Upgrade of RDF - Daytonport to at least 78 MVA |  | MN | 3.7 |  | Proposed | 1377324 | [5 empty] | Y | B
B | West | GRE | 2098 | 2008-02-22 | G390 | 2804 | 2010-10-28 | LNup | 2013-04-01 | Elk River #14 substation | Bunker Lake Distribution | 1 | 230 |  | 271 | Upgrade of Elk River #14 substation - Bunker Lake Distribution 230 kV to at least 271 MVA. |  | MN | 14.3 |  | Proposed | 4894756 | [5 empty] | Y | B
B | West | ITCM | 1147 | 2009-09-25 | G298 | 5386 | 2011-02-15 | SUB | 2011-12-31 | Triboji | Upgrades |  | 161 |  |  | Upgrade Triboji to 4 breaker ring bus |  | IA |  |  | Planned | 2300000 | Planning |  |  |  |  | Y | B
B | West | ITCM | 1147 | 2009-09-25 | G298 | 5387 | 2011-02-15 | SUB | 2011-12-31 | Cayler | Switch Station |  | 161 |  |  | New switch station (paid for by customer) tapping the Dickinson Co-Wisdom 161kV line |  | IA |  |  | Planned | 0 | Planning |  |  |  |  | Y | B
B | West | ITCM | 1741 | 2011-02-15 | G517 | 4027 | 2011-02-15 | COM | 2012-12-31 | Communication System Upgrades |  |  | 161 |  |  |  |  | MN |  |  | Planned | 400000 | Planning | Network |  | Y |  | Y | B
B | West | ITCM | 1741 | 2011-02-15 | G517 | 4026 | 2011-02-15 | SUB | 2012-12-31 | Heron Lake Substation |  |  | 161 |  |  |  |  | MN |  |  | Planned | 4195530 | Planning | Network |  | Y |  | Y | B
B | West | ITCM | 1741 | 2011-02-15 | G517 | 4025 | 2011-02-15 | SUB | 2012-12-31 | Cottonwood County substation |  |  | 161 |  |  |  |  | MN |  |  | Planned | 4833216 | Planning | Network |  | Y |  | Y | B
B | West | ITCM | 1741 | 2011-02-15 | G517 | 4028 | 2011-02-15 | LN | 2012-12-31 | South Storden | Cottonwood County | 1 | 161 |  |  |  |  | MN |  |  | Planned | 4092575 | Planning | Network |  | Y |  | Y | B
B | West | ITCM | 1741 | 2011-02-15 | G517 | 3292 | 2011-02-15 | LNrb | 2012-12-31 | Heron Lake | South Storden | 1 | 161 |  | 440 | Rebuild line to higher capacity |  | MN |  |  | Planned | 6818660 | Planning | Network |  | Y |  | Y | B
B | West | ITCM | 1741 | 2011-02-15 | G517 | 2235 | 2011-02-15 | LN | 2012-12-31 | Storden (Cottonwood County) | Dotson | 1 | 161 |  | 446 | New line |  | MN | 26 |  | Planned | 16379839 | Planning | Network |  | Y |  | Y | B
B | West | MDU | 1148 | 2005-11-18 |  | 1798 | 2005-11-18 | Breakers | 2012-12-31 | Java (Glenham) | generator |  | 115 | 1 | 39 | new generator |  | SD |  |  | Planned |  |  | Generator |  |  |  | Y | B
B | West | MDU | 1153 | 2005-11-18 |  | 1803 | 2005-11-18 | INT | 2012-09-01 | Crownbutte Wind (Gascoyne) | generator and associated network upgrades |  | 115 | 1 | 19 | new generator |  | ND |  |  | Planned |  |  | Generator |  |  |  | Y | B
B | West | MDU | 3083 | 2009-09-15 | Dickinson Loop | 5365 | 2009-09-15 | CB | 2014-10-01 | North Dickinson | 2 PCB |  | 115 |  |  | Complete North Dickinson bus |  | ND |  |  | Planned | 1200000 | Engineering |  |  |  |  | Y | B
B | West | MDU | 3083 | 2009-09-15 | Dickinson Loop | 5366 | 2009-09-15 | TX | 2014-10-01 | West Dickinson | 115/41.6 kV transformer | 1 | 115 | 41.6 | 60 | New transformer & substation |  | ND |  |  | Planned | 7400000 | Engineering |  |  |  |  | Y | B
B | West | MDU | 3083 | 2009-09-15 | Dickinson Loop | 5367 | 2009-09-15 | CB | 2014-10-01 | Dickinson Basin | 1 PCB |  | 115 |  |  | Add terminal for new loop line |  | ND |  |  | Planned | 550000 | Engineering |  |  |  |  | Y | B
B | West | MDU | 3083 | 2009-09-15 | Dickinson Loop | 5364 | 2009-09-15 | LN | 2014-10-01 | North Dickinson | Dickinson West | 1 | 115 |  | 120 | New line Segment |  | ND |  | 3 | Planned | 750000 | Engineering |  |  |  |  | Y | B
B | West | MDU | 3083 | 2009-09-15 | Dickinson Loop | 5363 | 2009-09-15 | LN | 2014-10-01 | Dickinson Basin | Dickinson West | 1 | 115 |  | 120 | New line Segment |  | ND |  | 5 | Planned | 1250000 | Engineering |  |  |  |  | Y | B
B | West | MEC | 2937 | 2009-09-14 | G0103 | 5112 | 2009-09-14 | TX | 2014-06-01 | Sub 39 | Transformer | 2 | 345 | 161 | 560 | Add 2nd 345-161 kV xfmr | J8 | IL |  |  | Proposed | 14500000 | Planning |  |  |  |  | Y | B
B | West | MEC | 2938 | 2009-09-14 | G0104 | 5113 | 2009-09-14 | LN | 2014-06-01 | Sub 39 | Cordova | 1 | 345 |  | 1471 | Uprate 345 kV line structures | J8 | IL | 15.5 |  | Proposed | 400000 | Planning |  |  |  |  | Y | B
B | West | MEC | 2939 | 2010-09-01 | G0307 | 5115 | 2010-09-01 | CB | 2016-06-01 | Raun |  |  | 345 |  |  | Terminal at the MEC Raun Substation | G8 | IA |  |  | Proposed | 1300000 | Planning 2010$ |  |  |  |  | Y | B
B | West | MEC | 2939 | 2010-09-01 | G0307 | 5116 | 2010-09-01 | CB | 2016-06-01 | WAPA Sioux City |  |  | 345 |  |  | Terminal at the WAPA Sioux City Substation | G7 | IA |  |  | Proposed | 1300000 | Planning 2010$ |  |  |  |  | Y | B
B | West | MEC | 2939 | 2010-09-01 | G0307 | 5114 | 2010-09-01 | LN | 2016-06-01 | Raun | WAPA Sioux City | 1 | 345 |  |  | New 345 kV line between Raun and WAPA Sioux City | G8 | IA |  | 23 | Proposed | 25800000 | Planning 2010$ |  |  |  |  | Y | B
B | West | MP | 1292 | 2011-09-06 | 14 | 2123 | 2011-09-06 | LNup | 2012-12-01 | ETCO | Forbes | 1 | 115 |  | 122/134 | Increase ground clearance |  | MN |  |  | Planned | 400000 | [5 empty] | Y | B
B | West | OTP | 549 | 2009-11-18 | Jamestown 115 kV Reactor | 1530 | 2010-04-05 | IND | 2015-12-01 | Jamestown | Reactor |  | 115 |  | 25 Mvar | Add a 1 x 25 MVAr reactor at OTP Jamestown substation | E4 | ND |  |  | Proposed | 250000 | Planning | Network |  |  |  | Y | B
B | West | OTP | 585 | 2009-11-18 | Pelican Rapids Line Upgrade to 115kV | 589 | 2010-09-28 | LNcnv | 2013-12-31 | Pelican Rapids | Pelican Rapids Turkey Plant | 1 | 115 |  | 85 | Convert an existing 41.6 kV line to 115 kV | G4 | MN | 2.5 |  | Planned | 858869 | Planning |  |  |  |  | Y | B
B | West | OTP | 2824 | 2011-09-06 | Hensel 115 kV capacitor | 4962 | 2011-09-06 | LN | 2014-12-31 | Hensel 115 kV | Hensel 69/41.6 kV |  | 115 | 41.6 | 2 x 15 MVAR | Install New Capacitor Bank on Hensel 115 kV line for Voltage Support During Contingencies |  | ND |  |  | Proposed | 750000 | Proposed |  |  |  |  | Y | B
B | West | XEL | 2107 | 2008-02-22 | G520 | 2820 | 2011-06-29 | LN | 2009-04-02 | G520 Substation | new substation | 1 | 115 | 34.5 |  | Install new 3-position 115 kV substation with breakers, switches, buswork, steel, foundations, control house and associated equipment. Install new loop in-and-out tap, 3.5 miles of double circuit, 115 kV transmission line. |  | MN |  | 3.5 | Planned | 5930926 |  | Network |  | Y |  | Y | B
B | West | XEL | 2115 | 2008-02-22 | G491 | 2841 | 2011-06-29 | LN | 2010-09-01 | Chanarambie | Lake Yankton | 1 | 115 |  |  | Three spans of the existing 115 kV transmission line between Chanarambie and Lake Yankton will be relocated immediately outside of the Chanarambie substation to accommodate the expansion of the substation for G491. |  | MN |  |  | Planned | 58152 |  | Network |  | Y |  | Y | B
B | West | XEL | 2115 | 2008-02-22 | G491 | 2840 | 2011-06-29 | SUB | 2010-09-01 | Chanarambie Substation | substation upgrades | 1 | 115 |  |  | G491: three new 115 kV breakers and disconnect switches, control house expansion, structural steel and foundations associated with this new equipment, control and protection equipment associated with these new installations |  | MN |  |  | Planned | 4305000 |  | Network |  | Y |  | Y | B
B | West | XEL | 3099 | 2009-11-19 |  | 5429 | 2009-12-09 | TX | 2013-06-01 | Franklin | Transformer | 1 | 115 | 69 | 70 | upgrade to70 MVA |  | MN |  |  | Planned | 2400000 |  |  |  | N |  | Y | B
B | West | XEL | 3099 | 2009-11-19 |  | 5430 | 2009-12-09 | TX | 2013-06-01 | Franklin | Transformer | 2 | 115 | 69 | 70 | upgrade to70 MVA |  | MN |  |  | Planned | 2400000 |  |  |  | N |  | Y | B
B in MTEP10 | Central | AmerenIL | 2964 | 2010-12-06 |  | 5163 | 2011-07-05 | SUB | 2011-06-01 | ADM North-North 27th Street | Connection to Secure Energy | 1 | 138 | 1 | 478 | Secure Energy - Provide connection to Secure Energy coal gasification plant with 5 PCB 138 kV ring bus substation. Plant would connect in the Decatur area to ADM North-North 27th Street 138 kV Line 1604 between ADM North and Caterpillar Substations. | K10 | IL |  |  | Proposed | 5966000 | Engineering |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 2978 | 2009-12-23 |  | 5181 | 2009-09-14 | CAP | 2013-06-01 | ESK Customer Sub | 32 Mvar, 138 kV Capacitor Bank | 1 | 138 |  | 32 | ESK Customer Substation - Install 32 Mvar, 138 kV capacitor bank to improve customer load power factor. | K8 | IL |  |  | Proposed | 1521000 | Engineering |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3200 | 2010-07-13 | RGOS 765 | 5760 | 2010-07-13 | Sub | 2025-01-01 | Rising | upgrade existing substation |  | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IL |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3200 | 2010-07-13 | RGOS 765 | 5750 | 2010-07-13 | Sub | 2025-01-01 | MO-A Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MO |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3200 | 2010-07-13 | RGOS 765 | 5711 | 2010-07-13 | LN | 2025-01-01 | Goose Creek | Rising | 1 | 345 |  | 1195 | Equipment upgrade to increase line rating |  | IL | 18 |  | Conceptual | 27000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5902 | 2010-07-13 | Sub | 2025-01-01 | IL-K Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IL |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5935 | 2010-07-13 | Sub | 2025-01-01 | Rising | upgrade existing substation | 1 | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IL |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5925 | 2010-07-13 | Sub | 2025-01-01 | Newton | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IL |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5908 | 2010-07-13 | Sub | 2025-01-01 | Meredosia | new substation | 1 | 345 | 138 |  | Add 4 new 345 bay(s) at New station. Add 2 new 138 bay(s) at New station. Add 2 new 345/138 autotransformer(s). |  | IL |  |  | Conceptual | 44000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5882 | 2010-07-13 | Sub | 2025-01-01 | Fargo | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | IL |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5852 | 2010-07-13 | LN | 2025-01-01 | Goose Creek | Rising | 1 | 345 |  | 1195 | Equipment upgrade to increase line rating |  | IL | 18 |  | Conceptual | 27000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 2970 | 2010-12-06 |  | 5169 | 2011-04-22 | CB | 2012-06-01 | Apache Flats | AECI Scruggs Delivery Pt. | 1 | 161 |  | 558 | Apache Flats 161 kV Substation - Install 1-161 kV, 2000 A PCB and necessary metering and relaying to provide a delivery point for Associated Electric's Scruggs 161-69 kV Substation. | I11 | MO |  |  | Planned | 1035000 | Engineering |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3200 | 2010-07-13 | RGOS 765 | 5726 | 2010-07-13 | Sub | 2025-01-01 | Fairport | new substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 3 new 345 bay(s) at new station. Add 1 new 765/345 autotransformer(s). |  | MO |  |  | Conceptual | 102000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3200 | 2010-07-13 | RGOS 765 | 4040 | 2010-07-13 | LN | 2025-01-01 | Montgomery | St. Francois | 1 | 765 |  | 3975 |  |  | MO |  | 103.8946 | Conceptual | 332462592 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3200 | 2010-07-13 | RGOS 765 | 4062 | 2010-07-13 | Sub | 2025-01-01 | St. Francois | upgrade existing substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 765/345 autotransformer(s). |  | MO |  |  | Conceptual | 84300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3200 | 2010-07-13 | RGOS 765 | 4063 | 2010-07-13 | Sub | 2025-01-01 | Montgomery | upgrade existing substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 765/345 autotransformer(s). |  | MO |  |  | Conceptual | 84300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3202 | 2010-07-13 | RGOS Native | 5945 | 2010-07-13 | Sub | 2025-01-01 | Thomas Hill | upgrade existing substation | 1 | 345 | 161 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 161 bay(s) at Existing station. Add 1 new 345/161 autotransformer(s). |  | MO |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3202 | 2010-07-13 | RGOS Native | 5933 | 2010-07-13 | Sub | 2025-01-01 | Palmyra | new substation | 1 | 345 | 161 |  | Add 2 new 345 bay(s) at New station. Add 1 new 161 bay(s) at Existing station. Add 1 new 345/161 autotransformer(s). |  | MO |  |  | Conceptual | 27800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3202 | 2010-07-13 | RGOS Native | 5931 | 2010-07-13 | Sub | 2025-01-01 | Overton | upgrade existing substation | 1 | 345 | 161 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 161 bay(s) at Existing station. Add 1 new 345/161 autotransformer(s). |  | MO |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3202 | 2010-07-13 | RGOS Native | 5916 | 2010-07-13 | Sub | 2025-01-01 | MO-A Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MO |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3202 | 2010-07-13 | RGOS Native | 5881 | 2010-07-13 | Sub | 2025-01-01 | Fairport | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | MO |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | AmerenMO | 3202 | 2010-07-13 | RGOS Native | 5862 | 2010-07-13 | Sub | 2025-01-01 | Adair | new substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at New station. |  | MO |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5718 | 2010-07-13 | Sub | 2025-01-01 | Bain | upgrade existing substation |  | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5729 | 2010-07-13 | Sub | 2025-01-01 | Granville | upgrade existing substation |  | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | DEM | 3200 | 2010-07-13 | RGOS 765 | 5707 | 2011-01-11 | LN | 2025-01-01 | Kokomo | Tipton | 1 | 230 |  | 497 | Equipment upgrade to increase line rating |  | IN | 16.8 |  | Conceptual | 12600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | DEM | 3200 | 2010-07-13 | RGOS 765 | 5706 | 2011-01-11 | LN | 2025-01-01 | Kokomo | New London | 1 | 230 |  | 497 | Equipment upgrade to increase line rating |  | IN | 8.28 |  | Conceptual | 6210000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | DEM | 3202 | 2010-07-13 | RGOS Native | 5782 | 2010-07-13 | LN | 2025-01-01 | Noblesville | Nucor | 1 | 345 |  | 1510 |  |  | IN |  | 55.56 | Conceptual | 111120000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | DEM, IPL | 3200 | 2010-07-13 | RGOS 765 | 5708 | 2010-07-13 | LN | 2025-01-01 | Whitestown | Guion | 1 | 345 |  | 1195 | Equipment upgrade to increase line rating |  | IN | 13.44 |  | Conceptual | 26880000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | HE | 3202 | 2010-07-13 | RGOS Native | 5909 | 2010-07-13 | Sub | 2025-01-01 | Merom | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | IN |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | HE, AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5781 | 2010-07-13 | LN | 2025-01-01 | Merom | Newton | 1 | 345 |  | 1510 |  |  | IL/IN |  | 50.28 | Conceptual | 77460000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | HE, DEM | 3202 | 2010-07-13 | RGOS Native | 5780 | 2010-07-13 | LN | 2025-01-01 | Merom | Gwynn | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | IN |  | 127.44 | Conceptual | 254880000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | IPL | 3200 | 2010-07-13 | RGOS 765 | 5763 | 2010-07-13 | Sub | 2025-01-01 | Stout | upgrade existing substation |  | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | IPL | 3200 | 2010-07-13 | RGOS 765 | 5732 | 2010-07-13 | Sub | 2025-01-01 | Guion | upgrade existing substation |  | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | IPL | 3200 | 2010-07-13 | RGOS 765 | 5709 | 2010-07-13 | LN | 2025-01-01 | Petersburg | Thompson | 1 | 345 |  | 1195 | Equipment upgrade to increase line rating |  | IN | 115.68 |  | Conceptual | 231360000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | IPL | 3212 | 2010-08-19 |  | 5980 | 2010-08-19 | LN | 2015-01-01 | Wheatland | Breed | 1 | 345 |  | 1386 MVA | rating upgrade and close Wheatland 345 tie CB |  | IN |  |  | Proposed | 12000000 | [5 empty] | Y | B
B in MTEP10 | Central | LGEE | 3202 | 2010-07-13 | RGOS Native | 5851 | 2010-07-13 | LN | 2025-01-01 | Daviess | 7HARDIN 345.00 | 1 | 345 |  | 945 | Equipment upgrade to increase line rating |  | IN | 79.2 |  | Conceptual | 158400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | MIPU, AmerenMO | 3200 | 2010-07-13 | RGOS 765 | 5660 | 2010-07-13 | LN | 2025-01-01 | Fairport | Montgomery | 1 | 765 |  | 3975 |  |  | MO |  | 205.2924 | Conceptual | 656935680 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | SIGE | 3200 | 2010-07-13 | RGOS 765 | 5716 | 2010-07-13 | Sub | 2025-01-01 | AB Brown | upgrade existing substation |  | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central | SIGE | 3202 | 2010-07-13 | RGOS Native | 5861 | 2010-07-13 | Sub | 2025-01-01 | AB Brown | upgrade existing substation | 1 | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central/Non-MISO | AmerenIL, Non-MISO | 3200 | 2010-07-13 | RGOS 765 | 5662 | 2010-07-13 | LN | 2025-01-01 | Fairport | MO-A Station | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | MO |  | 50.9322 | Conceptual | 117144060 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central/Non-MISO | AmerenIL, Non-MISO | 3200 | 2010-07-13 | RGOS 765 | 5659 | 2010-07-13 | LN | 2025-01-01 | Meadow Lake | IN-E Station | 1 | 345 |  | 1510 |  |  | IN |  | 25.3109 | Conceptual | 50621760 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central/Non-MISO | AmerenMo Non-MISO | 3202 | 2010-07-13 | RGOS Native | 5783 | 2010-07-13 | LN | 2025-01-01 | Fairport | Adair | 1 | 345 |  | 1510 |  |  | MO |  | 111.24 | Conceptual | 100116000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central/Non-MISO | CE, AmerenIL | 3200 | 2010-07-13 | RGOS 765 | 5685 | 2010-07-13 | LN | 2025-01-01 | IL-F Station | IN-E Station | 1 | 345 |  | 1510 |  |  | IL/IN |  | 55.7049 | Conceptual | 86171688 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central/Non-MISO | Non-MISO | 3202 | 2010-07-13 | RGOS Native | 5778 | 2010-07-13 | LN | 2025-01-01 | Greentown | Blue Creek | 1 | 765 |  | 3975 |  |  | IN/OH |  | 72.36 | Conceptual | 202608000 | Planning |  |  |  |  | Y | B
B in MTEP10 | Central/Non-MISO | Non-MISO | 3202 | 2010-07-13 | RGOS Native | 5784 | 2010-07-13 | LN | 2025-01-01 | Fairport | MO-A Station | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | MO |  | 50.88 | Conceptual | 117024000 | Planning |  |  |  |  | Y | B
B in MTEP10 | DEM | DEM | 3202 | 2010-07-13 | RGOS Native | 5888 | 2010-07-13 | Sub | 2025-01-01 | Greentown | upgrade existing substation | 1 | 765 |  |  | Add 1 new 765 bay(s) at Existing station. |  | IN |  |  | Conceptual | 12550000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITC | 1856 | 2009-09-14 |  | 3744 | 2011-01-11 | LN | 2015-12-31 | Jewell | Belle River - Greenwood Jct | 1 | 345 |  |  | Cut Pontiac-Greenwood-Belle River into Jewell creating Pontiac-Jewell and Jewell-Belle River-Greenwwod |  | MI |  |  | Proposed | 2600000 | [5 empty] | Y | B
B in MTEP10 | East | ITC | 1856 | 2009-09-14 |  | 3743 | 2011-01-11 | LN | 2015-12-31 | Jewell | Pontiac | 1 | 345 |  |  | Cut Pontiac-Greenwood-Belle River into Jewell creating Pontiac-Jewell and Jewell-Belle River-Greenwwod |  | MI |  |  | Proposed | 2600000 | [5 empty] | Y | B
B in MTEP10 | East | ITC | 2932 | 2009-09-14 |  | 5104 | 2009-12-01 | LN | 2015-06-01 | St Antoine | Essex | 1 | 120 |  |  | Construct 2nd underground cable from St Antoine to Essex (5.1 miles). |  | MI |  | 5.1 | Proposed | 54800000 | [5 empty] | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5745 | 2010-07-13 | Sub | 2025-01-01 | MI-D Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5752 | 2010-07-13 | Sub | 2025-01-01 | Murphy | new substation |  | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5746 | 2010-07-13 | Sub | 2025-01-01 | MI-E Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5744 | 2010-07-13 | Sub | 2025-01-01 | MI-C Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5740 | 2010-07-13 | Sub | 2025-01-01 | Keystone | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5730 | 2010-07-13 | Sub | 2025-01-01 | Greenwood | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3200 | 2010-07-13 | RGOS 765 | 5710 | 2010-07-13 | LN | 2025-01-01 | 19STOGA 345.00 | 19BFOOT 345.00 | 1 | 345 |  | 1756 | Equipment upgrade to increase line rating |  | MI | 45.6 |  | Conceptual | 82080000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5920 | 2010-07-13 | Sub | 2025-01-01 | Murphy | new substation | 1 | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5910 | 2010-07-13 | Sub | 2025-01-01 | MI-C Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5911 | 2010-07-13 | Sub | 2025-01-01 | MI-D Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5912 | 2010-07-13 | Sub | 2025-01-01 | MI-E Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5903 | 2010-07-13 | Sub | 2025-01-01 | Keystone | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5850 | 2010-07-13 | LN | 2025-01-01 | 19STOGA 345.00 | Blackfoot | 1 | 345 |  | 1756 | Equipment upgrade to increase line rating |  | MI | 45.6 |  | Conceptual | 82080000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | ITCT | 3202 | 2010-07-13 | RGOS Native | 5889 | 2010-07-13 | Sub | 2025-01-01 | Greenwood | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East | METC | 3210 | 2010-07-21 |  | 5953 | 2010-07-21 | LN | 2014-06-01 | Vanderbilt | Riggsville |  | 138 |  |  | Rebuild 30.3 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. |  | MI | 30.3 |  | Proposed | 33254000 | [5 empty] | Y | B
B in MTEP10 | East | Non-MISO | 3202 | 2010-07-13 | RGOS Native | 5834 | 2010-07-13 | LN | 2025-01-01 | OH-B Station | OH-C Station | 1 | 765 |  | 3975 |  |  | OH |  | 49.32 | Conceptual | 138096000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East/Non-MISO | NIPS, CE | 3202 | 2010-07-13 | RGOS Native | 5848 | 2010-07-13 | LN | 2025-01-01 | Sheffield | BURNH; B 345.00 | 1 | 345 |  | 1314 | Equipment upgrade to increase line rating |  | IL/IN | 7.2 |  | Conceptual | 12600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East/Non-MISO | NIPS, CE | 3202 | 2010-07-13 | RGOS Native | 5849 | 2010-07-13 | LN | 2025-01-01 | St. John | Crete | 1 | 345 |  | 1334 | Equipment upgrade to increase line rating |  | IL/IN | 14.4 |  | Conceptual | 25200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | East/Non-MISO | Non-MISO | 3202 | 2010-07-13 | RGOS Native | 5779 | 2010-07-13 | LN | 2025-01-01 | South Canton | OH-C Station | 1 | 765 |  | 3975 |  |  | OH |  | 99.48 | Conceptual | 278544000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5887 | 2010-07-13 | Sub | 2025-01-01 | Granville | upgrade existing substation | 1 | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | DEM | 3202 | 2010-07-13 | RGOS Native | 5893 | 2010-07-13 | Sub | 2025-01-01 | Gwynn | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IN |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | DEM | 3202 | 2010-07-13 | RGOS Native | 5926 | 2010-07-13 | Sub | 2025-01-01 | Noblesville | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | IN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | DEM | 3202 | 2010-07-13 | RGOS Native | 5928 | 2010-07-13 | Sub | 2025-01-01 | Nucor | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | IN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | IPL | 3202 | 2010-07-13 | RGOS Native | 5891 | 2010-07-13 | Sub | 2025-01-01 | Guion | upgrade existing substation | 1 | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | IN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | MEC | 3202 | 2010-07-13 | RGOS Native | 5875 | 2010-07-13 | Sub | 2025-01-01 | Cordova (MEC) | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IL |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | Non-MISO | 3202 | 2010-07-13 | RGOS Native | 5874 | 2010-07-13 | Sub | 2025-01-01 | Collins | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | IL |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | XEL | 3202 | 2010-07-13 | RGOS Native | 5895 | 2010-07-13 | Sub | 2025-01-01 | Hazel | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | MN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | MISO | XEL | 3202 | 2010-07-13 | RGOS Native | 5878 | 2010-07-13 | Sub | 2025-01-01 | Eden Prairie | upgrade existing substation | 1 | 345 | 115 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 115 bay(s) at Existing station. Add 1 new 345/115 autotransformer(s). |  | MN |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, DPC | 3200 | 2010-07-13 | RGOS 765 | 5694 | 2010-07-13 | LN | 2025-01-01 | Mitchell Co | North La Crosse | 1 | 765 |  | 3975 |  |  | MN/WI |  | 89.2794 | Conceptual | 313570092 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, DPC | 3202 | 2010-07-13 | RGOS Native | 5826 | 2010-07-13 | LN | 2025-01-01 | Mitchell County | Genoa | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | IA/MN/WI |  | 82.8 | Conceptual | 202464000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, MEC | 3200 | 2010-07-13 | RGOS 765 | 5693 | 2010-07-13 | LN | 2025-01-01 | Mitchell Co | Hills | 1 | 765 |  | 3975 |  |  | IA/MN |  | 178.913 | Conceptual | 574060800 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, MEC | 3202 | 2010-07-13 | RGOS Native | 5812 | 2010-07-13 | LN | 2025-01-01 | Hazleton | Hills | 1 | 345 |  | 1510 |  |  | IA |  | 87.12 | Conceptual | 139392000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, MEC | 3202 | 2010-07-13 | RGOS Native | 5811 | 2010-07-13 | LN | 2025-01-01 | Hazleton | Blackhawk | 1 | 345 |  | 1510 |  |  | IA |  | 27.72 | Conceptual | 44352000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, MEC | 3202 | 2010-07-13 | RGOS Native | 5835 | 2010-07-13 | LN | 2025-01-01 | Ottumwa | Montezuma | 1 | 345 |  | 478 |  |  | IA |  | 42.96 | Conceptual | 68736000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, XEL | 3200 | 2010-07-13 | RGOS 765 | 4034 | 2010-07-13 | LN | 2025-01-01 | Mitchell Co | Hampton Corner | 1 | 765 |  | 3975 |  |  | MN |  | 91.536 | Conceptual | 320376000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ALTW, XEL | 3202 | 2010-07-13 | RGOS Native | 5818 | 2010-07-13 | LN | 2025-01-01 | Lakefield | Chanarambie | 1 | 345 |  | 1510 |  |  | MN |  | 58.08 | Conceptual | 104544000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5754 | 2010-07-13 | Sub | 2025-01-01 | North Madison | upgrade existing substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 765/345 autotransformer(s). |  | WI |  |  | Conceptual | 84300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5758 | 2010-07-13 | Sub | 2025-01-01 | Paddock | upgrade existing substation |  | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5762 | 2010-07-13 | Sub | 2025-01-01 | SEC | upgrade existing substation |  | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5764 | 2010-07-13 | Sub | 2025-01-01 | Tamarac Tap | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5767 | 2010-07-13 | Sub | 2025-01-01 | WI-D Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5712 | 2010-07-13 | LN | 2025-01-01 | Arcadian | Mill Rd | 1 | 345 |  | 1076 | Equipment upgrade to increase line rating |  | WI | 36 |  | Conceptual | 75600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5675 | 2010-07-13 | LN | 2025-01-01 | Elm Road | Tamarac Tap | 1 | 345 |  | 1510 |  |  | WI |  | 30.4325 | Conceptual | 63908208 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5725 | 2010-07-13 | Sub | 2025-01-01 | Elm Road | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5723 | 2010-07-13 | Sub | 2025-01-01 | Darlington | new substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 2 new 345 bay(s) at New station. Add 1 new 765/345 autotransformer(s). |  | WI |  |  | Conceptual | 90200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5703 | 2010-07-13 | LN | 2025-01-01 | SEC | Tamarac Tap | 1 | 345 |  | 1510 |  |  | WI |  | 54.3024 | Conceptual | 114035040 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5714 | 2010-07-13 | LN | 2025-01-01 | Edgewater | Cedar Sauk | 1 | 345 |  | 956 | Equipment upgrade to increase line rating |  | WI | 56.4 |  | Conceptual | 118440000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5713 | 2010-07-13 | LN | 2025-01-01 | Cypress | Mill Rd | 1 | 345 |  | 1076 | Equipment upgrade to increase line rating |  | WI | 61.2 |  | Conceptual | 128520000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5672 | 2010-07-13 | LN | 2025-01-01 | Darlington | North Madison | 1 | 765 |  | 3975 |  |  | WI |  | 64.5071 | Conceptual | 258028320 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5698 | 2010-07-13 | LN | 2025-01-01 | Paddock | Darlington | 1 | 345 |  | 1510 |  |  | WI |  | 62.1047 | Conceptual | 130419828 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5747 | 2010-07-13 | Sub | 2025-01-01 | Mill Rd | upgrade existing substation |  | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | WI |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5799 | 2010-07-13 | LN | 2025-01-01 | Cypress | Mill Road | 1 | 345 |  | 1510 |  |  | WI |  | 63.36 | Conceptual | 133056000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5798 | 2010-07-13 | LN | 2025-01-01 | Cypress | Forest Jct | 1 | 345 |  | 1510 |  |  | WI |  | 28.92 | Conceptual | 60732000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5802 | 2010-07-13 | LN | 2025-01-01 | Elm Road | Tetonka | 1 | 345 |  | 1510 |  |  | WI |  | 30.48 | Conceptual | 64008000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5788 | 2010-07-13 | LN | 2025-01-01 | Arcadian | Mill Road | 1 | 345 |  | 1076 |  |  | WI |  | 9.96 | Conceptual | 20916000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5803 | 2010-07-13 | LN | 2025-01-01 | Forest Jct | Sheboygan Falls | 1 | 345 |  | 1510 |  |  | WI |  | 41.76 | Conceptual | 87696000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5932 | 2010-07-13 | Sub | 2025-01-01 | Paddock | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5936 | 2010-07-13 | Sub | 2025-01-01 | Rocky Run | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5938 | 2010-07-13 | Sub | 2025-01-01 | SEC | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5940 | 2010-07-13 | Sub | 2025-01-01 | Sheboygan Falls | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5924 | 2010-07-13 | Sub | 2025-01-01 | Nelson Dewey | new substation | 1 | 345 | 161 |  | Add 6 new 345 bay(s) at New station. Add 2 new 161 bay(s) at New station. Add 2 new 345/161 autotransformer(s). |  | WI |  |  | Conceptual | 55800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5942 | 2010-07-13 | Sub | 2025-01-01 | Spring Green | new substation | 1 | 345 | 138 |  | Add 3 new 345 bay(s) at New station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | WI |  |  | Conceptual | 33800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5944 | 2010-07-13 | Sub | 2025-01-01 | Tamarack Tap | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5948 | 2010-07-13 | Sub | 2025-01-01 | Cardinal | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5939 | 2010-07-13 | Sub | 2025-01-01 | South Fon du Lac | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5927 | 2010-07-13 | Sub | 2025-01-01 | North Randolph | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5913 | 2010-07-13 | Sub | 2025-01-01 | Mill Road | upgrade existing substation | 1 | 345 | 138 |  | Add 2 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | WI |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5877 | 2010-07-13 | Sub | 2025-01-01 | Darlington | new substation | 1 | 345 | 138 |  | Add 5 new 345 bay(s) at New station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | WI |  |  | Conceptual | 45600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5840 | 2010-07-13 | LN | 2025-01-01 | SEC 345.00 | Tamarack Tap | 1 | 345 |  | 1510 |  |  | WI |  | 54.36 | Conceptual | 114156000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5838 | 2010-07-13 | LN | 2025-01-01 | Rocky Run | North Randolph | 1 | 345 |  | 1510 |  |  | WI |  | 84.72 | Conceptual | 177912000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5842 | 2010-07-13 | LN | 2025-01-01 | South Fon du Lac | Sheboygan Falls | 1 | 345 |  | 1510 |  |  | WI |  | 37.08 | Conceptual | 77868000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5876 | 2010-07-13 | Sub | 2025-01-01 | Cypress | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5841 | 2010-07-13 | LN | 2025-01-01 | South Fon du Lac | North Randolph | 1 | 345 |  | 1510 |  |  | WI |  | 35.52 | Conceptual | 74592000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5836 | 2010-07-13 | LN | 2025-01-01 | Paddock | Darlington | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | WI |  | 62.16 | Conceptual | 167832000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5865 | 2010-07-13 | Sub | 2025-01-01 | Arcadian | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | WI |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5866 | 2010-07-13 | Sub | 2025-01-01 | Arpin | upgrade existing substation | 1 | 345 | 138 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 138 bay(s) at Existing station. Add 1 new 345/138 autotransformer(s). |  | WI |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5844 | 2010-07-13 | LN | 2025-01-01 | Tamarack Tap | Sheboygan Falls | 1 | 345 |  | 1510 |  |  | WI |  | 54.36 | Conceptual | 114156000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5855 | 2010-07-13 | LN | 2025-01-01 | Edgewater | Cedar Sauk | 1 | 345 |  | 956 | Equipment upgrade to increase line rating |  | WI | 56.4 |  | Conceptual | 118440000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5830 | 2010-07-13 | LN | 2025-01-01 | Nelson Dewey | Darlington | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | WI |  | 54.6 | Conceptual | 147420000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5883 | 2010-07-13 | Sub | 2025-01-01 | Forest Jct | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5880 | 2010-07-13 | Sub | 2025-01-01 | Elm Road | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | CE, AmerenIL | 3202 | 2010-07-13 | RGOS Native | 5817 | 2010-07-13 | LN | 2025-01-01 | IL-F Station | IN-E Station | 1 | 345 |  | 1510 |  |  | IL/IN |  | 55.8 | Conceptual | 86340000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | CE, MEC | 3202 | 2010-07-13 | RGOS Native | 5858 | 2010-07-13 | LN | 2025-01-01 | Quad Cities | Cordova (MEC) | 1 | 345 |  | 1173 | Equipment upgrade to increase line rating |  | IL | 2.4 |  | Conceptual | 3600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | DPC | 3200 | 2010-07-13 | RGOS 765 | 5753 | 2010-07-13 | Sub | 2025-01-01 | North La Crosse | upgrade existing substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 765/345 autotransformer(s). |  | WI |  |  | Conceptual | 84300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | DPC | 3202 | 2010-07-13 | RGOS Native | 5921 | 2010-07-13 | Sub | 2025-01-01 | North LaCrosse | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | DPC | 3202 | 2010-07-13 | RGOS Native | 5886 | 2010-07-13 | Sub | 2025-01-01 | Genoa | new substation | 1 | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | WI |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | DPC | 3202 | 2010-07-13 | RGOS Native | 5831 | 2010-07-13 | LN | 2025-01-01 | North LaCrosse | Genoa | 1 | 345 |  | 1510 |  |  | WI |  | 22.08 | Conceptual | 46368000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | DPC, ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5696 | 2010-07-13 | LN | 2025-01-01 | North La Crosse | North Madison | 1 | 765 |  | 3975 |  |  | WI |  | 119.1626 | Conceptual | 476650560 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | DPC, ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5805 | 2010-07-13 | LN | 2025-01-01 | Genoa | Nelson Dewey | 1 | 345 |  | 1510 |  |  | IA |  | 70.8 | Conceptual | 113280000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3200 | 2010-07-13 | RGOS 765 | 5755 | 2010-07-13 | Sub | 2025-01-01 | ND-New Station | new substation |  | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3200 | 2010-07-13 | RGOS 765 | 5743 | 2010-07-13 | Sub | 2025-01-01 | McHenry | upgrade existing substation |  | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 34600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3200 | 2010-07-13 | RGOS 765 | 5692 | 2010-07-13 | LN | 2025-01-01 | McHenry | ND-New Station | 1 | 345 |  | 1510 |  |  | ND |  | 145.6452 | Conceptual | 203903280 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5794 | 2010-07-13 | LN | 2025-01-01 | Center | McHenry | 1 | 345 |  | 1510 |  |  | ND |  | 80.28 | Conceptual | 112392000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5934 | 2010-07-13 | Sub | 2025-01-01 | Prairie | new substation | 1 | 345 | 230 |  | Add 5 new 345 bay(s) at New station. Add 2 new 230 bay(s) at New station. Add 2 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 57400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5907 | 2010-07-13 | Sub | 2025-01-01 | McHenry | new substation | 1 | 345 | 230 |  | Add 4 new 345 bay(s) at New station. Add 2 new 230 bay(s) at New station. Add 2 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 45600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5923 | 2010-07-13 | Sub | 2025-01-01 | ND New Station | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5837 | 2010-07-13 | LN | 2025-01-01 | Prairie | ND New Station | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 66.48 | Conceptual | 126312000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5872 | 2010-07-13 | Sub | 2025-01-01 | Center | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | GRE | 3202 | 2010-07-13 | RGOS Native | 5824 | 2010-07-13 | LN | 2025-01-01 | McHenry | ND New Station | 1 | 345 |  | 1510 |  |  | ND |  | 145.68 | Conceptual | 203952000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5739 | 2010-07-13 | Sub | 2025-01-01 | IA-H Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5686 | 2010-07-13 | LN | 2025-01-01 | Lakefield Junction | IA-B Station | 1 | 345 |  | 1510 |  |  | IA/MN |  | 61.0855 | Conceptual | 101138208 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5683 | 2010-07-13 | LN | 2025-01-01 | IA-G Station | IA-H Station | 1 | 345 |  | 1510 |  |  | IA |  | 35.7377 | Conceptual | 57180288 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5738 | 2010-07-13 | Sub | 2025-01-01 | IA-G Station | new substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 4 new 345 bay(s) at New station. Add 1 new 765/345 autotransformer(s). |  | IA |  |  | Conceptual | 102000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5737 | 2010-07-13 | Sub | 2025-01-01 | IA-F Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5736 | 2010-07-13 | Sub | 2025-01-01 | IA-B Station | new substation |  | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5733 | 2010-07-13 | Sub | 2025-01-01 | Guthrie Center | new substation |  | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5681 | 2010-07-13 | LN | 2025-01-01 | IA-B Station | IA-F Station | 1 | 345 |  | 1510 |  |  | IA |  | 26.884 | Conceptual | 43014336 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5682 | 2010-07-13 | LN | 2025-01-01 | IA-F Station | IA-G Station | 1 | 345 |  | 1510 |  |  | IA |  | 38.9242 | Conceptual | 62278656 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5741 | 2010-07-13 | Sub | 2025-01-01 | Lakefield | new substation |  | 765 | 345 |  | Add 4 new 765 bay(s) at New station. Add 1 new 345 bay(s) at New station. Add 1 new 765/345 autotransformer(s). |  | MN |  |  | Conceptual | 84200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5679 | 2010-07-13 | LN | 2025-01-01 | Guthrie Center | IA-H Station | 1 | 345 |  | 1510 |  |  | IA |  | 41.241 | Conceptual | 65985600 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3200 | 2010-07-13 | RGOS 765 | 5748 | 2010-07-13 | Sub | 2025-01-01 | Mitchell Co | new substation |  | 765 | 345 |  | Add 5 new 765 bay(s) at New station. Add 1 new 765/345 autotransformer(s). |  | MN |  |  | Conceptual | 103400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5898 | 2010-07-13 | Sub | 2025-01-01 | IA-B Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5896 | 2010-07-13 | Sub | 2025-01-01 | Hazleton | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5809 | 2010-07-13 | LN | 2025-01-01 | Guthrie Center | IA-H Station | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | IA |  | 41.28 | Conceptual | 94944000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5816 | 2010-07-13 | LN | 2025-01-01 | IA-G Station | IA-H Station | 1 | 345 |  | 1510 |  |  | IA |  | 35.76 | Conceptual | 57216000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5815 | 2010-07-13 | LN | 2025-01-01 | IA-F Station | IA-G Station | 1 | 345 |  | 1510 |  |  | IA |  | 38.88 | Conceptual | 62208000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5814 | 2010-07-13 | LN | 2025-01-01 | IA-B Station | IA-F Station | 1 | 345 |  | 1510 |  |  | IA |  | 26.88 | Conceptual | 43008000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5813 | 2010-07-13 | LN | 2025-01-01 | Hazleton | Mitchell County | 1 | 345 |  | 956 |  |  | IA |  | 85.32 | Conceptual | 136512000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5899 | 2010-07-13 | Sub | 2025-01-01 | IA-F Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5930 | 2010-07-13 | Sub | 2025-01-01 | Ottumwa | new substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5900 | 2010-07-13 | Sub | 2025-01-01 | IA-G Station | new substation | 1 | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5901 | 2010-07-13 | Sub | 2025-01-01 | IA-H Station | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5914 | 2010-07-13 | Sub | 2025-01-01 | Mitchell County | new substation | 1 | 345 |  |  | Add 5 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 29400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5819 | 2010-07-13 | LN | 2025-01-01 | Lakefield | IA-B Station | 1 | 345 |  | 1510 |  |  | IA/MN |  | 61.08 | Conceptual | 101136000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | ITCM | 3202 | 2010-07-13 | RGOS Native | 5892 | 2010-07-13 | Sub | 2025-01-01 | Guthrie Center | new substation | 1 | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3200 | 2010-07-13 | RGOS 765 | 5724 | 2010-07-13 | Sub | 2025-01-01 | Ellendale | upgrade existing substation |  | 345 | 230 |  | Add 5 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 46400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3200 | 2010-07-13 | RGOS 765 | 5751 | 2010-07-13 | Sub | 2025-01-01 | MT_Zone | upgrade existing substation |  | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 2 new 230 bay(s) at Existing station. Add 2 new 345/230 autotransformer(s). |  | MT |  |  | Conceptual | 41100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3200 | 2010-07-13 | RGOS 765 | 5674 | 2010-07-13 | LN | 2025-01-01 | Ellendale | Tetonka | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 25.2748 | Conceptual | 48022044 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3202 | 2010-07-13 | RGOS Native | 5796 | 2010-07-13 | LN | 2025-01-01 | Center | Tetonka | 1 | 345 |  | 1510 |  |  | ND |  | 150.48 | Conceptual | 210672000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3202 | 2010-07-13 | RGOS Native | 5801 | 2010-07-13 | LN | 2025-01-01 | Ellendale | Tetonka | 1 | 345 |  | 1510 |  |  | ND |  | 25.32 | Conceptual | 35448000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3202 | 2010-07-13 | RGOS Native | 5946 | 2010-07-13 | Sub | 2025-01-01 | Tetonka | new substation | 1 | 345 | 230 |  | Add 7 new 345 bay(s) at New station. Add 2 new 230 bay(s) at Existing station. Add 2 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 64700000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3202 | 2010-07-13 | RGOS Native | 5919 | 2010-07-13 | Sub | 2025-01-01 | MT_Zone | new substation | 1 | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 2 new 230 bay(s) at New station. Add 2 new 345/230 autotransformer(s). |  | MT |  |  | Conceptual | 45600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3202 | 2010-07-13 | RGOS Native | 5885 | 2010-07-13 | Sub | 2025-01-01 | Fort Thompson | new substation | 1 | 345 | 230 |  | Add 2 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | SD |  |  | Conceptual | 22800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU | 3202 | 2010-07-13 | RGOS Native | 5879 | 2010-07-13 | Sub | 2025-01-01 | Ellendale | new substation | 1 | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 34600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU, OTP | 3200 | 2010-07-13 | RGOS 765 | 5673 | 2010-07-13 | LN | 2025-01-01 | Ellendale | Oakes | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 27.6416 | Conceptual | 52519116 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MDU, OTP | 3202 | 2010-07-13 | RGOS Native | 5800 | 2010-07-13 | LN | 2025-01-01 | Ellendale | Oakes | 1 | 345 |  | 1510 |  |  | ND |  | 27.6 | Conceptual | 38640000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3200 | 2010-07-13 | RGOS 765 | 5678 | 2010-07-13 | LN | 2025-01-01 | Grimes | Hills | 1 | 765 |  | 3975 |  |  | IA |  | 141.264 | Conceptual | 452044800 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3200 | 2010-07-13 | RGOS 765 | 5735 | 2010-07-13 | Sub | 2025-01-01 | Hills | upgrade existing substation |  | 765 | 345 |  | Add 4 new 765 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 765/345 autotransformer(s). |  | IA |  |  | Conceptual | 84300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3200 | 2010-07-13 | RGOS 765 | 5731 | 2010-07-13 | Sub | 2025-01-01 | Grimes | new substation |  | 765 | 345 |  | Add 4 new 765 bay(s) at New station. Add 3 new 345 bay(s) at New station. Add 1 new 765/345 autotransformer(s). |  | IA |  |  | Conceptual | 102000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3200 | 2010-07-13 | RGOS 765 | 5684 | 2010-07-13 | LN | 2025-01-01 | IA-G Station | Grimes | 1 | 765 |  | 3975 |  |  | IA |  | 105.2914 | Conceptual | 336932352 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5808 | 2010-07-13 | LN | 2025-01-01 | Grimes | Montezuma | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | IA |  | 77.52 | Conceptual | 178296000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5807 | 2010-07-13 | LN | 2025-01-01 | Grimes | Lehigh | 1 | 345 |  | 1510 |  |  | IA |  | 61.92 | Conceptual | 99072000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5897 | 2010-07-13 | Sub | 2025-01-01 | Hills | new substation | 1 | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5905 | 2010-07-13 | Sub | 2025-01-01 | Lehigh | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5917 | 2010-07-13 | Sub | 2025-01-01 | Montezuma | new substation | 1 | 345 |  |  | Add 6 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 35400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5869 | 2010-07-13 | Sub | 2025-01-01 | Bondurant | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | IA |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5868 | 2010-07-13 | Sub | 2025-01-01 | Blackhawk | new substation | 1 | 345 | 161 |  | Add 4 new 345 bay(s) at New station. Add 2 new 161 bay(s) at New station. Add 2 new 345/161 autotransformer(s). |  | IA |  |  | Conceptual | 44000000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5853 | 2010-07-13 | LN | 2025-01-01 | Bondurant | Montezuma | 1 | 345 |  | 1510 | Equipment upgrade to increase line rating |  | IA | 58.08 |  | Conceptual | 92928000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5856 | 2010-07-13 | LN | 2025-01-01 | Montezuma | Hills | 1 | 345 |  | 1510 | Equipment upgrade to increase line rating |  | IA | 63.84 |  | Conceptual | 102144000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5854 | 2010-07-13 | LN | 2025-01-01 | Bondurant | Sycamore | 1 | 345 |  | 1510 | Equipment upgrade to increase line rating |  | IA | 12 |  | Conceptual | 19200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5845 | 2010-07-13 | LN | 2025-01-01 | Webster | Blackhawk | 1 | 345 |  | 1510 |  |  | IA |  | 106.08 | Conceptual | 169728000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5829 | 2010-07-13 | LN | 2025-01-01 | Montezuma | Hills | 2 | 345 |  | 1510 |  |  | IA |  | 63.84 | Conceptual | 102144000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC | 3202 | 2010-07-13 | RGOS Native | 5890 | 2010-07-13 | Sub | 2025-01-01 | Grimes | new substation | 1 | 345 |  |  | Add 5 new 345 bay(s) at New station. |  | IA |  |  | Conceptual | 35400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC, ALTW | 3200 | 2010-07-13 | RGOS 765 | 5677 | 2010-07-13 | LN | 2025-01-01 | Grimes | Guthrie Center | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | IA |  | 42.0246 | Conceptual | 96656580 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC, ALTW | 3200 | 2010-07-13 | RGOS 765 | 5704 | 2010-07-13 | LN | 2025-01-01 | Webster | IA-G Station | 1 | 345 |  | 1510 |  |  | IA |  | 72.9854 | Conceptual | 116776704 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC, ALTW | 3202 | 2010-07-13 | RGOS Native | 5806 | 2010-07-13 | LN | 2025-01-01 | Grimes | Guthrie Center | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | IA |  | 42 | Conceptual | 96600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC, ALTW | 3202 | 2010-07-13 | RGOS Native | 5846 | 2010-07-13 | LN | 2025-01-01 | Webster | IA-G Station | 1 | 345 |  | 1510 |  |  | IA |  | 72.96 | Conceptual | 116736000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MEC, ALTW | 3202 | 2010-07-13 | RGOS Native | 5820 | 2010-07-13 | LN | 2025-01-01 | Lehigh | IA-G Station | 1 | 345 |  | 1510 |  |  | IA |  | 69.36 | Conceptual | 110976000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MPW | 2935 | 2010-09-21 | MPW-WR | 5108 | 2010-09-21 | LN | 2017-06-01 | Wiggins | Power Plant | 1 | 69 |  | 89 | Reconductor Line from 336.4 to 636 ACSR |  | IA | 4.2 |  | Proposed | 252000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | MPW | 2935 | 2010-09-21 | MPW-WR | 5107 | 2010-09-21 | LN | 2017-06-01 | South | Wiggins | 1 | 69 |  | 89 | Reconductor Line from 336.4 to 636 ACSR |  | IA | 0.8 |  | Proposed | 48000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5756 | 2010-07-13 | Sub | 2025-01-01 | Oakes | upgrade existing substation |  | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 34600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5759 | 2010-07-13 | Sub | 2025-01-01 | Prairie | new substation |  | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5734 | 2010-07-13 | Sub | 2025-01-01 | Hankinson | upgrade existing substation |  | 345 | 230 |  | Add 6 new 345 bay(s) at New station. Add 2 new 230 bay(s) at Existing station. Add 2 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 52900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5742 | 2010-07-13 | Sub | 2025-01-01 | Maple River | new substation |  | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5721 | 2010-07-13 | Sub | 2025-01-01 | Center | new substation |  | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5727 | 2010-07-13 | Sub | 2025-01-01 | Forman | upgrade existing substation |  | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 34600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5680 | 2010-07-13 | LN | 2025-01-01 | Hankinson | Forman | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 42.9337 | Conceptual | 81574068 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5690 | 2010-07-13 | LN | 2025-01-01 | Maple River | Hankinson | 1 | 345 |  | 1510 |  |  | ND |  | 66.3631 | Conceptual | 92908368 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5691 | 2010-07-13 | LN | 2025-01-01 | Maple River | Prairie | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 83.0802 | Conceptual | 157852380 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3200 | 2010-07-13 | RGOS 765 | 5697 | 2010-07-13 | LN | 2025-01-01 | Oakes | Forman | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 26.5651 | Conceptual | 50473728 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5810 | 2010-07-13 | LN | 2025-01-01 | Hankinson | Forman | 1 | 345 |  | 1510 |  |  | ND |  | 42.96 | Conceptual | 60144000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5906 | 2010-07-13 | Sub | 2025-01-01 | Maple River | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | ND |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5929 | 2010-07-13 | Sub | 2025-01-01 | Oakes | new substation | 1 | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 34600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5857 | 2010-07-13 | LN | 2025-01-01 | Prairie | Winger | 1 | 230 |  | 389 | Equipment upgrade to increase line rating |  | ND | 69.6 |  | Conceptual | 52200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5867 | 2010-07-13 | Sub | 2025-01-01 | Big Stone | new substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at New station. |  | SD |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5833 | 2010-07-13 | LN | 2025-01-01 | Oaks | Forman | 1 | 345 |  | 1510 |  |  | ND |  | 26.52 | Conceptual | 37128000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5884 | 2010-07-13 | Sub | 2025-01-01 | Forman | new substation | 1 | 345 | 230 |  | Add 3 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 34600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5894 | 2010-07-13 | Sub | 2025-01-01 | Hankinson | new substation | 1 | 345 | 230 |  | Add 5 new 345 bay(s) at New station. Add 2 new 230 bay(s) at New station. Add 2 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 57400000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5823 | 2010-07-13 | LN | 2025-01-01 | Maple River | Prairie | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 83.04 | Conceptual | 157776000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP | 3202 | 2010-07-13 | RGOS Native | 5822 | 2010-07-13 | LN | 2025-01-01 | Maple River | Hankinson | 1 | 345 |  | 1510 |  |  | ND |  | 66.36 | Conceptual | 92904000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP, GRE | 3200 | 2010-07-13 | RGOS 765 | 5669 | 2010-07-13 | LN | 2025-01-01 | Center | McHenry | 1 | 345 |  | 1510 |  |  | ND |  | 80.3318 | Conceptual | 112464576 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP, GRE | 3200 | 2010-07-13 | RGOS 765 | 5699 | 2010-07-13 | LN | 2025-01-01 | Prairie | ND-New Station | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND |  | 66.4842 | Conceptual | 126319980 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP, MDU | 3200 | 2010-07-13 | RGOS 765 | 5765 | 2010-07-13 | Sub | 2025-01-01 | Tetonka | new substation |  | 345 | 230 |  | Add 7 new 345 bay(s) at New station. Add 2 new 230 bay(s) at New station. Add 2 new 345/230 autotransformer(s). |  | ND |  |  | Conceptual | 69200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP, MDU | 3200 | 2010-07-13 | RGOS 765 | 5671 | 2010-07-13 | LN | 2025-01-01 | Center | Tetonka | 1 | 345 |  | 1510 |  |  | ND |  | 150.4932 | Conceptual | 210690480 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | OTP, WAPA | 3202 | 2010-07-13 | RGOS Native | 5792 | 2010-07-13 | LN | 2025-01-01 | Big Stone | Granite Falls | 1 | 345 |  | 1510 |  |  | MN/SD |  | 69.12 | Conceptual | 122688000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | WAPA | 3202 | 2010-07-13 | RGOS Native | 5795 | 2010-07-13 | LN | 2025-01-01 | Center | MT_Zone | 1 | 345 |  | 1510 |  |  | MT/ND |  | 201.6 | Conceptual | 282240000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | WAPA | 3202 | 2010-07-13 | RGOS Native | 5791 | 2010-07-13 | LN | 2025-01-01 | Brookings County | White | 1 | 115 |  | 160 |  |  | SD |  | 0.6 | Conceptual | 300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | WAPA, MDU | 3202 | 2010-07-13 | RGOS Native | 5804 | 2010-07-13 | LN | 2025-01-01 | Fort Thompson | Tetonka | 1 | 345 |  | 1510 |  |  | ND/SD |  | 163.2 | Conceptual | 228480000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3121 | 2010-01-27 |  | 5470 | 2010-01-27 | LN | 2016-06-01 | Kenrick | Ritter Park | 1 | 115 |  |  | Upgrade to 2-795 ACSR |  | MN |  |  | Planned | [6 empty] | Y | B
B in MTEP10 | West | XEL | 3121 | 2010-01-27 |  | 5471 | 2010-01-27 | LN | 2016-06-01 | Ritter Park | Dakota Heights | 1 | 115 |  |  | Upgrade to 2-795 ACSR |  | MN |  |  | Planned | [6 empty] | Y | B
B in MTEP10 | West | XEL | 3121 | 2010-01-27 |  | 5469 | 2010-01-27 | LN | 2016-06-01 | Lake Marion | Kenrick | 1 | 115 |  |  | Upgrade to 2-795 ACSR |  | MN |  |  | Planned | 6200000 | [5 empty] | Y | B
B in MTEP10 | West | XEL | 3121 | 2010-01-27 |  | 5472 | 2010-01-27 | LN | 2016-06-01 | Dakota Heights | Burnsville | 1 | 115 |  |  | Upgrade to 2-795 ACSR |  | MN |  |  | Planned | [6 empty] | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5766 | 2010-07-13 | Sub | 2025-01-01 | White | upgrade existing substation |  | 345 | 115 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 115 bay(s) at Existing station. Add 1 new 345/115 autotransformer(s). |  | SD |  |  | Conceptual | 16100000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5761 | 2010-07-13 | Sub | 2025-01-01 | SD-H Station | new substation |  | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | SD |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5666 | 2010-07-13 | LN | 2025-01-01 | Brookings County | Hampton Corner | 1 | 765 |  | 3975 |  |  | MN/SD |  | 210.7278 | Conceptual | 734385859.2 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5665 | 2010-07-13 | LN | 2025-01-01 | Brookings County | New 765 Sub 2 | 1 | 765 |  | 3975 |  |  | MN/SD |  | 20.1924 | Conceptual | 66696772.8 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5664 | 2010-07-13 | LN | 2025-01-01 | New 765 Sub 1 | New 765 Sub 2 | 1 | 765 |  | 3975 |  |  | MN |  | 25.8262 | Conceptual | 90391560 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5667 | 2010-07-13 | LN | 2025-01-01 | Brookings County | SD-H station | 1 | 345 |  | 1510 |  |  | SD |  | 58.0226 | Conceptual | 81231696 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 4059 | 2010-07-13 | Sub | 2025-01-01 | Hampton Corner | upgrade existing substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 765/345 autotransformer(s). |  | MN |  |  | Conceptual | 84300000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5722 | 2010-07-13 | Sub | 2025-01-01 | New 765 Sub 2 | new substation |  | 765 | 115 |  | Add 4 new 765 bay(s) at New station. Add 2 new 115 bay(s) at New station. Add 2 new 765/115 autotransformer(s). |  | MN |  |  | Conceptual | 100600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5720 | 2010-07-13 | Sub | 2025-01-01 | New 765 Sub 1 | new substation |  | 765 | 115 |  | Add 4 new 765 bay(s) at New station. Add 2 new 115 bay(s) at New station. Add 2 new 765/115 autotransformer(s). |  | MN |  |  | Conceptual | 100600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5719 | 2010-07-13 | Sub | 2025-01-01 | Brookings County | new substation |  | 765 | 345 |  | Add 4 new 765 bay(s) at New station. Add 2 new 345 bay(s) at New station. Add 2 new 765/345 autotransformer(s). |  | SD |  |  | Conceptual | 118200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5717 | 2010-07-13 | Sub | 2025-01-01 | Alexandria | upgrade existing substation |  | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | MN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5695 | 2010-07-13 | LN | 2025-01-01 | MN-K Station | IA-J Station | 1 | 345 |  | 1510 |  |  | IA/MN |  | 48.188 | Conceptual | 78101486.4 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5688 | 2010-07-13 | LN | 2025-01-01 | Lakefield Junction | New 765 Sub 1 | 1 | 765 |  | 3975 |  |  | MN |  | 58.0798 | Conceptual | 203279160 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5749 | 2010-07-13 | Sub | 2025-01-01 | MN-K Station | new substation |  | 765 | 345 |  | Add 3 new 765 bay(s) at New station. Add 1 new 765/345 autotransformer(s). |  | MN |  |  | Conceptual | 78200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3200 | 2010-07-13 | RGOS 765 | 5701 | 2010-07-13 | LN | 2025-01-01 | SD-H Station | SD-J Station | 1 | 345 |  | 1510 |  |  | SD |  | 53.4794 | Conceptual | 74871216 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5793 | 2010-07-13 | LN | 2025-01-01 | Buffalo Ridge | Chanarambie | 1 | 345 |  | 1510 |  |  | MN |  | 25.8 | Conceptual | 46440000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5789 | 2010-07-13 | LN | 2025-01-01 | Brookings County | Buffalo Ridge | 1 | 345 |  | 1510 |  |  | MN/SD |  | 20.16 | Conceptual | 34032000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5864 | 2010-07-13 | Sub | 2025-01-01 | Alexandria | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MN |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5941 | 2010-07-13 | Sub | 2025-01-01 | Sioux City | new substation | 1 | 345 | 230 |  | Add 2 new 345 bay(s) at New station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | IA |  |  | Conceptual | 22800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5937 | 2010-07-13 | Sub | 2025-01-01 | SD-H Station | new substation | 1 | 345 |  |  | Add 3 new 345 bay(s) at New station. |  | SD |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5943 | 2010-07-13 | Sub | 2025-01-01 | Split Rock | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | SD |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5947 | 2010-07-13 | Sub | 2025-01-01 | Watertown | upgrade existing substation | 1 | 345 | 230 |  | Add 1 new 345 bay(s) at Existing station. Add 1 new 230 bay(s) at Existing station. Add 1 new 345/230 autotransformer(s). |  | SD |  |  | Conceptual | 16900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5915 | 2010-07-13 | Sub | 2025-01-01 | MN-K Station | new substation | 1 | 345 |  |  | Add 2 new 345 bay(s) at New station. |  | MN |  |  | Conceptual | 11800000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5904 | 2010-07-13 | Sub | 2025-01-01 | Lakefield | new substation | 1 | 345 | 161 |  | Add 3 new 345 bay(s) at New station. Add 1 new 345 bay(s) at Existing station. Add 1 new 345/161 autotransformer(s). |  | MN |  |  | Conceptual | 23500000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5918 | 2010-07-13 | Sub | 2025-01-01 | Monticello | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | MN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5922 | 2010-07-13 | Sub | 2025-01-01 | North Rochester | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | MN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5870 | 2010-07-13 | Sub | 2025-01-01 | Brookings County | new substation | 1 | 345 |  |  | Add 4 new 345 bay(s) at New station. |  | SD |  |  | Conceptual | 23600000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5790 | 2010-07-13 | LN | 2025-01-01 | Brookings County | SD-H Station | 1 | 345 |  | 1510 |  |  | SD |  | 58.08 | Conceptual | 81312000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5871 | 2010-07-13 | Sub | 2025-01-01 | Buffalo Ridge | new substation | 1 | 345 | 115 |  | Add 2 new 345 bay(s) at New station. Add 2 new 115 bay(s) at New station. Add 2 new 345/115 autotransformer(s). |  | MN |  |  | Conceptual | 32200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5873 | 2010-07-13 | Sub | 2025-01-01 | Chanarambie | new substation | 1 | 345 | 115 |  | Add 2 new 345 bay(s) at New station. Add 2 new 115 bay(s) at New station. Add 2 new 345/115 autotransformer(s). |  | MN |  |  | Conceptual | 32200000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5863 | 2010-07-13 | Sub | 2025-01-01 | Adams | upgrade existing substation | 1 | 345 |  |  | Add 1 new 345 bay(s) at Existing station. |  | MN |  |  | Conceptual | 5900000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5828 | 2010-07-13 | LN | 2025-01-01 | Monticello | Alexandria | 1 | 345 |  | 1510 |  |  | MN |  | 97.8 | Conceptual | 176040000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL | 3202 | 2010-07-13 | RGOS Native | 5825 | 2010-07-13 | LN | 2025-01-01 | Minnesota Valley | Hazel | 1 | 230 |  | 338 |  |  | MN |  | 7.44 | Conceptual | 5580000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, ALTW | 3202 | 2010-07-13 | RGOS Native | 5786 | 2010-07-13 | LN | 2025-01-01 | Adams | Mitchell County | 1 | 345 |  | 956 |  |  | IA/MN |  | 8.04 | Conceptual | 14016000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, DPC | 3202 | 2010-07-13 | RGOS Native | 5832 | 2010-07-13 | LN | 2025-01-01 | North Rochester | North LaCrosse | 1 | 345 |  | 1510 |  |  | MN/WI |  | 69.84 | Conceptual | 126432000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, MDU | 3200 | 2010-07-13 | RGOS 765 | 5702 | 2010-07-13 | LN | 2025-01-01 | SD-H Station | Tetonka | 1 | 345 |  | 1510 |  |  | ND/SD |  | 151.9918 | Conceptual | 212788464 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, MDU | 3202 | 2010-07-13 | RGOS Native | 5839 | 2010-07-13 | LN | 2025-01-01 | SD-H Station | Tetonka | 2 | 345 |  | 1510 | 2nd circuit of double circuit |  | ND/SD |  | 151.92 | Conceptual | 288648000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, MEC | 3200 | 2010-07-13 | RGOS 765 | 5689 | 2010-07-13 | LN | 2025-01-01 | Lakefield Junction | IA-G Station | 1 | 765 |  | 3975 |  |  | IA/MN |  | 109.7532 | Conceptual | 355430412 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, MEC | 3202 | 2010-07-13 | RGOS Native | 5827 | 2010-07-13 | LN | 2025-01-01 | MN-K Station | IA-J Station | 1 | 345 |  | 1510 |  |  | IA/MN |  | 48.24 | Conceptual | 78192000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, OTP | 3200 | 2010-07-13 | RGOS 765 | 5663 | 2010-07-13 | LN | 2025-01-01 | Alexandria | Hankinson | 1 | 345 |  | 1510 |  |  | MN/ND |  | 90.59 | Conceptual | 155254104 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, OTP | 3202 | 2010-07-13 | RGOS Native | 5787 | 2010-07-13 | LN | 2025-01-01 | Alexandria | Hankinson | 1 | 345 |  | 1510 |  |  | MN/ND |  | 90.6 | Conceptual | 155256000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, WAPA | 3202 | 2010-07-13 | RGOS Native | 5843 | 2010-07-13 | LN | 2025-01-01 | Split Rock | Sioux City | 1 | 345 |  | 717 |  |  | IA/SD |  | 85.2 | Conceptual | 129288000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West | XEL, WAPA | 3202 | 2010-07-13 | RGOS Native | 5859 | 2010-07-13 | LN | 2025-01-01 | Split Rock | White | 1 | 345 |  | 1308 | Equipment upgrade to increase line rating |  | SD | 70.8 |  | Conceptual | 99120000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Central | AmerenIL, MEC | 3202 | 2010-07-13 | RGOS Native | 5785 | 2010-07-13 | LN | 2025-01-01 | Fargo | Oak Grove | 1 | 345 |  | 1510 |  |  | IL |  | 73.92 | Conceptual | 110880000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Central | MIPU, MEC | 3200 | 2010-07-13 | RGOS 765 | 5661 | 2010-07-13 | LN | 2025-01-01 | Fairport | Grimes | 1 | 765 |  | 3975 |  |  | IA/MO |  | 140.9237 | Conceptual | 450955776 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | CE, ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5668 | 2010-07-13 | LN | 2025-01-01 | Byron | Darlington | 1 | 765 |  | 3975 |  |  | IL/WI |  | 70.6774 | Conceptual | 221095152 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | CE, ATC LLC | 3200 | 2010-07-13 | RGOS 765 | 5687 | 2010-07-13 | LN | 2025-01-01 | Liberty | Elm Road | 1 | 345 |  | 1510 |  |  | IL/WI |  | 44.6964 | Conceptual | 84763368 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | CE, ATC LLC | 3202 | 2010-07-13 | RGOS Native | 5821 | 2010-07-13 | LN | 2025-01-01 | Liberty | Elm Road | 1 | 345 |  | 1510 |  |  | IL/WI |  | 44.64 | Conceptual | 84672000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | CE, MEC | 3200 | 2010-07-13 | RGOS 765 | 5700 | 2010-07-13 | LN | 2025-01-01 | Quad Cities | Hills | 1 | 765 |  | 3975 |  |  | IA/IL |  | 77.2633 | Conceptual | 246977134.56 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | CE, MEC | 3202 | 2010-07-13 | RGOS Native | 5797 | 2010-07-13 | LN | 2025-01-01 | Cordova | Hills | 1 | 345 |  | 1510 |  |  | IA/IL |  | 78.84 | Conceptual | 125928000 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | OTP, WAPA | 3200 | 2010-07-13 | RGOS 765 | 5670 | 2010-07-13 | LN | 2025-01-01 | Center | Mt. Zion | 1 | 345 |  | 1510 |  |  | MT/ND |  | 201.5137 | Conceptual | 282119208 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | WAPA, MDU | 3200 | 2010-07-13 | RGOS 765 | 5676 | 2010-07-13 | LN | 2025-01-01 | Fort Thompson | Tetonka | 1 | 345 |  | 1510 |  |  | ND/SD |  | 163.1283 | Conceptual | 228379552.8 | Planning |  |  |  |  | Y | B
B in MTEP10 | West/Non-MISO | XEL, WAPA | 3200 | 2010-07-13 | RGOS 765 | 5715 | 2010-07-13 | LN | 2025-01-01 | Split Rock | White | 1 | 345 |  | 1308 | Equipment upgrade to increase line rating |  | SD | 70.8 |  | Conceptual | 99120000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 2967 | 2011-04-22 |  | 5166 | 2011-04-22 | CAP | 2013-06-01 | Grand Tower Plant | 2-Stage, 80 Mvar Capacitor Bank | 1 | 138 |  | 80 | Grand Tower Plant - Install 2-stage 80 Mvar (2 x 40 Mvar) 138 kV capacitor bank. 2-138 kV PCB's needed. | K11 | IL |  |  | Proposed | 2715000 | Engineering |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 2977 | 2011-04-22 |  | 5180 | 2009-09-14 | LN | 2013-06-01 | LaSalle-Oglesby 138 kV | Relocate LaSalle Substation | 1 | 138 |  | 120 | LaSalle 138-34.5 kV Substation - Relocate Substation to avoid flooding and to permit remediation of manufactured gas plant site. (Approx. 1 mile move.) | K8 | IL |  |  | Proposed | 1347000 | Engineering |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 2979 | 2011-04-22 |  | 5182 | 2009-09-14 | CB | 2013-06-01 | AECI Enon Substation | Install 2-345 kV Breakers |  | 345 |  |  | Enon 345/161 kV Substation - Install 2-345 kV PCB's on incoming 345 kV lines. (Belleau-Enon and Enon-Montgomery | J10 | MO |  |  | Proposed | 1876000 | Engineering |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 2982 | 2011-04-22 |  | 5185 | 2009-09-14 | TEQ | 2013-12-01 | Washington Street | South Bloomington | 1326 | 138 |  | 255 | Washington Street-S. Bloomington 138 kV Line 1326 - Replace terminal equipment (wavetrap, 3-CT's and bus conductor) at S. Bloomington with equipment capable of carrying minimum 2000 A under summer emergency conditions. | K9 | IL |  |  | Proposed | 137000 | Engineering |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 3009 | 2011-04-22 | AMRN12 | 5217 | 2010-07-08 | LN | 2018-06-01 | Hutsonville Plant | Merom | 1 | 345 |  | 1793 | Newton-Hutsonville 345 kV line – New 40 mi. 3000 A summer emergency capability line. Hutsonville-Merom 345 kV line - New 12 mi. 3000 A summer emergency capability line. 345/138 kV 560 MVA transformer @ Hutsonville | L10 | IL |  | 12 | Proposed | 100000000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 3009 | 2011-04-22 | AMRN12 | 5218 | 2009-12-23 | TX | 2018-06-01 | Hutsonville Plant | Install 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Newton-Hutsonville 345 kV line – New 40 mi. 3000 A summer emergency capability line. Hutsonville-Merom 345 kV line - New 12 mi. 3000 A summer emergency capability line. 345/138 kV 560 MVA transformer @ Hutsonville | L10 | IL |  |  | Proposed | 10000000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 3010 | 2011-04-22 | AMRN13 | 5219 | 2010-12-06 | LN | 2025-12-01 | Baldwin | N.W. Cape | 1 | 345 |  | 1793 | Baldwin-Grand Tower-N.W. Cape 345 kV - Construct 69 miles of 3000 A summer emergency capability. Install a 560 MVA, 345/138 kV transformer at Grand Tower | K11 | IL |  | 69 | Proposed | 146000000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 3010 | 2011-04-22 | AMRN13 | 5220 | 2010-12-06 | TX | 2025-12-01 | Grand Tower Plant | Install 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Install a 560 MVA, 345/138 kV transformer at Grand Tower | K11 | IL |  |  | Proposed | 5000000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenIL | 3201 | 2011-04-22 | RGOS DC | 5775 | 2010-07-13 | Sub | 2025-01-01 | Grand Tower | DC Station for 6400 MW |  | 800 |  | 6400 |  |  | IL |  |  | Conceptual | 274500000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenMO | 2971 | 2011-04-22 | AMRN5 | 5171 | 2010-12-06 | LN | 2012-06-01 | Rivermines-Maries-1 | Tap for Rolla Alfermann Substation | 1 | 138 |  | 478 | Rolla Alfermann Substation - Tap Rivermines-Maries-1 138 kV line to establish 138 kV supply to new 138-34.5 kV Alfermann Substation, owned by City of Rolla. Ameren to construct tapping structures. 1-138 kV, 1200 A disconnect switch | I11 | MO |  |  | Planned | 481500 | Engineering |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenMO | 2971 | 2011-04-22 | AMRN5 | 5170 | 2010-12-06 | LN | 2012-06-01 | Clark-O-2 | Tap for Rolla Alfermann Substation | 1 | 138 |  | 478 | Rolla Alfermann Substation - Tap Clark-Osage-2 138 kV line to establish 138 kV supply to new 138-34.5 kV Alfermann Substation, owned by City of Rolla. Ameren to construct tapping structures. 1-138 kV, 1200 A disconnect switch. | I11 | MO |  |  | Planned | 481500 | Engineering |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenMO | 2973 | 2011-04-22 |  | 5174 | 2010-12-06 | SUB | 2016-12-01 | Mason-Carrollton-8 | Connection to Howard Bend 138-12 kV Sub | 1 | 138 |  | 478 | Howard Bend 138-12 kV Substation - Provide 138 kV ring bus connection from Mason-Carrollton-8 138 kV line to new Howard Bend Substation. Install 1-138 kV, 2000 A PCB at Carrollton Substation as a bus-tie. | J11 | MO |  |  | Proposed | 1371000 | Planning |  |  |  |  | Y | B
B in MTEP11 | Central | AmerenMO | 2988 | 2011-04-22 |  | 5192 | 2011-04-22 | LN | 2016-06-01 | Warrenton | Lincoln 138-34.5 kV Bulk | 1 | 161 |  | 280 | Warrenton-Lincoln Bulk Substation 161 kV - Establish a second 161 kV supply to Lincoln Bulk Substation from Warrenton Substation. 10 miles of new 161 kV line, 2-161 kV, 2000 A PCBs at Warrenton Substation. | J10 | MO |  | 10 | Proposed | 12000000 | Planning |  |  |  |  | Y | B
B in MTEP11 | East | ITC | 3282 | 2010-09-15 | 8 | 6114 | 2010-09-15 | LNrb | 2013-12-31 | Southfield | Sunset | 1 | 120 |  | 220 | Rebuild 6.4 mile 120 kV line |  | Mi | 6.4 |  | Planned | 7100000 | Planning |  |  |  |  | Y | C>B
B in MTEP11 | East | METC | 1803 | 2011-03-28 |  | 3618 | 2011-03-28 | LNrb | 2013-12-31 | Plum | Stover | 1 | 138 |  | 191 | Rebuild 8.8 miles (230 kV construction, operate at 138 kV) |  | MI | 8.8 |  | Planned | 10900000 | Planning |  |  |  |  | Y | C>B
B in MTEP11 | East | METC | 1815 | 2011-03-28 |  | 3649 | 2011-03-28 | LNrb | 2014-12-31 | Chase | Mecosta | 1 | 138 |  | 108 | Rebuild 7.2 miles (230 kV construction, operate at 138 kV) |  | MI | 7.2 |  | Planned | 8900000 | Planning |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 2799 | 2010-09-15 |  | 4924 | 2010-04-30 | LN | 2013-07-01 | Kinchelo Tap | Kinross | 1 | 69 |  | 84 MVA | Construct a 3 mile line to connect the Kinross load |  | MI |  | 3 | Conceptual | 3882248 | eng | Interconnection |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3119 | 2010-09-15 | 3119 | 5464 | 2010-06-18 | LN | 2016-06-01 | Tone | Kincheloe | 1 | 69 |  | 48 MVA | Increase ground clearance for 6923 Pine River-9Mile 69kV line to 167 deg f clearance |  | MI | 2.51 |  | Proposed | 299043 | eng |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3119 | 2010-09-15 | 3119 | 5465 | 2010-06-18 | LN | 2016-06-01 | Kincheloe | 9 Mile | 1 | 69 |  | 48 MVA | Increase ground clearance for 6923 Pine River-9Mile 69kV line to 167 deg f clearance |  | MI | 8.18 |  | Proposed | 980861 | eng |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3119 | 2010-09-15 | 3119 | 5463 | 2010-06-18 | LN | 2016-06-01 | Rudyard | Tone | 1 | 69 |  | 48 MVA | Increase ground clearance for 6923 Pine River-9Mile 69kV line to 167 deg f clearance |  | MI | 5.85 |  | Proposed | 693780 | eng |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3119 | 2010-09-15 | 3119 | 5462 | 2010-06-18 | LN | 2016-06-01 | Pine River | Rudyard | 1 | 69 |  | 48 MVA | Increase ground clearance for 6923 Pine River-9Mile 69kV line to 167 deg f clearance |  | MI | 0.22 |  | Proposed | 26316 | eng |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3209 | 2010-09-15 |  | 5976 | 2011-02-24 | TX | 2013-10-25 | Edgewater | Transformer | 1 | 138 | 69 | 60 | Replace Edgewater 138/69kV Tr T21 with a larger unit and uprate terminal equipment to a minimum of the transformer ratings |  | WI |  |  | Proposed | 2704736 | eng |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3209 | 2010-09-15 |  | 5977 | 2011-02-24 | TX | 2013-10-25 | Edgewater | Transformer | 2 | 138 | 69 | 60 | Replace Edgewater 138/69kV Tr T22 with a larger unit and uprate terminal equipment to a minimum of the transformer ratings |  | WI |  |  | Proposed | 2704735 | eng |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3490 | 2011-03-22 | PR04027 | 6450 | 2011-03-22 | Line | 2013-04-15 | Doylestown | Rio Pumping Station | 1 | 69 |  | 72 | Asset Management project to Rebuild Y-20 Doylestown to Rio Pumping Station |  | WI | 11.46 |  | Planned | 7400000 | Engineering |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3514 | 2011-06-07 |  | 6493 | 2011-06-07 | SS | 2013-09-01 | 96th Street Sub |  |  | 138 |  |  |  |  | WI |  |  | Proposed | 28000000 | Planning |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3514 | 2011-06-07 |  | 6494 | 2011-06-07 | Load | 2013-09-01 | Walker Load Move | [5 empty] | Relocate Walker Load from line 96S to line 5042 BMD |  | WI |  |  | Proposed |  | Planning |  |  |  |  | Y | C>B
B in MTEP11 | West | ATC LLC | 3519 | 2011-07-12 | PR04441 | 6515 | 2011-07-12 | SUB | 2012-12-31 | Riverbend |  |  | 138 | 24.9 |  | Loop the Ranegline-Port Washington 138 kV line 731 into a new breakered Riverbend SS |  | WI |  | 0.078 | Proposed | 3016359 | Engineering |  |  |  |  | Y | C>B
B in MTEP11 | West | MEC | 3201 | 2011-04-22 | RGOS DC | 5774 | 2010-07-13 | Sub | 2025-01-01 | IA-G | DC Station for 6400 MW |  | 800 |  | 6400 |  |  | IA |  |  | Conceptual | 274500000 | Planning |  |  |  |  | Y | B
B in MTEP11 | West | MEC | 3201 | 2011-04-22 | RGOS DC | 5772 | 2010-07-13 | Sub | 2025-01-01 | Lakefield Jct | DC Station for 6400 MW |  | 800 |  | 6400 |  |  | MN |  |  | Conceptual | 274500000 | Planning |  |  |  |  | Y | B
B in MTEP11 | West | MEC | 3201 | 2011-04-22 | RGOS DC | 5773 | 2010-07-13 | Sub | 2025-01-01 | IA-B | DC Station for 6400 MW |  | 800 |  | 6400 |  |  | IA |  |  | Conceptual | 274500000 | Planning |  |  |  |  | Y | B
B in MTEP11 | West | MEC | 3214 | 2010-09-07 | G1405 | 6098 | 2010-09-07 | TEQ | 2015-12-01 | Sub 17 | Sub 39 | 1 | 161 |  | 260 | Sub 17 & Sub 39 Replace Relays 161-17-39-1 and Remove Wave Trap |  | IL |  |  | Proposed | 225000 | Planning 2010$ |  |  |  |  | Y | C>B
B in MTEP11 | West | MEC | 3215 | 2010-09-07 | T6242 | 6089 | 2010-09-07 | CAP | 2014-06-01 | Sub 49 | Capacitor |  | 161 |  | 50 | Sub 49 161 kV 50 MVAr Capacitor |  | IL |  |  | Proposed | 840000 | Planning 2010$ |  |  |  |  | Y | C>B
B in MTEP11 | West | MEC | 3216 | 2011-02-15 | G1352 | 6096 | 2010-09-07 | TEQ | 2014-06-01 | Plymouth |  |  | 161 |  | 450 | Plymouth Substation 161 kV Line Terminal |  | IA |  |  | Planned | 500000 | Planning 2010$ |  |  |  |  | Y | C>B
B in MTEP11 | West | MEC | 3216 | 2011-02-15 | G1352 | 6097 | 2010-09-07 | TEQ | 2014-06-01 | Sioux City |  |  | 161 |  | 450 | WAPA Sioux City 161kV Line Terminal |  | IA |  |  | Planned | 500000 | Planning 2010$ |  |  |  |  | Y | C>B
B in MTEP11 | West | MEC | 3216 | 2011-02-15 | G1352 | 6095 | 2010-09-07 | LN | 2014-06-01 | Plymouth | Sioux City | 2 | 161 |  | 450 | Plymouth-Sioux City 161 kV Line |  | IA |  | 2 | Planned | 1400000 | Planning 2010$ |  |  |  |  | Y | C>B
B in MTEP11 | West | MEC | 3266 | 2010-09-07 | T6164 | 6085 | 2010-09-07 | LNrb | 2016-06-01 | Sub 56 | Sub 89 | 1 | 161 |  | 314 | Sub 56-89 161 kV line uprate |  | IA | 22 |  | Proposed | 680000 | Planning 2010$ |  |  |  |  | Y | C>B
B in MTEP11 | West | OTP | 3431 | 2010-09-28 |  | 6327 | 2010-09-28 | TX | 2012-10-01 | Hankinson 230 | Hankinson 41.6 |  | 230 | 41.6 |  | Add a second 230/41.6 kV transformer at Hankinson Substation which will include the addition of 2 new 230 kV breakers. |  | ND |  |  | Planned | 835000 | Planning |  |  |  |  | Y | C>B
B in MTEP11 | West | OTP | 3462 | 2011-01-11 | Project G-968 100 MW Wind Farm near Viking MN | 6388 | 2011-01-01 | LN | 2012-10-30 | Karlstad 115 kV | Viking 115 kV | 1 | 115 | 115 |  | Add 3 breaker 115 kV ring bus |  | MN |  |  | Proposed | 2800000 | Planning |  |  |  |  | Y | C>B
B in MTEP11 | West | OTP | 3464 | 2011-01-11 | Project G-873 20 MW Wind Donaldson 41.6 kV LN | 6390 | 2011-07-01 | LN | 2012-12-01 | Donaldson 41.6 | Donaldson -town 41.6 kV | 1 | 41.6 |  |  | Add 3 Way Switch on 41.6 kV line between Donaldson 115 kV substation to Donaldson distribution sub. |  | MN |  |  | Proposed | 160000 | Planning |  |  |  |  | Y | B
B in MTEP11 | West | OTP | 3465 | 2011-01-11 | Project G-875 80 MW Wind Donaldson 115/41.6 kV | 6391 | 2011-01-01 | TX | 2012-12-31 | Donaldson 115 kV | Donaldson 41.6 kV |  | 115 | 41.6 |  | Add 3 new 115 kV Breakers & expand substation to accommodate wind farm. |  | MN |  |  | Proposed | 1500000 | Planning |  |  |  |  | Y | B
B in MTEP11 | West | XEL | 3201 | 2011-04-22 | RGOS DC | 5771 | 2010-07-13 | Sub | 2025-01-01 | Brookings | DC Station for 6400 MW |  | 800 |  | 6400 |  |  | SD |  |  | Conceptual | 274500000 | Planning |  |  |  |  | Y | B
B in MTEP11 | West/Central/N-MISO | MEC, AmerenMo | 3201 | 2011-04-22 | RGOS DC | 5769 | 2010-07-13 | LN | 2025-01-01 | IA-B | Hang Rock | 1 | 765 |  | 6400 |  |  | IA/MO/IL/IN/OH |  | 6401 | Conceptual | 2297669299.2 | Planning |  |  |  |  | Y | B
B in MTEP11 | West/Non-MISO | XEL, Non-MISO | 3201 | 2011-04-22 | RGOS DC | 5770 | 2010-07-13 | LN | 2025-01-01 | Brookings County | Blue Creek | 1 | 765 |  | 6400 |  |  | MN/IA/IL/IN/OH |  | 6401 | Conceptual | 1731350174.4 | Planning |  |  |  |  | Y | B
C | Central | ALTW, Non MISO | 2198 | 2008-08-05 | 39 | 4066 | 2008-08-05 | TX | 2018-08-01 | Pontiac | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | IL |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | Central | ALTW, Non MISO | 2198 | 2008-08-05 | 8 | 4038 | 2008-08-05 | LN | 2018-08-01 | Rock Creek | Pontiac | 1 | 765 |  | 3768 | new line |  | IA/IL |  | 108 | Conceptual | 348000000 | [5 empty] | Y | C
C | Central | Ameren | 1539 | 2007-04-02 |  | 2616 | 2009-09-14 | CB | 2015-06-01 | Roxford | Stallings | 1 | 345 |  | 1195 | Install PCB at Roxford Substation | K10 | IL |  |  | Proposed | 1000000 | [5 empty] | Y | C
C | Central | AmerenIL | 1536 | 2007-04-02 |  | 2613 | 2009-09-14 | LNrc | 2014-06-01 | Latham | Mason City | 1 | 138 |  | 255 | Reconductor Latham Tap-Kickapoo Tap | K9 | IL | 15.75 |  | Proposed | 4670000 | [5 empty] | Y | C
C | Central | AmerenIL | 1538 | 2010-12-06 |  | 2615 | 2010-12-06 | LNrb | 2015-06-01 | Pana, North | Ramsey, East | 1 | 138 |  | 240 | Rebuild line for operation at 120 degrees C | K10 | IL | 18.43 |  | Proposed | 5500000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 1540 | 2008-12-10 |  | 2617 | 2008-12-10 | LNrc | 2014-06-01 | Sidney | Windsor | 1 | 138 |  | 321 | Reconductor to 1600 A Summer Emergency | L9 | IL | 13.1 |  | Proposed | 3900000 | [5 empty] | Y | C
C | Central | AmerenIL | 2232 | 2009-09-22 |  | 4146 | 2009-09-22 | TX | 2018-08-01 | Kewanee | Transformer | 1 | 345 | 138 | 336 | new transformer |  | IL |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | Central | AmerenIL | 2232 | 2009-09-22 |  | 4102 | 2009-09-22 | LN | 2018-08-01 | Kewanee | East Moline | 1 | 345 |  | 1793 | new line |  | IL |  | 30.6 | Conceptual | 34000000 | [5 empty] | Y | C
C | Central | AmerenIL | 2233 | 2009-09-22 |  | 4147 | 2009-09-22 | LN | 2018-08-01 | Kewanee | Tazewell | 1 | 345 |  | 1793 | new line |  | IL |  | 60 | Conceptual | 85000000 | [5 empty] | Y | C
C | Central | AmerenIL | 2242 | 2009-05-06 |  | 4156 | 2010-05-08 | LN | 2020-06-01 | Norris City | Albion | 1 | 345 |  | 1793 | new line |  | IL |  | 25.8 | Conceptual | 50000000 | [5 empty] | Y | C
C | Central | AmerenIL | 2283 | 2008-12-10 |  | 4199 | 2010-12-06 | LN | 2014-06-01 | South Bloomington | 138 kV Bus |  | 138 |  |  | Install two new 2000 A, 138 kV Bus-Tie Breakers | K9 | IL |  |  | Proposed | 1030000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2289 | 2008-08-29 |  | 4205 | 2009-09-14 | LN | 2014-06-01 | Benton | W. Frankfort | 1 | 138 |  | 175 | Reconductor 350 kcmil Copper with 1200 A summmer emergency capability | K11 | IL | 9.62 |  | Proposed | 1871000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2290 | 2009-12-23 |  | 4206 | 2009-09-14 | LN | 2015-06-01 | Joppa | 2nd. 345/161 kV Transformer |  | 345 | 161 | 560 | Install 2nd. 345/161 kV, 560 MVA Transformer | K11 | IL |  |  | Proposed | 4000000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2293 | 2008-08-29 |  | 4209 | 2009-09-14 | LN | 2014-06-01 | N. Lasalle | La Salle Jct. | 1 | 138 |  | 321 | Reconductor 477 kcmil ACSR w/ 1600 A summer emergency capability in L1556A | K8 | IL | 9.68 |  | Proposed | 2515000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2294 | 2009-09-22 |  | 4210 | 2009-09-22 | LN | 2013-06-01 | Stallings 345/138 kV Substation | 138 kV Bus-Tie Position 1302 |  | 138 |  | 478 | Reconnect or replace 1200 A CT to 2000 A | K11 | IL |  |  | Proposed | [6 empty] | Y | C
C | Central | AmerenIL | 2295 | 2008-08-29 |  | 4211 | 2010-12-06 | LN | 2015-06-01 | W. Mt. Vernon | E. W. Frankfort | 1 | 345 |  | 1200 | Upgrade terminal equipment to 3000 A | K11 | IL |  |  | Proposed | 1366000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2299 | 2008-08-29 |  | 4215 | 2009-09-14 | CAP | 2015-06-01 | Fargo 138-69 kV Substation | 138 kV Capacitor Bank |  | 138 |  |  | Install 138 kV Capacitor Bank (size to be determined) | K9 | IL |  |  | Proposed | 1500000 | [5 empty] | Y | C
C | Central | AmerenIL | 2300 | 2009-12-23 |  | 4216 | 2009-12-23 | LN | 2019-06-01 | Hennepin Plant | 2-3000 A PCB's |  | 138 |  |  | Install 2-3000 A, 138 kV Bus-Tie Breaker | K8 | IL |  |  | Proposed | 9124000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2301 | 2008-08-29 |  | 4217 | 2010-12-06 | LN | 2014-06-01 | Hennepin | Oglesby Line 1556 | 1 | 138 |  | 321 | Reconductor 477 kcmil ACSR to 1600 A summer emergency capability | K8 | IL | 8.37 |  | Proposed | 4215000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2302 | 2008-08-29 |  | 4218 | 2009-09-14 | LN | 2015-06-01 | Madison Industrial | Madison State Street | 1 | 138 |  | 240 | Reconductor 795 SAC to 1200 A summer emergency capability | K9 | IL | 2.35 |  | Proposed | 710000 | [5 empty] | Y | C
C | Central | AmerenIL | 2305 | 2008-08-29 |  | 4220 | 2008-08-29 | CAP | 2013-06-01 | Monmouth 138/69 kV Substation | 30 Mvar, 138 kV Capacitor Bank |  | 138 |  |  | Install 30 Mvar, 138 kV Capacitor Bank | J9 | IL |  |  | Proposed | 1022000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenIL | 2983 | 2009-09-14 |  | 5186 | 2009-09-14 | CAP | 2014-06-01 | Mt. Carmel | Install Capacitor Bank(s) |  | 138 |  |  | Mt. Carmel - Install capacitor bank(s). | L11 | IL |  |  | Proposed | 1500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 2985 | 2009-12-10 |  | 5188 | 2009-09-14 | CAP | 2014-06-01 | Monmouth Blvd. Sub. | Install 138 kV, 30 Mvar Capacitor Bank |  | 138 |  | 30 | Monmouth Blvd 138/69 kV Substation - Install 138 kV 30 Mvar capacitor bank and circuit breaker. | J9 | IL |  |  | Proposed | 1500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 2994 | 2009-12-10 |  | 5199 | 2009-09-14 | CB | 2015-06-01 | Wood River-N.Staunton-1436 | Supply to Gillespie Macoupin 138-34.5 kV Sub. | 1 | 138 |  | 280 | Gillespie Macoupin 138-34.5 kV Substation - Tap Wood River-North Staunton 138 kV Line 1436 and make a 138 kV 'in-out' arrangement at the substation with installation of the 2nd. 138-34.5 kV transformer. 2-2000 A, 138 kV PCB's needed. | K10 | IL |  |  | Proposed | 2000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 2995 | 2009-12-10 |  | 5200 | 2009-09-14 | TEQ | 2015-06-01 | Brokaw | Normal East | 1 | 138 |  | 240 | Brokaw 345/138 kV Substation - Replace 477 kcmil ACSR Bus Conductor in Brokaw-Normal East 138 kV Line 1578 position with conductor capable of carrying 1200 A continuously. | K9 | IL |  |  | Proposed | 100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 2999 | 2009-12-10 |  | 5205 | 2009-09-14 | LN | 2015-06-01 | LaSalle | Oglesby | 1496 | 138 |  | 240 | LaSalle-Oglesby Main 138 kV Line 1496 - Reconductor 2.16 miles of 477 kcmil ACSR and 336 kcmil ACSR with conductor capable of carrying 1200 A under summer emergency conditions. | K9 | IL | 2.16 |  | Proposed | 650000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3001 | 2010-12-06 | AMRN10 | 5208 | 2009-09-14 | LN | 2015-06-01 | Baldwin-Pr. State 345 kV | Supply to Mascoutah Sub. | 1 | 345 |  | 1195 | Mascoutah Area 345/138 kV Substation - Supply from the Baldwin-Prairie State 345 kV line. | K11 | IL |  | 1 | Proposed | 1000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3001 | 2010-12-06 | AMRN10 | 5207 | 2009-09-14 | SUB | 2015-06-01 | Mascoutah Area | New 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Mascoutah Area 345/138 kV Substation - Install a new 345/138 kV Substation. 1-560 MVA 345/138 kV transformer, 3-345 kV PCB's, 1-138 kV PCB. | K11 | IL |  |  | Proposed | 8000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3002 | 2009-12-10 |  | 5209 | 2009-09-14 | LN | 2015-06-01 | N. Decatur | Clinton Rt. 54 | 1313 | 138 |  | 240 | N. Decatur-Clinton Rt. 54 138 kV Line 1313 - Reconductor 5.41 miles of 336 kcmil ACSR conductor in the N. Decatur-County Hwy. 20 line section with conductor capable of carrying 1200 A under summer emergency conditions. | K9 | IL | 5.41 |  | Proposed | 1650000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3004 | 2009-12-10 |  | 5211 | 2009-09-14 | CAP | 2015-06-01 | Gilman Sub | Install 138 kV capacitor bank | 1 | 138 |  |  | Gilman 138-69 kV Substation - Install 138 kV capacitor bank and PCB | L9 | IL |  |  | Proposed | 1500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3005 | 2009-12-10 |  | 5212 | 2009-09-14 | TEQ | 2015-12-01 | S. Belleville | Tilden | 1526 | 138 |  | 280 | S. Belleville-Tilden 138 kV Line 1526 - Replace 1200 A terminal equipment (PCB, CT's, and bus conductor) at S. Belleville Substation with equipment capable of carrying 2000 A continuously. | K11 | IL |  |  | Proposed | 1100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3006 | 2009-12-10 |  | 5213 | 2009-09-14 | LN | 2016-06-01 | Vermilion | Champaign | 1396 | 138 |  | 240 | Vermilion-Champaign 138 kV Line 1396 - Reconductor 26.8 miles of 477 kcmil ACSR with minimum 1200 A SE capability. | L9 | IL | 26.8 |  | Conceptual | 8100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3011 | 2009-12-10 |  | 5221 | 2009-09-14 | LN | 2017-06-01 | Joppa | Mound City | 1 | 161 |  | 280 | Joppa-Mound City 161 kV Line - Reconductor 23.4 mi. 556 ACSR with conductor capable of carrying 1200 A under summer emergency conditions. | K12 | IL | 23.4 |  | Conceptual | 7100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3012 | 2009-12-10 |  | 5222 | 2009-09-14 | TEQ | 2017-06-01 | Brokaw | Normal, East | 1 | 138 |  | 287 | Normal East 138/34 kV Substation - Upgrade 600 A terminal equipment to minimum 1200 A SE capability in the Brokaw-Normal East 138 kV line terminal. | K9 | IL |  |  | Proposed | 100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3013 | 2009-12-10 |  | 5223 | 2009-09-14 | LN | 2017-06-01 | Turkey Hill | Cahokia | 1492 | 345 |  | 1793 | Turkey Hill-Cahokia 345 kV - Reinsulate the existing Turkey Hill-Cahokia 138 kV Line 1492 (18.8 miles) to 345 kV service. | K11 | IL | 18.8 |  | Proposed | 1000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3015 | 2009-12-10 |  | 5225 | 2009-09-14 | LN | 2018-06-01 | Grand Tower Plant | E. W. Frankfort | 1 | 345 |  | 1793 | Grand Tower-E.W. Frankfort 345 kV - New 41 mile, 345 kV, 3000 A line. 345 kV PCBs: 2-Grand Tower; 2- E.W. Frankfort | K11 | IL |  | 41 | Conceptual | 82000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3016 | 2009-12-10 |  | 5226 | 2011-09-07 | TX | 2019-11-15 | Galesburg Sub | Install 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Galesburg 345/138 kV Substation - 1-560 MVA 345/138 kV transformer, 3-345 kV PCBs for 345 kV ring bus | J9 | IL |  |  | Conceptual | 18480000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3018 | 2009-09-14 |  | 5228 | 2009-12-23 | LN | 2018-06-01 | Tazewell | Tremont Tap | 1 | 138 |  | 160 | –Meredosia-Ipava 345 kV Line – New 43 mi. double-circuit line from Meredosia to Ipava. | K9 | IL | 3 | 3 | Conceptual | 2922000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3019 | 2009-09-14 |  | 5229 | 2009-12-23 | TX | 2018-06-01 | Oglesby Substation | New 345/138 kV Xfmr | 1 | 345 | 138 | 560 | –3-Position 345 kV Ring Busses at Meredosia, Quincy, Ipava | K9 | IL |  |  | Conceptual | 6000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3021 | 2009-09-14 |  | 5231 | 2009-09-14 | LN | 2018-06-01 | Mound City | Charleston | 1 | 161 |  | 280 | Mound City-Charleston 161 kV Line - New 20 mile, 1200 A summer emergency capability line. 3-161 kV PCBs: 2-Mound City, 1-Charleston. | K12 | IL |  | 20 | Conceptual | 23000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3023 | 2009-09-14 |  | 5233 | 2009-09-14 | LN | 2018-06-01 | E. Collinsville | Porter Rd. | 1432 | 138 |  | 411 | E. Collinsville-Porter Road 138 kV Line 1432 - Reconductor 5.15 miles of 477 kcmil ACSR with conductor capable of carrying 2000 A under summer emergency conditions. | K11 | IL | 5.15 |  | Proposed | 1600000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3024 | 2010-12-06 |  | 5234 | 2009-09-15 | TX | 2015-06-01 | Bunsonville Sub | Install 2nd. 345/138 kV Xfmr |  | 345 | 138 |  | Bunsonville 345/138 kV Substation - Install 2nd. 560 MVA Transformer. | L9 | IL |  |  | Proposed | 5000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3026 | 2009-09-14 |  | 5236 | 2009-09-14 | CB | 2019-06-01 | Havana Plant | Connection to R.A.T. | 1 | 138 |  |  | Havana Plant 138 kV Switchyard - Add 138 kV Connection for new Reserve Auxiliary Transformer needed to supply new pollution control load. | K9 | IL |  |  | Conceptual | 100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3029 | 2010-12-06 | AMRN16 | 5241 | 2009-09-14 | LN | 2019-06-01 | Gibson City | Brokaw | 1 | 138 |  | 240 | Gibson City Plant 138 kV Outlet - Increase capabilty of Gibson City-Brokaw and Gibson City-Paxton 138 kV lines. | K9 | IL | 28.39 |  | Conceptual | 6750000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3030 | 2009-09-14 | AMRN16 | 5242 | 2009-09-14 | LN | 2019-06-01 | Gibson City | Paxton | 1 | 138 |  | 240 | Gibson City Plant 138 kV Outlet - Increase capabilty of Gibson City-Brokaw and Gibson City-Paxton 138 kV lines. | K9 | IL | 15.93 |  | Conceptual | 6750000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3033 | 2010-12-06 | AMRN18 | 5249 | 2009-09-14 | LN | 2019-06-01 | Dupo | Dupo Ferry | 1 | 138 |  | 411 | New Dupo-Dupo Ferry 138 kV 2000 A line. | J11 | IL |  | 0.5 | Conceptual | 1500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3033 | 2010-12-06 | AMRN18 | 5248 | 2009-09-14 | LN | 2019-06-01 | Cahokia | Dupo | 1 | 345 |  | 1793 | New 8 mi. 3000 A 345 kV line from Cahokia Substation, 2-345 kV PCBs @ Cahokia, and 138 kV Outlet to Cahokia-Meramec circuits near Lemay Taps. New Dupo-Dupo Ferry 138 kV 2000 A line. | J11 | IL |  | 8 | Conceptual | 14692000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3033 | 2010-12-06 | AMRN18 | 5247 | 2009-09-14 | SUB | 2019-06-01 | Dupo Sub | New 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Dupo Area 345/138 kV Substation - 1-560 MVA Transformer, 8-138 kV PCBs. | J11 | IL |  |  | Conceptual | 6000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3035 | 2009-09-14 |  | 5251 | 2009-09-14 | LN | 2019-06-01 | Kinmundy | Salem, West | 1 | 138 |  | 240 | Kinmundy-Salem, West 138 kV line - Increase clearances to ground. | K10 | IL | 10.33 |  | Conceptual | 1100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3036 | 2009-09-14 |  | 5252 | 2009-09-14 | TX | 2019-06-01 | Latham Sub | Install 2nd. 345/138 kV Xfmr | 2 | 345 | 138 | 448 | Latham 345/138 kV Substation - Install 2nd. 345/138 kV, 448 MVA Transformer. 1-345 kV PCB, 1-138 kV PCB. | K9 | IL |  |  | Conceptual | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3037 | 2009-09-14 |  | 5253 | 2009-09-14 | LN | 2019-06-01 | Rush Island | Dupo | 1 | 345 |  | 1793 | Rush Island-Dupo 345 kV Line - New 27 mile, 3000 A summer emergency capability line. Design for double-circuit. 2-345 kV PCBs: 1-Rush Island, 1-Dupo. | J11 | IL |  | 27 | Conceptual | 49000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3039 | 2009-09-14 |  | 5255 | 2009-09-14 | LN | 2020-06-01 | Grand Tower Plant | Joppa Plant | 1 | 345 |  | 1793 | Grand Tower-Joppa 345 kV Line - New 50 mile 345 kV, 3000 A line. 345 kV PCBs: 2-Grand Tower; 1-Joppa. | K11 | IL |  | 50 | Conceptual | 100000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3040 | 2009-09-14 |  | 5256 | 2009-09-14 | LN | 2020-06-01 | Tazewell | S. Bloomington | 1 | 345 |  | 1793 | Tazewell-South Bloomington 345 kV Line - New 35 mile, 345 kV, 3000 A line. 345 kV PCBs: 2 at Tazewell, 3 at South Bloomington switching station. | K9 | IL |  | 35 | Conceptual | 87500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3043 | 2009-09-14 |  | 5259 | 2009-09-14 | LN | 2020-06-01 | LaSalle | Oglesby | 1 | 345 |  | 1793 | LaSalle-Oglesby 345 kV Line - New 22 mi. 3000 A summer emergency capability line; 1-345 kV PCB at LaSalle, 1-138 kV PCB at Oglesby. | K9 | IL |  | 22 | Conceptual | 44000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3044 | 2009-09-14 |  | 5260 | 2009-09-14 | LN | 2021-06-01 | Roxford | Pawnee | 1 | 345 |  | 1793 | Roxford-Pawnee 345 kV Line - New 60 mile, 3000 A summer emergency capability line. 3-345 kV PCBs (1-Roxford, 2-Pawnee). Install WAMS - PMU at Pawnee on new line terminal. | K10 | IL |  | 60 | Conceptual | 120000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3175 | 2010-05-05 |  | 5606 | 2010-05-05 | LN | 2020-06-01 | Palmyra Tap | Pawnee | 1 | 765 |  | 3975 | Construct new 765 kV Line | J10 | IL |  | 117.7 | Conceptual | 347557224 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3176 | 2010-05-05 |  | 5607 | 2010-05-05 | LN | 2020-06-01 | Pawnee | Breed | 1 | 765 |  | 3975 | Construct new 765 kV Line | K10 | IL |  | 140.4 | Conceptual | 404702844 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3177 | 2010-05-05 |  | 5608 | 2010-05-05 | TX | 2020-06-01 | Pawnee | Substation |  | 765 | 345 | 2250 | Install 765/345 kV Transformer | K10 | IL |  |  | Conceptual | 28200000 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3178 | 2010-05-05 |  | 5609 | 2010-05-05 | LN | 2020-06-01 | Pawnee | Powerton | 1 | 765 |  | 3975 | Construct new 765 kV Line | K9 | IL |  | 79.2 | Conceptual | 224509670 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3182 | 2010-05-05 |  | 5613 | 2010-05-05 | LN | 2020-06-01 | St. Francois | Grand Tower | 1 | 765 |  | 3975 | Construct new 765 kV Line | J11 | MO |  | 63.4 | Conceptual | 193607736 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3183 | 2010-05-05 |  | 5614 | 2010-05-05 | TX | 2020-06-01 | Grand Tower | Substation |  | 765 | 345 | 2250 | Install 765/345 kV Transformer | K11 | IL |  |  | Conceptual | 28200000 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3184 | 2010-05-05 |  | 5615 | 2010-05-05 | LN | 2020-06-01 | Grand Tower | Rockport | 1 | 765 |  | 3975 | Construct new 765 kV Line | L11 | IL |  | 172 | Conceptual | 494506712 | Planning |  |  |  |  | y | C
C | Central | AmerenIL | 3197 | 2010-06-30 | 1 | 5652 | 2010-06-30 | TX | 2014-05-01 | Kewanee | Transformer | 1 | 161 | 138 |  | new transformer |  | IL |  |  | Proposed | 4000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3197 | 2010-06-30 | 1 | 5651 | 2011-04-22 | LN | 2017-06-01 | Oak Grove | Kewanee | 1 | 161 |  |  | new line |  | IL |  | 38 | Proposed | 57000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3198 | 2010-06-30 | 2 | 5654 | 2010-06-30 | TX | 2014-05-01 | Kewanee | Transformer | 1 | 345 | 138 |  | new transformer |  | IL |  |  | Proposed | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3198 | 2010-06-30 | 2 | 5655 | 2010-06-30 | TX | 2014-05-01 | Kewanee | Transformer | 1 | 345 | 138 |  | new transformer |  | IL |  |  | Proposed | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3198 | 2010-06-30 | 2 | 5653 | 2011-04-22 | LN | 2017-06-01 | Oak Grove | Kewanee | 1 | 345 |  |  | new line |  | IL |  | 38 | Proposed | 76000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenIL | 3336 | 2010-09-15 |  | 6201 | 2010-09-15 | LN | 2014-06-01 | Gilman | Watseka | 1 | 138 |  | 322 | Reconductor to 1600 A summer emergency capability |  | IL | 15.21 |  | Proposed | 4763000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3338 | 2010-12-06 |  | 6203 | 2010-09-15 | TX | 2013-06-01 | Lanesville |  | 1 | 345 | 138 | 560 | Replace existing transformer with a 560 MVA unit |  | IL |  |  | Proposed | 4000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3339 | 2010-09-15 |  | 6204 | 2010-09-15 | LN | 2014-06-01 | Pana, North | Taylorville, South | 1 | 138 |  | 322 | Reconductor to 1600 A summer emergency capability. Upgrade terminal equipment to match |  | IL | 12.91 |  | Proposed | 4073000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3340 | 2010-09-15 |  | 6205 | 2010-09-15 | TEQ | 2016-06-01 | Pawnee, North | Taylorville, South | 1 | 138 |  | 240 | Replace bus conductor at both terminals to 1200 A summer emergency capability |  | IL | 17.99 |  | Proposed | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3341 | 2010-09-15 |  | 6206 | 2010-09-15 | LN | 2015-06-01 | Diamond Star | West Washington Street | 1 | 138 |  | 240 | Reconductor 336 kcmil ACSR conductor to 1200 A summer emergency capability |  | IL | 1.25 |  | Proposed | 375000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3342 | 2010-09-15 |  | 6207 | 2010-09-15 | LN | 2015-06-01 | Diamond Star | McClean County Sw. Station | 1 | 138 |  | 160 | Increase ground clearance on 477 kcmil ACSR conductor |  | IL | 2.4 |  | Proposed | 240000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3343 | 2010-09-15 |  | 6208 | 2010-09-15 | LN | 2015-06-01 | Raab Rd | White Oak Tap | 1 | 138 |  | 160 | Increase ground clearance on 477 kcmil ACSR conductor |  | IL | 3.92 |  | Proposed | 400000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3344 | 2010-09-15 |  | 6209 | 2010-09-15 | LN | 2015-06-01 | El Paso Tap | Minonk Tap | 1 | 138 |  | 160 | Increase ground clearance on 477 kcmil ACSR conductor |  | IL | 13.88 |  | Proposed | 1300000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3345 | 2010-09-15 |  | 6210 | 2010-09-15 | LN | 2016-06-01 | R. S. Wallace | E. Peoria | 1 | 138 |  | 159 | Increase ground clearance on 477 kcmil ACSR |  | IL | 0.6 |  | Proposed | 60000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3346 | 2010-09-15 |  | 6211 | 2010-09-15 | LN | 2016-06-01 | Mason | Holland | 1 | 138 |  | 240 | Reconductor 795 kcmil ACSR to 1200 A summer emergency capability |  | IL | 0.05 |  | Proposed | 25000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3347 | 2010-09-15 |  | 6212 | 2010-09-15 | LN | 2016-06-01 | Mason | San Jose Rail | 1 | 138 |  | 240 | Reconductor 795 kcmil ACSR to 1200 A summer emergency capability |  | IL | 0.05 |  | Proposed | 25000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3348 | 2011-08-26 |  | 6213 | 2011-03-07 | TX | 2017-06-01 | Pawnee Sub | Install 2nd. 345/138 kV xfmr | 1 | 345 | 138 | 560 | Pawnee, West 345/138 kV Substation - Replace existing transformer with 560 MVA unit |  | IL |  |  | Proposed | 5000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3349 | 2010-09-15 |  | 6214 | 2010-09-15 | CB | 2020-06-01 | East Galesburg | Monmouth Blvd. | 1 | 138 |  | 160 | Replace breaker at East Galesburg with 1200 A breaker. Replace terminal equipment to 1200 A capability. |  | IL | 8.55 |  | Conceptual | 1000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3350 | 2010-09-15 |  | 6215 | 2010-12-06 | LN | 2012-12-01 | East Kewanee | Princeton Tap | 1 | 138 |  | 240 | Reconductor 477 kcmil ACSR conductor to 1200 A summer emergency capability. Replace terminal equipment at East Kewanee to 1200 A capability. |  | IL | 15.33 |  | Planned | 2656000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3351 | 2010-09-15 |  | 6216 | 2010-09-15 | CB | 2015-06-01 | Wood River Sub | Install 2-138 kV Bus-Tie Breakers |  | 138 |  | 478 | Install 2-2000 A, 138 kV bus-tie breakers |  | IL |  |  | Proposed | 2000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3352 | 2010-09-15 |  | 6217 | 2010-09-15 | CAP | 2013-06-01 | West Tilton Sub | Install 40 Mvar Cap Bank |  | 138 |  |  | Install 40 Mvar, 138 kV capacitor bank. |  | IL |  |  | Proposed | 1500000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3353 | 2010-09-15 |  | 6218 | 2010-09-15 | CB | 2012-06-01 | Edwards | Keystone | 1 | 138 |  | 382 | Replace 138 kV, 1200 A breaker and terminal equipment at Keystone terminal to 2000 A capability |  | IL | 3.27 |  | Proposed | 1100000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3354 | 2010-09-15 |  | 6219 | 2010-09-15 | LN | 2014-06-01 | Edwards | Caterpillar Sub 1 | 1 | 138 |  | 220 | Increase ground clearand on 795 kcmil ACSR and 927 ACAR conductor |  | IL | 9.47 |  | Proposed | 950000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3362 | 2010-09-15 |  | 6229 | 2010-09-15 | SUB | 2013-09-30 | California Ridge Switching Station | Generator connection |  | 138 |  |  | Install a 3-position ring bus to facilitate connection of wind farm (H100) to the Sidney-Rantoul Jct. 138 kV line. |  | IL |  |  | Proposed | 3240000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL | 3369 | 2010-09-15 |  | 6240 | 2010-12-06 | TEQ | 2012-06-01 | Quincy, East | Replace 138-34.5 kV Trnsformer Bank #3 |  | 138 |  | 112 | Replace 138-34.5 kV Transformer Bank #3 with a 112 MVA unit. Replace 600 A, 138 kV disconnect switch with minimum 800 A capability |  | IL |  |  | Planned | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenIL, Non-MISO | 2197 | 2008-08-05 | 34 | 4061 | 2008-08-05 | LN | 2018-08-01 | St. Francois | Rockport | 1 | 765 |  | 2904 | new line |  | MO/IL/IN |  | 186 | Conceptual | 599000000 | [5 empty] | Y | C
C | Central | AmerenIL, Non-MISO | 2215 | 2008-08-05 | 37 | 4064 | 2008-08-05 | LN | 2018-08-01 | Coffeen | Sullivan | 1 | 765 |  | 3768 | new line |  | IL/IN |  | 100 | Conceptual | 322000000 | [5 empty] | Y | C
C | Central | AmerenMO | 2122 | 2008-02-14 |  | 3977 | 2011-07-05 | LN | 2011-11-17 | Point Prairie 161-34.5 kV Sub | AECI Enon Substation | 1 | 161 |  | 280 | Extend 1 mile of line to AECI Enon Substation | J10 | MO |  | 1 | Planned | 1896500 | [5 empty] | Y | C
C | Central | AmerenMO | 2292 | 2009-12-23 |  | 4208 | 2010-12-06 | SUB | 2016-06-01 | Kelso | 345/161 kV, 336 MVA Transformer |  | 345 | 161 | 450 | Replace 345/161 kV, 336 MVA Transformer w/ 450 MVA Transformer | K11 | MO |  |  | Proposed | 6134000 | Eng |  |  |  |  | Y | C
C | Central | AmerenMO | 2296 | 2009-12-23 |  | 4212 | 2009-09-14 | TX | 2013-06-01 | Belleau 345/138 kV Substation | 2nd. 345/138 kV, 560 MVA Transformer |  | 345 | 138 | 560 | Install 2nd. 345/138 kV, 560 MVA Transformer | J10 | MO |  |  | Proposed | 8335000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenMO | 2297 | 2009-12-10 |  | 4213 | 2009-09-14 | CAP | 2013-06-01 | Belleau 345/138 kV Substation | 120 Mvar, 138 kV Capacitor Bank |  | 138 |  |  | Install 120 Mvar, 138 kV Capacitor Bank (Install as 2-60 Mvar stages) | J10 | MO |  |  | Proposed | 3071000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenMO | 2298 | 2008-08-29 |  | 4214 | 2009-09-14 | CB | 2013-06-01 | AECI's Enon 345/161 kV Substation | 2-345 kV PCB's |  | 345 |  |  | Install 2-PCB's on incoming 345 kV lines at AECI's Enon Substation | J10 | MO |  |  | Proposed | 1876000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenMO | 2975 | 2010-12-06 |  | 5176 | 2009-09-14 | SUB | 2012-12-01 | Dupo Ferry-Selma-1 | Connection to Wings Enterprises | 1 | 138 |  | 287 | Dupo Ferry-Selma-1 138 kV Line - Install 3 position 138 kV ring bus and extend 138 kV line to serve a customer substation (Wings Enterprises). 3-138 kV, 1200A PCB's | J11 | MO |  |  | Proposed | 1141000 | Engineering |  |  |  |  | Y | C
C | Central | AmerenMO | 2987 | 2009-09-14 |  | 5191 | 2009-09-14 | CAP | 2014-06-01 | Taum Sauk Plant | Install 2-30 Mvar, 138 kV Capacitor Banks |  | 138 |  | 60 | Taum Sauk 138 kV Capacitor Banks - 2-30 Mvar banks; 2-138 kV synchronous PCBs. | J11 | MO |  |  | Conceptual | 1500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 2990 | 2009-09-14 | AMRN8 | 5194 | 2009-09-14 | LN | 2014-06-01 | Conway | Tyson | 3 | 138 |  | 240 | Conway-Tyson-3 138 kV - Increase ground clearance on Tyson-Orchard Gardens sections (7 miles) | J11 | MO | 7 |  | Proposed | 350000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 2990 | 2009-09-14 | AMRN8 | 5195 | 2009-09-14 | LN | 2014-06-01 | Conway | Tyson | 4 | 138 |  | 240 | Conway-Tyson-4 138 kV - Increase ground clearance on Tyson-Orchard Gardens sections (7 miles) | J11 | MO | 7 |  | Proposed | 350000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 2991 | 2009-12-23 |  | 5196 | 2009-09-14 | TX | 2014-06-01 | Mason 345/138 kV Sub | Replace Xfmr #2 | 2 | 345 | 138 | 700 | Mason 345/138 kV Substation - Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | J11 | MO |  |  | Proposed | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 2993 | 2009-12-23 |  | 5198 | 2009-09-14 | LN | 2014-06-01 | Dupo Ferry | Buck Knob | 1 | 138 |  | 275 | Dupo Ferry-Buck Knob 138 kV Line - Replace 22 mi. of 2-300 ACSR with maximum size conductor existing towers will support. | J11 | MO | 22 |  | Proposed | 6600000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 2996 | 2009-09-14 |  | 5201 | 2009-09-14 | LN | 2015-06-01 | Montgomery | Spencer Creek | 1 | 345 |  | 1072 | Montgomery-Spencer Creek 345 kV - Increase ground clearance on 28 miles of 795 kcmil ACSR conductor and upgrade terminal equipment at Montgomery Substation. | J10 | MO | 28 |  | Proposed | 9500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 2998 | 2009-09-14 |  | 5204 | 2009-09-14 | TX | 2015-06-01 | Overton Substation | 2nd. 345/161 kV Xfmr | 2 | 345 | 161 | 450 | Overton 345/161 kV Substation - 2nd Transformer - 450 MVA; 1-161 kV PCB, 2-345 kV PCBs, 345 kV Ring Bus | I10 | MO |  |  | Conceptual | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3000 | 2009-09-14 |  | 5206 | 2009-09-14 | TX | 2015-06-01 | Miller | New 138/161 kV Xfmr | 1 | 345 | 161 | 300 | Miller 138/161 kV Substation - Install a new 300 MVA 138/161 kV transformer to convert Miller-Zion line to 161 kV operation and increase voltage support to Jefferson City, Missouri area. | J11 | MO |  |  | Proposed | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3007 | 2010-12-06 | AMRN11 | 5215 | 2009-09-14 | TX | 2016-06-01 | Camden | Install 161/138 kV Xfmr | 1 | 161 | 138 | 300 | Install 300 MVA, 161/138 kV autotransformer at Camden | I11 | MO |  |  | Proposed | 5000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3007 | 2010-12-06 | AMRN11 | 5214 | 2009-09-14 | LN | 2016-06-01 | Camden | Ullman | 1 | 138 |  | 322 | Camden-Ullman 138 kV Line - Construct 16 miles of 138 kV between Camden Substation and Ullman, with 1600 A summer emergency capability. Install 300 MVA, 161/138 kV autotransformer at Camden | I11 | MO |  | 16 | Proposed | 24000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3008 | 2009-09-14 |  | 5216 | 2009-09-14 | CAP | 2016-06-01 | Overton Sub | Install 161 kV, 90 Mvar Capacitor Bank | 1 | 161 |  | 90 | Overton 161 kV Capacitor Bank - 1-90 Mvar capacitor bank, 1-161 kV synchronous PCB, 1-161 kV reactor. | I10 | MO |  |  | Conceptual | 1500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3014 | 2009-12-10 |  | 5224 | 2009-09-14 | LN | 2018-06-01 | Cape | Joppa | 1 | 161 |  | 375 | Cape-Joppa 161 kV Line - Reconductor line (40.27 miles) to 1600 A Summer Emergency Capability. | K11 | IL | 40.27 |  | Proposed | 12100000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3020 | 2009-09-14 |  | 5230 | 2009-09-14 | TEQ | 2018-06-01 | Overton | Columbia | 1 | 161 |  | 250 | Overton-Huntsdale-Columbia 161 kV - Replace 800 A CT at Overton Terminal with 1200 A unit. | I10 | MO |  |  | Proposed | 50000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3025 | 2010-12-06 |  | 5235 | 2009-12-23 | LN | 2019-06-01 | Rivermines | N. Farmington | 2 | 138 |  | 240 | Rivermines-N. Farmington 138 kV Line - Construct a second 138 kV line. | J11 | MO |  | 5.5 | Proposed | 7500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3027 | 2009-09-14 | AMRN14 | 5237 | 2009-09-14 | TX | 2019-06-01 | Campbell Substation | Install 2nd. 345/138 kV Xfmr | 2 | 345 | 138 | 560 | Campbell 345/138 kV Substation - 2nd 560 MVA transformer; 2-345 kV PCBs (1-Campbell, 1-Roxford); 1-138 kV PCB @ Campbell. | J10 | MO |  |  | Conceptual | 6000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3028 | 2009-09-14 | AMRN15 | 5240 | 2009-09-14 | LN | 2019-06-01 | Campbell | Page | 2 | 138 |  | 411 | Campbell-Euclid-Page 138 kV Line - Rebuild 5.25 mi. double-circuit 138 kV 2000 A SE capability. 3-138 kV PCBs (2-Campbell, 1-Page). Operate Euclid 138 kV Bus-Tie normally closed. | J10 | MO | 5.25 |  | Proposed | 4250000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3028 | 2009-09-14 | AMRN15 | 5239 | 2009-09-14 | LN | 2019-06-01 | Campbell | Page | 1 | 138 |  | 411 | Campbell-Euclid-Page 138 kV Line - Rebuild 5.25 mi. double-circuit 138 kV 2000 A SE capability. 3-138 kV PCBs (2-Campbell, 1-Page). Operate Euclid 138 kV Bus-Tie normally closed. | J10 | MO | 5.25 |  | Proposed | 4250000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3028 | 2009-09-14 | AMRN14 | 5238 | 2009-09-14 | LN | 2019-06-01 | Campbell | Roxford | 1 | 345 |  | 1793 | New 12.8 mi. Roxford-Campbell 345 kV 3000 A summer emergency capability line | J10 | MO |  | 12.8 | Conceptual | 12800000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3030 | 2009-09-14 |  | 5243 | 2009-09-14 | LN | 2019-06-01 | Labadie | Mason | 3 | 345 |  | 1793 | Labadie-Mason 345 kV Line #3 - New 25 mi. 3000 A summer emergency capability line designed for double-circuit. 345 kV PCBs: 1-Labadie, 1- Mason. | J10 | MO |  | 25 | Proposed | 37500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3031 | 2009-09-14 | AMRN17 | 5245 | 2009-09-14 | TX | 2019-06-01 | Page Area Sub | Install 345/138 kV Xfmr | 2 | 345 | 138 | 560 | Page Area 345/138 kV Substation -Second of 2-560 MVA transformers. 9-138 kV PCBs: 2-transformer, 1-bus-tie, 6-line (2-Warson, 2-Page, 2-Hunter). | J10 | MO |  |  | Conceptual | 5500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3031 | 2009-09-14 | AMRN17 | 5244 | 2009-09-14 | TX | 2019-06-01 | Page Area Sub | Install 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Page Area 345/138 kV Substation - First of 2-560 MVA transformers. 9-138 kV PCBs: 2-transformer, 1-bus-tie, 6-line (2-Warson, 2-Page, 2-Hunter). | J10 | MO |  |  | Conceptual | 5500000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3032 | 2009-12-23 |  | 5246 | 2009-12-23 | LN | 2019-06-01 | Campell | Mason | 1 | 345 |  | 1793 | Campbell-Page-Mason 345 kV Line - New 16.5 mi. 3000 A summer emergency capability line, plus reutilization of 14.5 miles of existing Page-Sioux-4 at 345 kV. | J10 | MO | 14.5 | 16.5 | Proposed | 35750000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3034 | 2009-09-14 |  | 5250 | 2009-09-14 | LN | 2019-06-01 | Loose Creek | Kingdom City | 1 | 345 |  | 1793 | Loose Creek-Kingdom City 345 kV Line - New 25 mile 345 kV, 3000 A line. 2-345 kV PCBs at Loose Creek, 2-345 kV PCBs at Kingdom City.. | I10 | MO |  | 25 | Conceptual | 52000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3038 | 2009-12-23 |  | 5254 | 2009-09-14 | LN | 2019-06-01 | Loose Creek | Pleasant Hill | 1 | 345 |  | 1793 | Loose Creek-Barnett-Windsor-Pleasant Hill 345 kV Line - New 138 mile 345 kV, 3000 A line. 560 MVA, 345/161 kV transformer at Barnett Substation. 345 kV PCBs: 2 at Loose Creek, 2 at Barnett, 2 at Windsor, 2 at Pleasant Hill. | I11 | MO |  | 138 | Conceptual | 249000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3042 | 2009-09-14 |  | 5258 | 2009-09-14 | LN | 2020-06-01 | Palmyra | Fairport | 1 | 345 |  | 1793 | Palmyra-Thomas Hill-Fairport - New 122 mile 345 kV, 3000 A line. 345 kV PCBs: 2 at Palmyra, 2 at Thomas Hill, 2 at Fairport. | I10 | MO |  | 122 | Conceptual | 220000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3045 | 2009-09-14 |  | 5261 | 2009-09-14 | LN | 2021-06-01 | St. Francois | Fletcher | 1 | 345 |  | 1793 | St. Francois-Fletcher 345 kV Line - New 48 mi. 3000 A SE capability. 345 kV terminals at St. Francois & Fletcher. Install WAMS - PMU at St. Francois on new line terminal. | J11 | MO |  | 48 | Conceptual | 86000000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3171 | 2010-05-05 |  | 5602 | 2010-05-05 | LN | 2018-06-01 | West Adair | Fairport | 1 | 345 |  | 1793 | Construct new 345 kV Line | H9 | MO |  | 113.2 | Conceptual | 171818625 | Planning |  |  |  |  | y | C
C | Central | AmerenMO | 3173 | 2010-05-05 |  | 5604 | 2010-05-05 | LN | 2020-06-01 | Fairport | Palmyra Tap | 1 | 765 |  | 3975 | Construct new 765 kV Line | H9 | MO |  | 176.6 | Conceptual | 500335836 | Planning |  |  |  |  | y | C
C | Central | AmerenMO | 3174 | 2010-05-05 |  | 5605 | 2010-05-05 | TX | 2020-06-01 | Palmyra Tap | Substation |  | 765 | 345 | 2250 | Install 765/345 kV Transformer | J10 | MO |  |  | Conceptual | 28200000 | Planning |  |  |  |  | y | C
C | Central | AmerenMO | 3179 | 2010-05-05 |  | 5610 | 2010-05-05 | LN | 2020-06-01 | Palmyra Tap | Montgomery | 1 | 765 |  | 3975 | Construct new 765 kV Line | J10 | MO |  | 67.9 | Conceptual | 192436860 | Planning |  |  |  |  | y | C
C | Central | AmerenMO | 3180 | 2010-05-05 |  | 5611 | 2010-05-05 | TX | 2020-06-01 | Montgomery | Substation |  | 765 | 345 | 2250 | Install 765/345 kV Transformer | J10 | MO |  |  | Conceptual | 28200000 | Planning |  |  |  |  | y | C
C | Central | AmerenMO | 3181 | 2010-05-05 |  | 5612 | 2010-05-05 | LN | 2020-06-01 | Montgomery | St. Francois | 1 | 765 |  | 3975 | Construct new 765 kV Line | J11 | MO |  | 104.1 | Conceptual | 295069852 | Planning |  |  |  |  | y | C
C | Central | AmerenMO | 3187 | 2010-06-16 |  | 5625 | 2010-06-16 | TX | 2020-06-01 | St. Francois | Substation |  | 765 | 345 | 2250 | Install 765/345 kV Transformer | J11 | MO |  |  | Conceptual | 28200000 | Planning |  |  |  |  | Y | C
C | Central | AmerenMO | 3356 | 2010-09-15 |  | 6222 | 2010-12-06 | TEQ | 2012-12-01 | Tegeler | Osage | 1 | 138 |  | 128 | Replace 138 kV disconnect switch at Freeburg with new 1200 A switch |  | MO |  |  | Planned | 200000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3364 | 2010-12-06 | AMRN22 | 6231 | 2010-09-15 | CB | 2015-06-01 | Franklin Sub. | Install 3-1200 A breakers |  | 138 |  |  | Install 3-1200 A breakers to accommodate 138 kV supplies to Prairie Dell 138-34.5 kV Substation |  | MO |  |  | Proposed | 3000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3364 | 2010-12-06 | AMRN22 | 6235 | 2011-04-22 | LN | 2015-06-01 | Gray Summit Sub. | Prairie Dell |  | 138 |  | 240 | Install 138 kV breakers, build 3.1 miles of new double circuit 138 kV line, and connect 9.6 miles of existing 138 kV line presently operated at 34.5 kV to establish supplies to Prairie Dell Substation |  | MO | 7.1 | 3.1 | Proposed | 1550000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3364 | 2010-12-06 | AMRN22 | 6234 | 2011-04-22 | LN | 2015-06-01 | Franklin | Prairie Dell |  | 138 |  | 240 | Install 138 kV breakers, build 3.1 miles of new double circuit 138 kV line, and connect 9.6 miles of existing 138 kV line presently operated at 34.5 kV to establish supplies to Prairie Dell Substation |  | MO | 2.5 | 3.1 | Proposed | 1550000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3364 | 2010-12-06 | AMRN22 | 6233 | 2010-09-15 | CB | 2015-06-01 | Prairie Dell Sub. | Install 4-1200 A breakers |  | 138 |  |  | Install 4-1200 A breakers to accommodate 138 kV supplies to Prairie Dell 138-34.5 kV Substation |  | MO |  |  | Proposed | 4000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3364 | 2010-12-06 | AMRN22 | 6232 | 2010-09-15 | CB | 2015-06-01 | Gray Summit Sub. | Install 1-1200 A breaker |  | 138 |  |  | Install 1-1200 A breaker to accommodate 138 kV supplies to Prairie Dell 138-34.5 kV Substation |  | MO |  |  | Proposed | 1000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3365 | 2010-09-15 |  | 6236 | 2010-09-15 | CB | 2011-12-01 | Delbridge | Install 2000 A breaker and disconnect switches |  | 138 |  | 367 | Install 2000 A breaker and 2-2000 A 138 kV motor operated disconnect switches |  | MO |  |  | Proposed | 2221000 | Engineering 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3366 | 2010-12-06 |  | 6237 | 2010-09-15 | CB | 2011-12-01 | Wallen Creek | Install 1200 A breaker and disconnect switches |  | 138 |  | 240 | Install 2000 A breaker and 2-2000 A 138 kV motor operated disconnect switches |  | MO |  |  | Proposed | 2221000 | Engineering 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO | 3367 | 2010-12-06 |  | 6238 | 2010-09-15 | LN | 2013-09-01 | Pershall | Taps to Berkeley-Sioux-1 138 kV |  | 138 |  | 240 | Install 4-2000 A breaker ring bus and connect to Berkeley-Sioux-1 138 kV to establish 138 kV connections for Pershall 138-12.47 kV Sub |  | MO |  |  | Proposed | 4631000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | AmerenMO, AmerenIL | 2195 | 2008-08-05 | 12 | 4042 | 2008-08-05 | LN | 2018-08-01 | Montgomery | Coffeen | 1 | 765 |  | 3576 | new line |  | MO/IL |  | 111 | Conceptual | 343000000 | [5 empty] | Y | C
C | Central | ATC LLC | 3486 | 2011-03-01 |  | 6443 | 2011-08-24 | Line | 2021-06-01 | Bluemound | Oak Creek | 1 | 138 |  | 574 | Uprate 138 kV line to 275 F |  | WI | 40 |  | Conceptual | 1400000 | Planning |  |  |  |  | Y | C
C | Central | BREC | 3435 | 2010-11-15 | LRP1 | 6338 | 2010-11-15 | LNrc | 2017-12-31 | Rome Junction | West Owensboro | 1 | 69 |  | 72 MVA | reconductor line |  | KY | 5.8 | 0 | Proposed | 440000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3436 | 2010-11-15 | LRP2 | 6339 | 2010-11-15 | LN | 2018-12-31 | Wilson | Sacremento | 1 | 69 |  | 72 MVA | new line |  | KY | 0 | 11 | Proposed | 2100000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3437 | 2010-11-15 | LRP3 | 6340 | 2010-11-15 | LNrc | 2018-12-31 | Thruston Junction | East Owensboro | 1 | 69 |  | 67 MVA | reconductor line |  | KY | 0.4 | 0 | Proposed | 40000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3438 | 2010-11-15 | LRP4 | 6341 | 2010-11-15 | Lnrc | 2018-12-31 | Daviess County | Philpot Tap | 1 | 69 |  | 72 MVA | reconductor line |  | KY | 7.7 | 0 | Proposed | 580000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3439 | 2010-11-15 | LRP5 | 6342 | 2010-11-15 | SUB | 2022-12-31 | Ensor 161 kV | Ensor 69 kV |  | 161 | 69 | 56 MVA | new substation |  | KY |  |  | Proposed | 6200000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3440 | 2010-11-15 | LRP6 | 6343 | 2010-11-15 | TX | 2024-12-31 | Reid EHV 161 kV | Reid EHV 69 kV |  | 161 | 69 | 56 MVA | new transformer |  | KY |  |  | Proposed | 5000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3441 | 2010-11-15 | LRP7 | 6344 | 2010-11-15 | Lnrc | 2020-12-31 | Olivet Church Road | Olivet Church Road Tap | 1 | 69 |  | 72 MVA | reconductor line |  | KY | 1.4 | 0 | Proposed | 150000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3442 | 2010-11-15 | LRP8 | 6345 | 2010-11-15 | TX | 2024-12-31 | White Oak 161 kV | White Oak 69 kV |  | 161 | 69 | 56 MVA | new transformer |  | KY |  |  | Proposed | 1900000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3443 | 2010-11-15 | LRP9 | 6346 | 2010-11-15 | TX | 2017-12-31 | Hardinsburg 161 kV | Hardinsburg 69 kV |  | 161 | 69 | 100 MVA | new transformers |  | KY |  |  | Proposed | 4000000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3444 | 2010-11-15 | LRP10 | 6347 | 2010-11-15 | TX | 2020-12-31 | Meade Coutny 161 kV | Meade County 69 kV |  | 161 | 69 | 56 MVA | new transformer |  | KY |  |  | Proposed | 700000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3445 | 2010-11-15 | LRP11 | 6348 | 2010-11-15 | CAP | 2020-12-31 | Brandenburg |  | 1 | 69 |  | 6 MVAR | new capacitor |  | KY |  |  | Proposed | 300000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | BREC | 3446 | 2010-11-15 | LRP12 | 6349 | 2010-11-15 | Lnrc | 2022-12-31 | Hardinsburg No. 1 | Harned | 1 | 69 |  | 72 MVA | reconductor line |  | KY | 2 | 0 | Proposed | 170000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | DEM | 840 | 2009-09-17 | AMIN0075 | 819 | 2009-02-18 | CAP | 2016-06-01 | Rushville | Capacitor |  | 69 |  | 14.4 MVAR | Add capacitor | M10 | IN |  |  | Planned | 510845.03 | Engineering |  |  |  |  | NT | C
C | Central | DEM | 1249 | 2009-09-17 | 602G6621 | 1957 | 2009-02-18 | CAP | 2016-12-31 | Frankfort 230 | Capacitor |  | 69 |  | 36 MVAR | Install 36 MVAR 69kV capacitor |  | IN |  |  | Planned | 632358 | Engineering |  |  |  |  | NT | C
C | Central | DEM | 1264 | 2011-03-25 | 702G6714 | 1981 | 2011-03-25 | LN | 2022-06-01 | Speed |  |  | 345 | 138 | 717 | Replace existing 345/138 transformer at Speed with a new transformer rated at 3,000A or higher. |  | IN |  |  | Alternative | 7541500 | Engineering |  |  |  |  | Y | C
C | Central | DEM | 1518 | 2011-01-11 | 202D7784 | 2594 | 2011-01-11 | TX | 2016-06-01 | Curliss | transformer | 1 | 138 | 69 | 150 | Install new Curliss 138-69 kV sub in the 5884 ckt, 150 MVA xfmr, Install one 69 kV circuit. Convert Glen Este and Batavia dist subs from 34 to 69kV primary voltage. |  | OH |  | 12.18 | Proposed | 9818000 | Engr |  |  |  |  | Y | C
C | Central | DEM | 1571 | 2011-01-11 | AMIN0060 | 3123 | 2011-03-25 | LN | 2015-06-01 | IPL Rockville | Avon East | 1 | 138 |  | 306 | Construct 4.3 miles / 954ACSR of 138kv line from IPL Rockville to Avon East | M9 | IN |  | 4.3 | Alternative | 2980000 | Engineering |  |  |  |  | Y | C
C | Central | DEM | 1900 | 2009-09-17 | AMIN0220 | 3796 | 2009-06-26 | Dist | 2015-06-01 | Avon Industrial Park | new dist sub | 1 | 138 | 12 | 306 | Avon Industrial Park (aka Central Logistics) - Construct 69/138-12kV - 22.4 MVA sub and 2.6 mile - 69kV radial line from roughly the Avon South sub - unknown if this will be a 69 or 138 kv sub | M9 | IN |  | 2.6 | Proposed | 923000 | Engr |  |  |  |  | NT | C
C | Central | DEM | 1904 | 2009-01-05 | AMIN0065 | 3801 | 2009-01-05 | LNup | 2015-06-01 | Batesville | Hillenbrand | 1 | 69 |  | 53 | Uprate 69kV Batesville to Hillenbrand to 100C – 4/0acsr – 2.1 miles – 69107 ckt | M10 | IN | 2.1 |  | Planned | 115960.76 | Engineering |  |  |  |  | NT | C
C | Central | DEM | 2124 | 2009-09-17 | 804J3044 | 2909 | 2009-06-26 | LN | 2020-06-01 | Brooklyn | HE Brooklyn | 1 | 69 |  | 153 | Brooklyn Sub to HE Brooklyn Sub reconductor 1.28 miles of 6940 line 4/0 Cu with 954ACSR@100C | M10 | IN | 1.28 |  | Planned | 320000 | Planning |  |  |  |  | NT | C
C | Central | DEM | 2125 | 2009-09-17 | AMIN0084 | 2910 | 2009-06-26 | TX | 2020-06-01 | Centerton | transformer | 1 | 138 | 69 | 168 | Upgrade/replace existing 75MVA 138/69kV bank with 150MVA bank | M10 | IN |  |  | Planned | 3091000 | 2009$, Engr |  |  |  |  | NT | C
C | Central | DEM | 2129 | 2009-09-17 | 604J3046 | 2914 | 2009-06-26 | LN | 2020-06-01 | Plainfield South | HE Mooresville Jct | 1 | 69 |  | 153 | Plainfield South to HE Mooresville Jct 69kV reconductor 4/0Cu with 954ACSR 2.03 miles | M10 | IN | 2.03 |  | Planned | 980000 | 2009$, Engr |  |  |  |  | NT | C
C | Central | DEM | 2135 | 2008-04-07 | AMIN0021 | 2920 | 2008-10-01 | CAP | 2014-06-15 | Franklin 230 | capacitor |  | 69 |  | 36 MVAR | Franklin 230 Sub 69kV Cap - Install 36MVAR 69kV bus capacitor bank | M10 | IN |  |  | Planned | 400000 | Plan |  |  |  |  | NT | C
C | Central | DEM | 2139 | 2008-04-07 | 602J3054 | 2924 | 2008-04-07 | TEQ | 2016-06-30 | Greenwood West | switch |  | 69 |  | 143 | Greenwood West Sub - upgrade (or replace, if required) 69kV Loadbreak switch #2 for 1200amp capacity in the 6999 ckt. | M10 | IN |  |  | Planned | 50000 | Planning |  |  |  |  | NT | C
C | Central | DEM | 2140 | 2009-09-17 | AMIN0063 | 2925 | 2009-09-17 | LN | 2015-06-30 | Greenwood West | Lenore Jct. | 1 | 69 |  | 100 | Greenwood West to Lenore Jct reconductor 69kV - 6949 ckt. with 477ACSR @ 100C conductor | M10 | IN | 5.51 |  | Planned | 1377500 | Planning |  |  |  |  | NT | C
C | Central | DEM | 2144 | 2008-04-07 | 604J3062 | 2930 | 2008-04-07 | LN | 2015-06-30 | Franklin 230 | Earlywood | 1 | 69 |  | 143 | Franklin 230kV sub to Earlywood sub reconductor 1.06 mile - 69kV - 69165 line with 954ACSR@100C | M10 | IN | 1.06 |  | Planned | 424000 | Planning |  |  |  |  | NT | C
C | Central | DEM | 2145 | 2011-03-25 | AMIN0022 | 2932 | 2011-03-25 | TX | 2020-06-01 | Franklin 230 | Bank 2 | 2 | 230 | 69 | 239 | Replace 230/69kV bank 2 with a 200MVA LTC transformer | M10 | IN |  |  | Planned | 2400000 | Plan |  |  |  |  | Y | C
C | Central | DEM | 2145 | 2011-03-25 | AMIN0022 | 2931 | 2011-03-25 | TX | 2020-06-01 | Franklin 230 | Bank 1 | 1 | 230 | 69 | 239 | Replace 230/69kV bank 1 with a 200MVA LTC transformer | M10 | IN |  |  | Planned | 2400000 | Plan |  |  |  |  | Y | C
C | Central | DEM | 2146 | 2008-04-07 | 604J3063 | 2933 | 2008-04-07 | LN | 2015-06-30 | HE Honey Creek Jct | Frances Creek Jct | 1 | 69 |  | 143 | HE Honey Creek Jct to Frances Creek Jct. reconductor 69kV - 1.12 mile line section of the 69102 ckt. with 954ACSR 100C conductor. | M10 | IN | 1.12 |  | Planned | 420000 | Planning |  |  |  |  | NT | C
C | Central | DEM | 2147 | 2008-04-07 | 604J3060 | 2934 | 2008-04-07 | LN | 2015-06-30 | Whiteland | Madison Ave Jct | 1 | 69 |  | 143 | Whiteland Sub to Greenwood North Tap to Madison Ave Jct reconductor 3.44 mile 69kV - 6997 line with 954ACSR 100C conductor. | M10 | IN | 3.44 |  | Planned | 1376000 | Planning |  |  |  |  | NT | C
C | Central | DEM | 2247 | 2008-08-05 | 49 | 4076 | 2008-08-05 | TX | 2018-08-01 | Gwynn | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | IN |  |  | Conceptual | 20000000 | [5 empty] | Y | C
C | Central | DEM | 2328 | 2009-09-17 | 704J3100 | 4260 | 2009-02-18 | LNrc | 2015-06-01 | Speed | HE Bethany | 1 | 69 |  | 71.7 | Speed to HE Bethany 69kV - 6955 Reconductor Ph2 - Replace 1.6 miles of 4/0 ACSR with 477 ACSR (new limiter 600A switches) | M10 | IN | 1.6 |  | Planned | 480000 | 2008$, Plan |  |  |  |  | NT | C
C | Central | DEM | 2329 | 2009-09-17 | 704J3098 | 4261 | 2009-02-18 | LNrc | 2014-06-01 | Clarksville | Indiana Arsenal | 1 | 69 |  | 100 | Clarksville to Indiana Arsenal 69kv - 6955 ckt. reconductor 1.1 miles of 4/0acsr with 477ACSR at 100C (this is Phase 2 remainder of 4/0ACSR in this line section) | M10 | IN | 1.1 |  | Planned | 330000 | 2008$, Plan |  |  |  |  | NT | C
C | Central | DEM | 2330 | 2009-09-17 | AMIN0066 | 4262 | 2009-02-18 | LNrc | 2014-06-01 | New Albany | HE Georgetown | 1 | 69 |  | 100 | New Albany to HE Georgetown 69kv - 6970 ckt. Reconductor 1.24 miles of 4/0acsr with 477acsr@100C | M11 | IN | 1.24 |  | Planned | 666000 | 2008$, Engr |  |  |  |  | NT | C
C | Central | DEM | 2795 | 2009-03-10 | Pioneer LLC | 4917 | 2009-03-10 | LN | 2015-05-01 | Rockport (AEP) | Greentown (DEM) | 1 | 765 |  |  | New 765 kV line from Rockport (AEP) to Greentown (DEM) |  | IN |  | 240 | Proposed | 1000000000 | Planning |  |  |  |  | Y | C
C | Central | DEM | 2862 | 2009-09-14 | AMIN0131 | 5015 | 2009-09-14 | LNup | 2016-06-01 | Staunton | Lone Star Jct | 1 | 138 |  | 160 | Uprate Staunton to Greencastle Jct to Lonestar Jct 13802 circuit 336ACSR for 100C cond temp operation (Lone Star Jct switches may also need upgraded to 1200A) | M10 | IN | 19.98 |  | Planned | 350000 | 2009$, Plan |  |  |  |  | Y | C
C | Central | DEM | 2864 | 2009-09-17 | AMIN0144 | 5017 | 2009-09-14 | LNrc | 2020-06-01 | Centeron | Martinsville | 1 | 69 |  | 153 | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | M10 | IN | 3.7 |  | Planned | 1110000 | 2009$, Plan |  |  |  |  | NT | C
C | Central | DEM | 2868 | 2009-09-14 | X04C7993 | 5021 | 2009-09-14 | LNrc | 2014-06-01 | Fairfax | Senco Sta. 2 | 1 | 69 |  | 153 | F868 - Reconductor Fairfax to Senco - Replace 4/0 ACSR with 954 ACSR - Approx 4.6 miles | N10 | OH | 4.6 |  | Proposed | 1711992 | 2009$, Engr |  |  |  |  | NT | C
C | Central | DEM | 2873 | 2009-09-14 | AMIN0216 | 5026 | 2010-09-22 | SUB | 2018-06-01 | Danville East | new dist sub | 1 | 69 | 12 |  | Construct new Danville East substation near HRH hospital - single 22.4MVA transformer - 6945 ckt to be looped through | M9 | IN |  | 0.5 | Proposed | 500000 | 2009$, Plan |  |  |  |  | NT | C
C | Central | DEM | 3382 | 2010-10-12 | AMIN0341 | 6255 | 2010-10-12 | Dist | 2017-12-31 | Vincennes Vigo St. | convert distribution sub | 1 | 138 | 12 | 287 | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV |  | IN |  | 2.3 | Planned | 1800000 | Planning 2010$ |  |  |  |  | Y | C
C | Central | DEM, IPL | 2783 | 2010-05-08 | 4 | 3105 | 2009-08-28 | LN | 2012-05-01 | Wheatland | Bloomington | 1 | 345 |  | 1200 | new line |  | IN |  | 61 | Proposed | 105000000 | Planning |  |  |  |  | Y | C
C | Central | DEM, Non-MISO | 2213 | 2008-08-05 | 60 | 4087 | 2008-08-05 | LN | 2018-08-01 | Buffington | Ghent | 1 | 345 |  | 1000 | new line |  | KY |  | 33.2 | Conceptual | 47000000 | [5 empty] | Y | C
C | Central | IPL | 2246 | 2008-08-05 | 48 | 4075 | 2008-08-05 | TX | 2018-08-01 | Petersburg | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | IN |  |  | Conceptual | 20000000 | [5 empty] | Y | C
C | Central | IPL | 2897 | 2009-09-14 | 2052 | 5070 | 2010-01-06 | LN | 2013-06-01 | Petersburg | Hanna/Frances Creek | 1 | 345 |  | 1195 | Increase line rating from 956 to 1195 MVA |  | IN | 111.42 |  | Proposed | 2500000 | Planning |  |  |  |  | Y | C
C | Central | IPL | 2898 | 2009-09-14 | New1 | 5071 | 2010-01-06 | SUB | 2014-06-01 | Hanna | Southeast | 1 | 138 |  | 574 | Increase line rating from 287 to 574 MVA |  | IN |  |  | Proposed | 4000000 | Planning |  |  |  |  | Y | C
C | Central | IPL | 2899 | 2009-09-14 | New2 | 5072 | 2010-01-06 | LN | 2015-06-01 | Guion | Whitestown | 1 | 345 |  | 1195 | Increase line rating from 956 to 1195 MVA |  | IN | 11.14 |  | Proposed | 1000000 | Planning |  |  |  |  | Y | C
C | Central | IPL | 2901 | 2009-09-14 | 1557 | 5076 | 2009-09-14 | LN |  | Petersburg | Duke Wheatland | 1 | 345 |  | 1386 | Increase line rating from 956 to 1386 MVA |  | IN | 11.22 |  | Proposed | 4000000 | Planning |  |  |  |  | Y | C
C | Central | IPL | 2901 | 2009-09-14 | 1557 | 5075 | 2009-09-14 | CB |  | Duke Wheatland | Bus Tie Breakers |  | 345 |  |  | Closing the Wheatland bus tie breakers connects the IPL Petersburg - Duke Wheatland - AEP Breed line into the Duke Wheatland 345 kV Substation |  | IN |  |  | Proposed | 0 | Planning |  |  |  |  | Y | C
C | Central | IPL | 2901 | 2009-09-14 | 1557 | 5074 | 2009-09-14 | LN |  | Hanna/Franklin Township | HE Bloomington | 1 | 345 |  | 1195 | New |  | IN |  | 45 | Proposed | 60400000 | Planning |  |  |  |  | Y | C
C | Central | IPL | 2901 | 2009-09-14 | 1557 | 5077 | 2009-09-14 | LN |  | Duke Wheatland | AEP Breed | 1 | 345 |  | 1386 | Increase line rating from 956 to 1386 MVA |  | IN | 40.27 |  | Proposed | 6500000 | Planning |  |  |  |  | Y | C
C | Central | MEC, AmerenMo | 2194 | 2008-08-05 | 11 | 4041 | 2008-08-05 | LN | 2018-08-01 | Montgomery | Toledo | 1 | 765 |  | 2640 | new line |  | IA/MO |  | 275 | Conceptual | 871000000 | [5 empty] | Y | C
C | Central | Non-MISO | 2199 | 2008-08-05 | 9 | 4039 | 2008-08-05 | LN | 2018-08-01 | Pontiac | Dequine | 1 | 765 |  | 4368 | new line |  | IL/IN |  | 87 | Conceptual | 265000000 | [5 empty] | Y | C
C | Central | Non-MISO | 2200 | 2008-08-05 | 22 | 4050 | 2008-08-05 | LN | 2018-08-01 | Dequine | South Chicago | 1 | 765 |  | 5376 | new line |  | IN |  | 64 | Conceptual | 161000000 | [5 empty] | Y | C
C | East | ATC LLC, ITC | 2208 | 2008-08-05 | 55 | 4082 | 2011-08-24 | LN | 2018-08-01 | Livingston | Dead River | 1 | 345 |  | 488 | new line |  | MI |  | 232 | Conceptual | 329000000 | [5 empty] | Y | C
C | East | DEM, Non-MISO | 2203 | 2008-08-05 | 42 | 4069 | 2008-08-05 | LN | 2018-08-01 | Blue Creek | Greentown | 1 | 765 |  | 6000 | new line |  | IN |  | 59 | Conceptual | 191000000 | [5 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1388 | 2010-01-06 | LN | 2018-12-31 | Saratoga 120 kV | Bunce Creek 120 kV | 1 | 120 |  | 313 |  | N6 | MI | 12.5 | 0.6 | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1385 | 2010-01-06 | TX | 2018-12-31 | Saratoga 345/120 kV (sw sta provisions) | transformer |  | 345 | 120 |  |  | N6 | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1387 | 2010-01-06 | LN | 2018-12-31 | Saratoga 120 kV | Wabash 120 kV | 1 | 120 |  | 299 |  | N6 | MI | 13.6 | 0.6 | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1389 | 2010-01-06 | LN | 2018-12-31 | Saratoga 120 kV | Burns 2 120 kV | 1 | 120 |  | 313 |  | N7 | MI | 17.7 | 0.6 | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1390 | 2010-01-06 | LNup | 2018-12-31 | Saratoga 345 kV | Greenwood 345 kV | 1 | 345 |  | 2241 |  | N6 | MI | 13.4 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1391 | 2010-01-06 | LN | 2018-12-31 | Saratoga 345 kV | Greenwood 345 kV | 2 | 345 |  | 2552 |  | N6 | MI |  | 13.4 | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1392 | 2010-01-06 | LNup | 2018-12-31 | Saratoga 345 kV | Pontiac 345 kV | 1 | 345 |  | 1769 |  | N7 | MI | 42.9 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1393 | 2010-01-06 | LN | 2018-12-31 | Saratoga 345 kV | Belle River 345 | 1 | 345 |  | 2259 |  | N7 | MI | 16.5 | 4.2 | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1394 | 2010-01-06 | TX | 2018-12-31 | Saratoga 345/120 kV | transformer | 1 | 345 | 120 | 700 |  | N6 | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 694 | 2010-01-06 | ITC9 | 1386 | 2010-01-06 | LN | 2018-12-31 | Saratoga 120 kV | Robin 120 kV | 1 | 120 |  | 444 |  | N6 | MI | 23.3 | 0.6 | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 936 | 2008-12-09 | LNup | 2018-06-01 | Lulu | Monroe 3-4 | 1 | 345 |  |  | New switching station with Majestic-Lemoyne and Milan-Allen cut in. New line to Monroe 1-2 and cut Lemoyne-Lulu into Monroe 3-4 |  | MI | 15 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 3711 | 2008-12-09 | SwSta | 2018-06-01 | Lulu 345 kV | New Switching Station |  | 345 |  |  | New switching station with Majestic-Lemoyne and Milan-Allen cut in. New line to Monroe 1-2 and cut Lemoyne-Lulu into Monroe 3-4 |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 938 | 2008-12-09 | LNup | 2018-06-01 | Lulu | Allen Junction | 1 | 345 |  |  | New switching station with Majestic-Lemoyne and Milan-Allen cut in. New line to Monroe 1-2 and cut Lemoyne-Lulu into Monroe 3-4 |  | MI | 19 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 937 | 2008-12-09 | LNup | 2018-06-01 | Lulu | Lemoyne | 1 | 345 |  |  | New switching station with Majestic-Lemoyne and Milan-Allen cut in. New line to Monroe 1-2 and cut Lemoyne-Lulu into Monroe 3-4 |  | MI | 42 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 935 | 2008-12-09 | LNup | 2018-06-01 | Lulu | Milan | 1 | 345 |  |  | switching station Majestic-Lemoyne and Milan-Allen cut in. New Monroe 1-2 and Lemoyne-Lulu into Monroe 3-4 |  | MI | 16 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 934 | 2008-12-09 | LNup | 2018-06-01 | Lulu | Majestic | 1 | 345 |  |  | New switching station with Majestic-Lemoyne and Milan-Allen cut in. New line to Monroe 1-2 and cut Lemoyne-Lulu into Monroe 3-4 |  | MI | 51 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 |  | 1579 | 2008-12-09 | SwSta | 2018-06-01 | Lulu | Monroe 1-2 | 1 | 345 |  |  | New switching station with Majestic-Lemoyne and Milan-Allen cut in. New line to Monroe 1-2 and cut Lemoyne-Lulu into Monroe 3-4 |  | MI | 12.1 | 3 | Proposed | [6 empty] | Y | C
C | East | ITC | 908 | 2010-01-06 | ii | 1580 | 2010-01-06 | LN | 2018-06-01 | Lemoyne | Monroe 3-4 | 1 | 345 |  | 2000 |  |  | MI | 33.1 | 3 | Proposed | [6 empty] | Y | C
C | East | ITC | 1012 | 2008-01-10 |  | 1582 | 2008-01-10 | LN | 2014-06-01 | Wayne | Newburg | 3 | 120 |  |  | New line (un-six wire Newburg - Wayne 2) |  | MI |  | 2.8 | Proposed | [6 empty] | Y | C
C | East | ITC | 1295 | 2010-01-06 |  | 5485 | 2010-01-06 | LN | 2016-06-30 | Quaker 120 | Southfield 120 | 2 | 120 |  | 242/290 | Rebuild the existing Quaker - Drexel - Southfield 120 kV line to double circuit and build a new Quaker - Southfield 120 kV line (7.5 miles) on the common structures. |  | MI |  | 7.35 | Proposed | [6 empty] | Y | C
C | East | ITC | 1295 | 2010-01-06 |  | 2124 | 2010-01-06 | LN | 2016-06-30 | Quaker 120 | To Drexel to Southfield 120 | 1 | 120 |  | 242/290 | Rebuild the existing Quaker - Drexel - Southfield 120 kV line to double circuit and build a new Quaker - Southfield 120 kV line (7.5 miles) on the common structures. |  | MI |  | 7.35 | Proposed | [6 empty] | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2370 | 2006-10-24 | LN | 2016-12-31 | Sprague Creek 765 kV | Bridgewater 765 kV | 1 | 765 |  | 4465 | 50 miles of new 765 kV line and new 765 kV Bridgewater Station | N7 | MI |  | 50 | Proposed | 225000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2375 | 2006-10-24 | LN | 2016-12-31 | Bridgewater 345 kV | Majestic 345 kV | 1 | 345 |  | 1828 | Taps the majestic end of the Allen Junction-Maj-Monroe 3 ender | N7 | MI |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2374 | 2006-10-24 | LN | 2016-12-31 | Bridgewater 765 kV | South Canton 765 kV | 1 | 765 |  | 4465 | 170 miles of new 765 kV line | N8 | MI/OH |  | 170 | Proposed | 600000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2373 | 2006-10-24 | LN | 2016-12-31 | Site A 765 kV | Marysville 765 kV | 1 | 765 |  | 4465 | Taps Current Marysville-Dumont 765 kV line | N8 | IN/OH |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2371 | 2006-10-24 | LN | 2016-12-31 | Bridgewater 765 kV | Site A 765 kV | 1 | 765 |  | 4465 | 135 miles of new 765 kV line and new 765 kV Site A Station | N8 | IN/OH |  | 135 | Proposed | 530000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2369 | 2006-10-24 | LN | 2016-12-31 | Sprague Creek 765 kV | Denver 765 kV | 1 | 765 |  | 4465 | 100 miles of new 765 kV line and new 765 kV Sprague Creek Station | N7 | MI |  | 100 | Proposed | 400000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2368 | 2006-10-24 | LN | 2016-12-31 | Kenowa 765 kV | Denver 765 | 1 | 765 |  | 4465 | 30 miles of new 765 kV line and new 765 kV Denver Station | M6 | MI |  | 30 | Proposed | 150000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2367 | 2006-10-24 | LN | 2016-12-31 | Cook 765 kV | Kenowa 765 kV | 1 | 765 |  | 4465 | 100 miles of new 765 kV line and new 765 kV Kenowa Station | M7 | MI |  | 100 | Proposed | 400000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2376 | 2006-10-24 | LN | 2016-12-31 | Bridgewater 345 kV | Majestic 345 kV | 2 | 345 |  | 1828 | Taps the Majestic-Milan 345 kV Circuit | N7 | MI |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2384 | 2006-10-24 | SUB | 2016-12-31 | Bridgewater 765/345 kV | transformer | 2 | 765 | 345 | 3040 | New 765/345 kV Xfmr at Bridgewater | N7 | MI |  |  | Proposed | 25000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2372 | 2006-10-24 | LN | 2016-12-31 | Site A 765 kV | Dumont 765 kV | 1 | 765 |  | 4465 | Taps Current Marysville-Dumont 765 kV line | M8 | IN/OH |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2377 | 2006-10-24 | LN | 2016-12-31 | Bridgewater 345 kV | Milan 345 kV | 1 | 345 |  | 1828 | Taps the Majestic-Milan 345 kV Circuit | N7 | MI |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2383 | 2006-10-24 | SUB | 2016-12-31 | Bridgewater 765/345 kV | transformer | 1 | 765 | 345 | 3040 | New 765/345 kV Xfmr at Bridgewater | N7 | MI |  |  | Proposed | 25000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2382 | 2006-10-24 | SUB | 2016-12-31 | Sprague Creek 765/345 kV | transformer | 1 | 765 | 345 | 3040 | New 765/345 kV Xfmr at Sprague Creek | N7 | MI |  |  | Proposed | 25000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2381 | 2006-10-24 | SUB | 2016-12-31 | Denver 765/138 kV | transformer | 1 | 765 | 138 | 1119 | New 765/138 kV Xfmr at Denver | M6 | MI |  |  | Proposed | 25000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2378 | 2006-10-24 | LN | 2016-12-31 | Sprague Creek 345 kV | Blackfoot 345 kV | 1 | 345 |  | 795 | Taps the Blackfoot-Madrid 345 kV Circuit | N7 | MI |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2379 | 2006-10-24 | LN | 2016-12-31 | Sprague Creek 345 kV | Madrid 345 kV | 1 | 345 |  | 795 | Taps the Blackfoot-Madrid 345 kV Circuit | N7 | MI |  |  | Proposed | 10000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1382 | 2006-10-24 | The 765 | 2380 | 2006-10-24 | SUB | 2016-12-31 | Kenowa 765/354 kV | transformer | 1 | 765 | 345 | 3040 | New 765/345 kV Xfmr at Kenowa | M7 | MI |  |  | Proposed | 25000000 | Planning unit cost |  |  |  |  | Y | C
C | East | ITC | 1550 | 2008-12-09 | ITC32 | 2639 | 2008-12-09 | LNup | 2015-05-31 | Hager 120 kV | Sunset 120 kV | 1 | 120 |  | 351 | Transpose line entrance with the Sunset-Southfield 120 kV circuit | N7 | MI | 0.1 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 1854 | 2010-01-06 |  | 3740 | 2008-01-10 | TEQ | 2018-06-01 | Riverview | Ironton | 1 | 120 |  |  | Replace Wave Trap |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 1854 | 2010-01-06 |  | 3739 | 2010-01-06 | LN | 2018-06-01 | Trenton Channel | Jefferson | 1 | 120 |  |  | reconductor/rebuild line |  | MI |  | 2.2 | Proposed | [6 empty] | Y | C
C | East | ITC | 1854 | 2010-01-06 |  | 3738 | 2008-01-10 | LN | 2018-06-01 | Trenton Channel | Jefferson | 1 | 120 |  |  | New Line (existing ROW) |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 1858 | 2008-01-10 |  | 3747 | 2009-12-01 | LN | 2013-06-01 | Wayne 345 kV | Substation Equipment |  | 345 |  |  | replace overloaded station equipment |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 2205 | 2008-08-05 | 15 | 4045 | 2008-08-05 | LN | 2018-08-01 | Evans | Spreague | 1 | 765 |  | 4008 | new line |  | MI |  | 95 | Conceptual | 304000000 | [5 empty] | Y | C
C | East | ITC | 2206 | 2008-08-05 | 19 | 4048 | 2008-08-05 | TX | 2018-08-01 | Spreague | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | MI |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | East | ITC | 2206 | 2008-08-05 | 17 | 4046 | 2008-08-05 | LN | 2018-08-01 | Spreague | Bridgewater | 1 | 765 |  | 6000 | new line |  | MI |  | 42 | Conceptual | 120000000 | [5 empty] | Y | C
C | East | ITC | 2933 | 2009-09-14 |  | 5105 | 2009-12-01 | LN | 2013-06-01 | Superior | Wayne | 1 | 120 |  |  | Rebuild the 10.5 miles of the Superior to Wayne 120 kV circuit from 477 ACSR to 954 ACSR on new structures. |  | MI | 10.5 |  | Proposed | 8800000 | [5 empty] | Y | C
C | East | ITC | 3129 | 2010-01-06 |  | 5505 | 2010-01-06 | LN | 2017-06-01 | Belle River | Bunce Creek 230 kV | 1 | 230 |  |  | Construct 13.5 miles 954 ACSR 138 kV circuit from Belle River to Bunce Creek |  | MI |  | 13.5 | Proposed | [6 empty] | Y | C
C | East | ITC | 3129 | 2010-01-06 |  | 5504 | 2010-01-06 | TX | 2017-06-01 | Belle River | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 3130 | 2010-01-06 |  | 5506 | 2010-01-06 | CAP | 2013-06-01 | Stratford | Stratford-New Capacitor |  | 120 |  | 50 Mvar | New 50 Mvar Capacitor |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 3130 | 2010-01-06 |  | 5507 | 2010-01-06 | CAP | 2013-06-01 | Wabash | Wabash-New Capacitor |  | 120 |  | 50 Mvar | New 50 Mvar Capacitor |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 3140 | 2010-01-06 |  | 5518 | 2010-01-06 | LN | 2017-06-01 | Belle River | St. Clair | 2 | 345 |  |  | Construct 1.12 miles 345 kV circuit from Belle River to St. Clair |  | MI |  | 1.12 | Proposed | [6 empty] | Y | C
C | East | ITC | 3141 | 2010-01-06 |  | 5519 | 2010-01-06 | LN | 2014-06-01 | Redrun | Chestnut | 2 | 120 |  |  | Construct 5 miles 120 kV circuit from Redrun to Chestnut |  | MI |  | 5 | Proposed | [6 empty] | Y | C
C | East | ITC | 3142 | 2010-01-06 |  | 5520 | 2010-01-06 | LN | 2016-06-01 | L-N-NW | Lincoln | 1 | 120 |  |  | Rebuild the section L-N-NW - Lincoln of the Lincoln-Northeast-Northwest 120 kV circuit to 954 ACSR conductor. |  | MI | 2.95 |  | Proposed | [6 empty] | Y | C
C | East | ITC | 3147 | 2010-01-06 |  | 5527 | 2010-01-06 | CAP | 2013-06-01 | Phoenix | New Capacitor |  | 120 |  | 75 Mvar | New 75 Mvar Capacitor |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 3148 | 2010-01-06 |  | 5528 | 2010-01-06 | TEQ | 2013-06-01 | Riverview | Ironton | 1 | 120 |  |  | Replace Wave Trap at Riverview |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | ITC | 3496 | 2011-03-28 |  | 6456 | 2011-03-28 |  | 2012-12-31 | NERC Alert Facility Ratings for 2012 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | [6 empty] | Y | C
C | East | ITC | 3497 | 2011-03-28 |  | 6457 | 2011-03-28 |  | 2013-12-31 | NERC Alert Facility Ratings for 2013 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | [6 empty] | Y | C
C | East | ITC | 3498 | 2011-03-28 |  | 6458 | 2011-03-28 |  | 2014-12-31 | NERC Alert Facility Ratings for 2014 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | [6 empty] | Y | C
C | East | ITC, Non-MISO | 2204 | 2008-08-05 | 40 | 4067 | 2008-08-05 | LN | 2018-08-01 | Cook | Evans | 1 | 765 |  | 4008 | new line |  | MI |  | 99 | Conceptual | 299000000 | [5 empty] | Y | C
C | East | ITC, Non-MISO | 2204 | 2008-08-05 | 43 | 4070 | 2008-08-05 | TX | 2018-08-01 | Evans | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | MI |  |  | Conceptual | 20000000 | [5 empty] | Y | C
C | East | ITC, Non-MISO | 2207 | 2008-08-05 | 18 | 4047 | 2008-08-05 | LN | 2018-08-01 | Bridgewater | Blue Creek | 1 | 765 |  | 3288 | new line |  | MI |  | 134 | Conceptual | 432000000 | [5 empty] | Y | C
C | East | ITC, Non-MISO | 2207 | 2008-08-05 | 20 | 4049 | 2008-08-05 | TX | 2018-08-01 | Bridgewater | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | MI |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | East | ITC, Non-MISO | 2209 | 2008-08-05 | 41 | 4068 | 2008-08-05 | LN | 2018-08-01 | Bridgewater | South Canton | 1 | 765 |  | 3024 | new line |  | MI/OH |  | 167 | Conceptual | 538000000 | [5 empty] | Y | C
C | East | ITCM, AmerenIL | 2785 | 2009-04-23 | 6 | 4895 | 2010-05-08 | TEQ | 2014-05-01 | Sorenson | +/- 800KV DC converter station | 1 | 800 |  | 6400 | new +/- 800KV DC converter station |  | IN |  |  | Proposed | 1900500000 | Planning |  |  |  |  | Y | C
C | East | METC | 642 | 2005-07-27 | 57 | 1325 | 2006-07-05 | LNup | 2017-06-01 | Argenta | Hazelwood(Sag) | 1 | 138 |  |  | conductor sag | M7 | MI | 0.1 |  | Proposed | 50000 | [5 empty] | Y | C
C | East | METC | 987 | 2005-07-27 | 118 | 1550 | 2005-07-27 | LN | 2013-06-01 | Emmet | Stover | 1 | 138 |  |  |  |  | MI |  |  | Proposed | 10250000 | [5 empty] | Y | C
C | East | METC | 1432 | 2010-01-06 | 180 | 2436 | 2010-01-06 | LN | 2015-06-01 | Withey Lake 138kV | Twining 138kV |  | 138 |  |  | Rebuild 0.2 miles of Withey Lake-Twining 138kV line |  | MI |  |  | Proposed | 100000 | [5 empty] | Y | C
C | East | METC | 1573 | 2008-10-01 | 198 | 3125 | 2007-07-16 | CAP | 2011-06-01 | Donaldson Creek | Donaldson Creek-New Capacitor |  | 138 |  | 23.3 Mvar | New 23.3 Mvar Capacitor |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1657 | 2007-10-26 |  | 2852 | 2007-10-26 | TEQ |  | Terminal Equipment Upgrade | [5 empty] | throughout system |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1795 | 2008-01-10 |  | 3604 | 2009-12-01 | LNup | 2012-06-01 | David Jct. | Bingham | 1 | 138 |  |  | reconductor (removes sag limits) |  | MI | 19 |  | Proposed | 11700000 | [5 empty] | Y | C
C | East | METC | 1800 | 2008-01-10 |  | 3611 | 2010-01-06 | LNup | 2013-06-01 | Argenta | Riverview | 1 | 138 |  |  | Remove sag limits |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1800 | 2008-01-10 |  | 3613 | 2008-01-10 | CB | 2013-06-01 | Riverview 138 kV | Substation Equipment |  | 138 |  |  | upgdrade CT, breaker, and switch |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1800 | 2008-01-10 |  | 3612 | 2008-01-10 | TEQ | 2013-06-01 | Argenta 138 kV | Substation Equipment |  | 138 |  |  | upgrade CT |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1804 | 2010-01-06 |  | 3620 | 2010-01-06 | TEQ | 2013-06-01 | Marquette | Substation Equipment |  | 138 |  |  | upgrade station equipment (relaying at Marquette) |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1805 | 2010-01-06 |  | 3622 | 2010-01-06 | LN | 2015-06-01 | Livingston | Emmet | 2 | 138 |  |  | new line (existing ROW) |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1805 | 2010-01-06 |  | 3624 | 2010-01-06 | LN | 2015-06-01 | Emmet | Oden | 2 | 138 |  |  | new line (existing ROW) |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1805 | 2010-01-06 |  | 3621 | 2010-01-06 | LNrc | 2015-06-01 | Livingston | Emmet | 1 | 138 |  |  | Rebuild |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1805 | 2010-01-06 |  | 3623 | 2010-01-06 | LNrc | 2015-06-01 | Emmet | Oden | 1 | 138 |  |  | Rebuild |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1807 | 2010-01-06 |  | 3626 | 2010-01-06 | LN | 2016-06-01 | Bullock | Murphy | 1 | 138 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1807 | 2010-01-06 |  | 3627 | 2008-01-10 | LN | 2016-06-01 | Begole | Richland | 1 | 138 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1807 | 2010-01-06 |  | 3628 | 2008-01-10 | LN | 2016-06-01 | Gleaner | Tittabawassee | 1 | 138 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1807 | 2010-01-06 |  | 3630 | 2008-01-10 | TX | 2016-06-01 | Bullock 230/138 kV | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1807 | 2010-01-06 |  | 3629 | 2010-01-06 | TX | 2016-06-01 | Murphy | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1808 | 2008-01-10 |  | 3631 | 2008-01-10 | LNrc | 2017-06-01 | Cowan Lake Jct | Four Mile | 1 | 138 |  |  | reconductor |  | MI | 15.5 |  | Proposed | [6 empty] | Y | C
C | East | METC | 1811 | 2008-01-10 |  | 3635 | 2008-01-10 | LN | 2018-06-01 | Gray Rd | Keystone | 1 | 138 |  |  | new line (existing WPC ROW) |  | MI |  | 9 | Proposed | [6 empty] | Y | C
C | East | METC | 1816 | 2010-01-06 |  | 3650 | 2010-01-06 | LNrc | 2014-06-01 | Mecosta | Croton | 1 | 138 |  |  | Rebuild 22 miles from Croton to Nineteen Mile (230 kV construction, operate at 138 kV) |  | MI | 22 |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5499 | 2010-01-06 | LN | 2019-06-01 | Mio | Twining | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 58.65 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5500 | 2010-01-06 | LN | 2019-06-01 | Mio | Livingston | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 41.85 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3683 | 2010-01-06 | LN | 2019-06-01 | Tippy | Sunoco Dr. | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 67.41 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3679 | 2010-01-06 | LN | 2019-06-01 | Crane Road | Hampton | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3680 | 2010-01-06 | LN | 2019-06-01 | Crane Road | Tittabawassee | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3681 | 2010-01-06 | TX | 2019-06-01 | Keystone | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3682 | 2010-01-06 | TX | 2019-06-01 | Livingston | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5501 | 2010-01-06 | LN | 2019-06-01 | Tippy | Keystone | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 36.79 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5498 | 2010-01-06 | LN | 2019-06-01 | Crane Road | Twining | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 49.35 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5497 | 2010-01-06 | LN | 2019-06-01 | Ludington | Sunoco Dr. | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5496 | 2010-01-06 | LN | 2019-06-01 | Kenowa | Sunoco Dr. | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5495 | 2010-01-06 | LN | 2019-06-01 | Mio | Livingston | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5494 | 2010-01-06 | LN | 2019-06-01 | Gallagher | Mio | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5493 | 2010-01-06 | LN | 2019-06-01 | Crane Road | Tittabawassee | 2 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5492 | 2010-01-06 | LN | 2019-06-01 | Crane Road | Manning | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5491 | 2010-01-06 | TX | 2019-06-01 | Tippy | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5489 | 2010-01-06 | TX | 2019-06-01 | Plum | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3684 | 2010-01-06 | TX | 2019-06-01 | Livingston | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5486 | 2010-01-06 | TX | 2019-06-01 | Mio | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5490 | 2010-01-06 | TX | 2019-06-01 | Keystone | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5487 | 2010-01-06 | TX | 2019-06-01 | Sunoco Dr. | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3685 | 2010-01-06 | LN | 2019-06-01 | Plum | Keystone | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 23.03 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3686 | 2010-01-06 | TX | 2019-06-01 | Twining | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3687 | 2010-01-06 | LN | 2019-06-01 | Livingston | Plum | 1 | 230 |  |  | New line (existing ROW) |  | MI |  | 30.7 | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3688 | 2010-01-06 | TX | 2019-06-01 | Crane Road | Transformer | 1 | 345 | 230 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 3689 | 2010-01-06 | LN | 2019-06-01 | Gallagher | Tittabawassee | 1 | 345 |  |  | new line resulting from line re-configuration |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 1831 | 2010-01-06 |  | 5488 | 2010-01-06 | TX | 2019-06-01 | Mio | Transformer | 1 | 230 | 138 |  | New Transformer |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 2490 | 2010-01-06 |  | 4487 | 2009-06-26 | TEQ | 2013-06-01 | Vergennes |  |  | 138 |  |  | Terminal equipment upgrade |  | MI |  |  | Proposed | 275000 | [5 empty] | Y | C
C | East | METC | 2490 | 2010-01-06 |  | 4486 | 2009-06-26 | TEQ | 2013-06-01 | North Belding |  |  | 138 |  |  | Terminal equipment upgrade |  | MI |  |  | Proposed | 275000 | [5 empty] | Y | C
C | East | METC | 2810 | 2009-06-26 |  | 4941 | 2009-06-26 | LNrc | 2014-06-01 | Delhi | Canal Jct | 1 | 138 |  |  | Rebuild 7.5 miles of 138kV line to 954 ACSR |  | MI | 18.7 |  | Proposed | 5500000 | [5 empty] | Y | C
C | East | METC | 2811 | 2010-10-20 |  | 4942 | 2010-10-20 | LNrb | 2015-06-01 | Karn | Cottage Grove | 1 | 138 |  |  | Rebuild 56miles of 138kV to 954 ACSR. |  | MI | 56 |  | Proposed | 51000000 | [5 empty] | Y | C
C | East | METC | 3103 | 2009-08-28 |  | 5436 | 2009-08-28 | CB | 2014-12-31 | Gallagher | breaker |  | 345 |  |  | new breaker |  | MI |  |  | Proposed | 2500000 | [5 empty] | Y | C
C | East | METC | 3103 | 2009-08-28 |  | 5435 | 2009-08-28 | CB | 2014-12-31 | Gallagher | breaker |  | 345 |  |  | new breaker |  | MI |  |  | Proposed | 2500000 | [5 empty] | Y | C
C | East | METC | 3128 | 2010-01-06 |  | 5502 | 2010-01-06 | LN | 2015-06-01 | Emmet | Riggsville | 1 | 138 |  |  | Construct a new 138 kV 954 ACSR circuit from Emmet to Riggsville |  | MI |  | 25 | Proposed | [6 empty] | Y | C
C | East | METC | 3128 | 2010-01-06 |  | 5503 | 2010-01-06 | LN | 2015-06-01 | Livingston | Riggsville | 2 | 138 |  |  | Install Livingston to Riggsville 138 kV circuit #2 utilize 954 ACSR conductor |  | MI |  | 25 | Proposed | [6 empty] | Y | C
C | East | METC | 3131 | 2010-01-06 |  | 5508 | 2010-01-06 | LN | 2015-06-01 | Bil-Mar Jct. | Port Sheldon Jct. | 1 | 138 |  |  | Improve sag clearance |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3132 | 2010-01-06 |  | 5509 | 2010-01-06 | LN | 2015-06-01 | Tallmadge | Tyler | 1 | 138 |  |  | Improve sag clearance |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3133 | 2010-01-06 |  | 5510 | 2010-01-06 | LN | 2014-06-01 | Claremont | Cornell | 1 | 138 |  |  | Rebuild/Reconductor the Bell Rd to N. Corunna and the Cornell to N. Corunna sections of 115 CU to 954 ACSR conductor. |  | MI | 4.34 |  | Proposed | [6 empty] | Y | C
C | East | METC | 3134 | 2010-01-06 |  | 5511 | 2010-01-06 | TEQ | 2012-06-01 | Weadock | Disconnect Switch |  | 138 |  |  | Replace a disconnect switch at Weadock. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3135 | 2010-01-06 |  | 5512 | 2010-01-06 | LN | 2016-06-01 | Airport | Alpena | 1 | 138 |  |  | Rebuild the existing Airport - Alpena circuit on DCT's to 954 ACSR conductor. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3135 | 2010-01-06 |  | 5513 | 2010-01-06 | LN | 2016-06-01 | Airport | Alpena | 2 | 138 |  |  | Install a second circuit from Airport to Alpena utilize the 954 ACSR conductor. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3136 | 2010-01-06 |  | 5514 | 2010-01-06 | LN | 2017-06-01 | Alpena | Iosco | 1 | 138 |  |  | Rebuild 20 miles from Alpena to Spruce Rd to 954 ACSR conductor and replace limiting station equipment |  | MI | 20 |  | Proposed | [6 empty] | Y | C
C | East | METC | 3137 | 2010-01-06 |  | 5515 | 2010-01-06 | LN | 2014-06-01 | Bard Road | Warren | 1 | 138 |  |  | Rebuild 20 miles from Bard Road to Warren to 954 ACSR conductor |  | MI | 20 |  | Proposed | [6 empty] | Y | C
C | East | METC | 3138 | 2010-01-06 |  | 5516 | 2010-01-06 | TEQ | 2014-06-01 | Mio | Gaylord | 1 | 138 |  |  | Replace terminal equipment at Mio |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3143 | 2010-01-06 |  | 5521 | 2010-01-06 | LN | 2019-06-01 | Northwest | Southfield | 1 | 120 |  |  | Rebuild the Northwest - Southfield circuit to 1431 ACSR conductor. |  | MI | 0.13 |  | Proposed | [6 empty] | Y | C
C | East | METC | 3144 | 2010-01-06 |  | 5522 | 2010-01-06 | TEQ | 2013-06-01 | Argenta | Morrow | 1 | 138 |  |  | Replace terminal equipment at Morrow |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3145 | 2010-01-06 |  | 5525 | 2010-01-06 | TEQ | 2014-06-01 | Blackstone | Leoni | 3 | 138 |  |  | Replace the 636 ACSR trainers at Blackstone substation. Upgrade the relaying at Leoni and Blackstone. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3145 | 2010-01-06 |  | 5524 | 2010-01-06 | TEQ | 2014-06-01 | Blackstone | Leoni | 2 | 138 |  |  | Replace the 636 ACSR trainers at Blackstone substation. Upgrade the relaying at Leoni and Blackstone. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3145 | 2010-01-06 |  | 5523 | 2010-01-06 | TEQ | 2014-06-01 | Blackstone | Leoni | 1 | 138 |  |  | Replace the 636 ACSR trainers at Blackstone substation. Upgrade the relaying at Leoni and Blackstone. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3146 | 2010-01-06 |  | 5526 | 2010-01-06 | TEQ | 2013-06-01 | Battle Creek | Verona | 2 | 138 |  |  | Replace the 795 ACSR trainer at Verona. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3149 | 2010-01-06 |  | 5529 | 2010-01-06 | TEQ | 2013-06-01 | Four Mile | Trainer |  | 138 |  |  | Replace the 2-4/0 Cu trainer at Four Mile. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3150 | 2010-01-06 |  | 5530 | 2010-01-06 | TEQ | 2014-06-01 | North Belding | Bricker | 1 | 138 |  |  | Replace the 336.4 ACSR trainer at North Belding. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3151 | 2010-01-06 |  | 5531 | 2010-01-06 | TEQ | 2014-06-01 | Spaulding | Pettis Jct. | 1 | 138 |  |  | Replace the 795 ACSR trainer at Spaulding. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3152 | 2010-01-06 |  | 5532 | 2010-01-06 | TEQ | 2016-06-01 | Riggsville | McGulpin | 1 | 138 |  |  | Replace 266.8 ACSR trainer at McGulpin and 336.4 ACSR trainer at Riggsville. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3153 | 2010-01-06 |  | 5533 | 2010-01-06 | TEQ | 2016-06-01 | Oden | Riggsville | 1 | 138 |  |  | Replace 336.4 ACSR trainer at McGulpin. |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3300 | 2010-10-20 |  | 3619 | 2011-03-28 | LNrc | 2015-06-01 | Stover | Livingston | 1 | 138 |  |  | Rebuild (230 kV construction, operate at 138 kV) |  | MI |  |  | Proposed | [6 empty] | Y | C
C | East | METC | 3492 | 2011-03-28 |  | 6452 | 2011-03-28 |  | 2012-12-31 | NERC Alert Facility Ratings for 2012 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | [6 empty] | Y | C
C | East | METC | 3493 | 2011-03-28 |  | 6453 | 2011-03-28 |  | 2013-12-31 | NERC Alert Facility Ratings for 2013 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | [6 empty] | Y | C
C | East | METC | 3494 | 2011-03-28 |  | 6454 | 2011-03-28 |  | 2014-12-31 | NERC Alert Facility Ratings for 2014 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | MI |  |  | Planned | [6 empty] | Y | C
C | East | MPPA | 2079 | 2009-09-14 | 17-4 | 3952 | 2009-09-14 | BUS | 2015-07-01 | South Airport Junction | Switches |  | 69 |  | 1200 Amps | Upgrade switches from 600A to 1200A |  | MI |  |  | Planned | 200000 | [5 empty] | Y | C
C | East | MPPA | 2080 | 2009-09-14 | 17-5 | 3953 | 2009-09-14 | BUS | 2019-07-01 | Barlow Junction | Switches |  | 69 |  | 1200 Amps | Upgrade switches from 600A to 1200A |  | MI |  |  | Planned | 200000 | [5 empty] | Y | C
C | East | MPPA | 2081 | 2009-09-14 | 17-6 | 3954 | 2009-09-14 | BUS | 2019-07-01 | Cass Road Junction | Switches |  | 69 |  | 1200 Amps | Upgrade switches from 600A to 1200A |  | MI |  |  | Planned | 200000 | [5 empty] | Y | C
C | East | NIPS | 1973 | 2010-04-04 | X7L6803 | 2763 | 2010-04-04 | LNup | 2017-12-01 | Leesburg | Northeast | 1 | 138 |  | 287 | Upgrade Connections and Circuit |  | IN | 8.5 |  | Conceptual | 5279000 | [5 empty] | Y | C
C | East | NIPS | 1979 | 2009-09-14 | 71C6817 | 2769 | 2010-09-15 | CAP | 2014-12-01 | Maple | Capacitor |  | 69 |  |  | Add two steps of 8.1 MVAR capacitors on the Maple Substation 69 kV bus. |  | IN |  |  | Conceptual | 1080000 | Engineering |  |  |  |  | Y | C
C | East | NIPS | 1980 | 2009-09-14 | 71C7203 | 2770 | 2010-09-15 | CAP | 2013-12-01 | Babcock | Capacitor |  | 69 |  |  | Add 2 to 3 - 9 .0 MVAR stages |  | IN |  |  | Conceptual | 1052000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1981 | 2009-09-14 | 71C7204 | 2771 | 2009-09-14 | CAP | 2013-12-01 | Kreitzburg | Capacitor |  | 69 |  |  | Add 2 to 3 - 9 .0 MVAR stages |  | IN |  |  | Proposed | 1052000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1983 | 2009-09-14 | 71C7206 | 2773 | 2009-09-14 | TX | 2016-12-01 | Dekalb | Transformer | 1 | 138 | 69 | 112 | Upgrade 138-69 Transformer |  | IN |  |  | Conceptual | 1700000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1984 | 2010-04-04 | 71C7209 | 2774 | 2010-04-04 | Sub | 2017-12-01 | South Knox | 138/69 kV Substation |  | 138 | 69 |  | New Substation |  | IN |  |  | Conceptual | 12568000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1985 | 2010-09-15 | 9320340 | 2775 | 2010-09-15 | LNup | 2017-12-01 | Wolcottville | South Milford | 1 | 69 |  | 81 | Circuit 6959 - Reconductor 2/0 CU to 336.4kcm ACSR |  | IN | 5.4 |  | Conceptual | 1671000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1989 | 2010-09-15 | 9325469 | 2779 | 2010-09-15 | LN | 2017-12-01 | South Milford | Helmer | 1 | 69 |  | 81 | Circuit 6959 - Reconductor 2/0 CU to 336.4kcm ACSR |  | IN | 4.7 |  | Conceptual | 1037000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1990 | 2010-09-15 | 9325471 | 2780 | 2010-09-15 | LN | 2016-12-01 | Dekalb | Angola | 1 | 69 |  | 81 | Circuit 6986 - Reconductor 2/0 CU to 336.4kcm ACSR |  | IN | 16.5 |  | Conceptual | 9253000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1993 | 2009-09-14 | 9325543 | 2783 | 2009-09-14 | Sub | 2017-12-01 | South Valparaiso | 138/69 kV Substation | 1 | 138 | 69 | 168 | New 138/69 kV Substation |  | IN |  |  | Conceptual | 4917000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 1994 | 2009-09-14 | 9326151 | 2784 | 2010-09-15 | LNrc | 2011-12-01 | Midway | Bristol | 1 | 69 |  | 81 | Circuit 6977 - Reconductor 2/0 ACSR to 336.4kcm ACSR |  | IN | 4.1 |  | Planned | 656000 | Engineering |  |  |  |  | Y | C
C | East | NIPS | 1998 | 2009-09-14 | X7L6606 | 2788 | 2010-09-15 | LNrb | 2013-12-01 | East Winamac | Lawton | 1 | 69 |  |  | Rebuild old pole line. Ckts 6962 & 6937 |  | IN | 4.5 |  | Proposed | 1339000 | Engineering |  |  |  |  | Y | C
C | East | NIPS | 2000 | 2009-09-14 | X7L6802 | 2790 | 2010-09-15 | LNrc | 2014-12-01 | Goshen Junction | Model Tap | 1 | 69 |  | 81 | Circuit 6977 - Reconductor 4/0 ACSR to 336.4kcm ACSR |  | IN | 0.5 |  | Planned | 52000 | Engineering |  |  |  |  | Y | C
C | East | NIPS | 2003 | 2009-09-14 | X7L6811 | 2793 | 2010-09-15 | LN | 2014-12-01 | Bruce Lake | Sw. 854 | 1 | 69 |  |  | Circuit 6937 - Rebuild old pole line. |  | IN |  |  | Proposed | 957800 | Engineering |  |  |  |  | Y | C
C | East | NIPS | 2244 | 2008-08-05 |  | 4158 | 2008-08-05 | LN | 2018-08-01 | Stillwell | Burr Oak | 1 | 345 |  | 1000 | new line |  | IN |  | 19.3 | Conceptual | 28000000 | [5 empty] | Y | C
C | East | NIPS | 2319 | 2009-09-14 | 71C7404 | 4245 | 2010-09-15 | SUB | 2013-05-01 | South Chalmers | Switch #62 |  | 69 |  |  | South Chalmers MO 62 load breaks and switch replacement. |  | IN |  |  | Proposed | 25000 | 08, Engineering |  |  |  |  | Y | C
C | East | NIPS | 2320 | 2010-09-15 | X7L6608 | 4246 | 2010-09-15 | LN | 2010-12-01 | Thayer | Starke | 1 | 138 |  |  | Circuit 13874 - Replace 58 wood poles up to 70 poles if need upon inspection, inspect and replace static wire as needed. First half of a two part project which will complete work begun in 2008. |  | IN |  |  | Planned | 600000 | 08, Engineering |  |  |  |  | Y | C
C | East | NIPS | 2321 | 2009-09-14 | 71C6336 | 4247 | 2009-09-14 | CAP | 2017-09-01 | Miller | Capacitor |  | 138 |  |  | Add one step of 100 MVAR capacitors on the Miller Substation 138 kV bus. Engineering only in 2010. |  | IN |  |  | Conceptual | 974838 | 08, Engineering |  |  |  |  | Y | C
C | East | NIPS | 2323 | 2009-09-14 | 9326172 | 4249 | 2009-09-14 | LN | 2016-12-01 | Hiple | Northport | 1 | 138 |  | 316 | Add new 138 kV terminals at Hiple and Northport Substations, and construct a new 10 mile 954 KCM ACSR 138 kV line between these two substations. Engineering only on 2008. |  | IN |  | 10 | Conceptual | 5770000 | 08, Engineering |  |  |  |  | Y | C
C | East | NIPS | 2324 | 2009-09-14 | 71C7213 | 4251 | 2009-09-14 | LN | 2016-05-01 | East Plymouth - (2) 345kV Line Extensions | Burr Oak and Leesburg | 1 | 345 |  |  | Split existing Burr Oak to Leesburg 345kV circuit and tie into new East Plymouth substation |  | IN |  |  | Conceptual | 2638409 | [5 empty] | Y | C
C | East | NIPS | 2324 | 2009-09-14 | 71C7213 | 4252 | 2009-09-14 | LN | 2016-05-01 | East Plymouth - (2) 138kV Line Extensions | Plymouth and Leesburg-Kosciusko | 1 | 138 |  |  | Split existing Plymouth-Leesburg-Kosciusko 138kV circuit and tie into new East Plymouth substation |  | IN |  |  | Conceptual | 3519080 | [5 empty] | Y | C
C | East | NIPS | 2324 | 2009-09-14 | 71C7213 | 4250 | 2009-09-14 | SUB | 2016-05-01 | East Plymouth 345/138 kV |  |  | 345 | 138 |  | Add East Plymouth 345/138 kV, 1-560 MVA Transformer Sub - New |  | IN |  |  | Conceptual | 12726528 | [5 empty] | Y | C
C | East | NIPS | 2792 | 2010-09-15 | X7L7502-71C6811-71C7517 | 4919 | 2010-09-15 | Lnup | 2012-12-01 | Northwest | circuit reconfiguration |  | 138 |  |  | Northwest circuit reconfig |  | IN |  |  | Conceptual | 2771000 | [5 empty] | Y | C
C | East | NIPS | 3399 | 2010-09-15 | X7L7705 | 6285 | 2010-09-15 | LN | 2010-12-01 | Goodland | Pine Creek |  | 69 |  | 65 | Circuit 6964 rebuild |  | IN | 29 |  | Proposed | 5567000 | Engineering |  |  |  |  | Y | C
C | East | NIPS | 3400 | 2010-09-15 | X7L7703 | 6286 | 2010-09-15 | LN | 2012-12-01 | Kreitzburg | Palmira |  | 69 |  | 55 | Extend 6951 to Palmira Substation |  | IN |  |  | Conceptual | 123000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 3401 | 2010-09-15 | X7L7704 | 6287 | 2010-09-15 | LN | 2013-12-01 | East Winamac | Bruce Lake |  | 69 |  | 65 | Circuit 6913 Rebuild Reconductor |  | IN | 10 |  | Conceptual | 2131000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 3402 | 2010-09-15 | X7L7706 | 6288 | 2010-09-15 | LN | 2013-12-01 | Goshen Jct | Third St. |  | 69 |  | 65 | Circuit 6981 Rebuild Reconductor |  | IN | 26 |  | Conceptual | 5563000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 3403 | 2010-09-15 | X7L7707 | 6289 | 2010-09-15 | LN | 2012-12-01 | Howe | LaGrange |  | 69 |  | 65 | Circuit 6987 Rebuild Reconductor |  | IN | 6.3 |  | Conceptual | 1383000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 3404 | 2010-09-15 | X7L7708 | 6290 | 2010-09-15 | LN | 2015-12-01 | Switch 151 | Warsaw |  | 69 |  | 60 | Circuit 6998, Switch 151 to Warsaw Sub Reconductor Rebuild |  | IN | 1.25 |  | Conceptual | 461000 | Planning |  |  |  |  | Y | C
C | East | NIPS | 3405 | 2010-09-15 | X7L7709 | 6291 | 2010-09-15 | LN | 2015-12-01 | Switch 934 | Switch 836 |  | 69 |  | 60 | Circuit 69-107 Reconductor |  | IN | 0.5 |  | Conceptual | 360000 | Planning |  |  |  |  | Y | C
C | West | ALTW, Non MISO | 2198 | 2008-08-05 | 38 | 4065 | 2008-08-05 | TX | 2018-08-01 | Rock Creek | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | IA |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 | 67 | 4094 | 2008-08-05 | LN | 2018-08-01 | Winnebago | Lakefield | 1 | 345 |  | 1000 | new line |  | MN |  | 55 | Conceptual | 59000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 | 68 | 4095 | 2008-08-05 | LN | 2018-08-01 | Hayward | Winnebago | 1 | 345 |  | 1000 | new line |  | MN |  | 50 | Conceptual | 53000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 |  | 4127 | 2008-08-05 | TX | 2018-08-01 | Adams | Transformer | 2 | 345 | 161 | 336 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 |  | 4126 | 2008-08-05 | TX | 2018-08-01 | Hayward | Transformer | 1 | 345 | 161 | 336 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 |  | 4125 | 2008-08-05 | TX | 2018-08-01 | Winnebago | Transformer | 1 | 345 | 161 | 336 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 |  | 4124 | 2008-08-05 | LN | 2018-08-01 | Hayward | Adams | 2 | 345 |  | 1000 | new line |  | MN |  | 37 | Conceptual | 40000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 |  | 4123 | 2008-08-05 | LN | 2018-08-01 | Hayward | Winnebago | 2 | 345 |  | 1000 | new line |  | MN |  | 50 | Conceptual | 53000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 |  | 4122 | 2008-08-05 | LN | 2018-08-01 | Winnebago | Lakefield | 2 | 345 |  | 1000 | new line |  | MN |  | 55 | Conceptual | 59000000 | [5 empty] | Y | C
C | West | ALTW, XEL | 2223 | 2008-08-05 | 71 | 4096 | 2008-08-05 | LN | 2018-08-01 | Hayward | Adams | 1 | 345 |  | 1000 | new line |  | MN |  | 37 | Conceptual | 40000000 | [5 empty] | Y | C
C | West | AmerenIL, ITCM | 2773 | 2010-05-08 | GPE | 4866 | 2009-08-14 | LN | 2020-12-31 | Plano | Hazleton | 1 | 765 |  | 3975/4570 MVA | Build 215 miles of new 765kV from the Hazleton substation in IA to the Plano substation in IL. |  | IA |  | 215 | Conceptual | 774000000 | [5 empty] | Y | C
C | West | ATC LLC | 89 | 2011-01-05 |  | 3248 | 2011-06-17 | LN | 2050-06-01 | Mill Rd | Bark River | 1 | 138 |  | 287/287 | Tap Bark River-Germantown into Mill Rd |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 89 | 2011-01-05 |  | 3249 | 2011-06-17 | LN | 2050-06-01 | Mill Rd | Germantown | 1 | 138 |  | 287/287 | Tap Bark River-Germantown into Mill Rd |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 89 | 2011-01-05 |  | 3250 | 2011-08-24 | LN | 2050-06-01 | Mill Rd | Sussex | 1 | 138 |  | 287/314 | Tap Sussex-Tamarack into Mill Rd |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 89 | 2011-01-05 |  | 3251 | 2011-08-24 | LN | 2050-06-01 | Mill Rd | Tamarack | 1 | 138 |  | 287/314 | Tap Sussex-Tamarack into Mill Rd |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 89 | 2011-01-05 |  | 3246 | 2011-06-17 | LN | 2050-06-01 | Mill Rd | Cypress | 1 | 345 |  | 586/586 | Tap Arcadian-Cypress into Mill Rd |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 89 | 2011-01-05 | 67 | 103 | 2011-06-17 | SUB | 2050-06-01 | Mill Road (renamed, was Lannon Junction) | transformer | 1 | 345 | 138 | 500 | transformer | K7 | WI |  |  | Conceptual | 29200000 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 89 | 2011-01-05 |  | 3247 | 2011-06-17 | LN | 2050-06-01 | Mill Rd | Arcadian | 1 | 345 |  | 586/586 | Tap Arcadian-Cypress into Mill Rd |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 341 | 2011-01-05 | newgrp19 | 483 | 2011-01-05 | LNrb | 2050-06-01 | Rockdale | Concord (rebuild to dbl ckt 138/345) | 1 | 345 |  | 815 | rebuild to dbl ckt 138/345 | K7 | WI | 22.6 |  | Conceptual | 22200000 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 341 | 2011-01-05 | newgrp19 | 477 | 2011-01-05 | SUB | 2050-06-01 | Concord 345/138 kV | transformer | 1 | 345 | 138 | 500 |  | K7 | WI |  |  | Conceptual | 12900000 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 341 | 2011-01-05 | newgrp19 | 893 | 2011-01-05 | LN | 2050-06-01 | Concord | Bark River | 1 | 345 |  | 815 | new line | K7 | WI |  | 19 | Conceptual | 50300000 | Eng | Network |  |  |  | Y | C
C | West | ATC LLC | 341 | 2011-01-05 | newgrp19 | 895 | 2011-01-05 | LNcnv | 2050-06-01 | Bark River | Mill Road | 1 | 345 |  | 815 | convert 138 to 345 kV | K7 | WI | 11 |  | Conceptual | 800000 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 341 | 2011-01-05 | newgrp19 | 894 | 2011-01-05 | TX | 2050-06-01 | Bark River | transformer | 1 | 345 | 138 | 500 | transformer | K7 | WI |  |  | Conceptual | 8400000 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 1621 | 2010-09-15 | PR03198 | 3239 | 2010-06-18 | LN | 2020-06-01 | Birchwood | Lake Delton | 1 | 138 |  | 383 | Build a new line between Birchwood & Lake Delton |  | WI | 5 |  | Conceptual | 5806000 | [5 empty] | Y | C
C | West | ATC LLC | 1625 | 2010-09-15 | PR03283 | 3244 | 2010-06-18 | LN | 2025-12-31 | North Randolph | South Fond du Lac | 1 | 345 |  | 1096 | Tap Columbia-South Fond du Lac into North Randolph |  | WI |  | 32.3 | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1625 | 2010-09-15 | PR03283 | 3243 | 2010-06-18 | LN | 2025-12-31 | North Randolph | Columbia | 1 | 345 |  | 1096 | Tap Columbia-South Fond du Lac into North Randolph |  | WI |  | 22.6 | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1625 | 2010-09-15 | PR03283 | 3242 | 2010-06-18 | TX | 2025-12-31 | North Randolph | Transformer | 1 | 345 | 138 | 500 | Install a 500 MVA 345/138 kV transformer at the North Randolph 138 kv SS by looping in the Columbia-South Fond du Lac 345-kV line |  | WI |  |  | Conceptual | 16552836 | [5 empty] | Y | C
C | West | ATC LLC | 1689 | 2010-09-15 | PR03927 | 3468 | 2010-06-18 | CAP | 2015-06-01 | Ripon | Capacitor bank |  | 69 |  | 1x8.2 MVAR | Install a new 8.2 MVAR capacitor bank at Ripon 69 kV substation |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1689 | 2010-09-15 | PR03927 | 3467 | 2010-06-18 | CAP | 2015-06-01 | Ripon | Capacitor bank |  | 69 |  | 1x8.2 MVAR | Upgrade 4.1 MVAR capacitor bank to 8.2 MVAR |  | WI |  |  | Conceptual | 895300 | [5 empty] | Y | C
C | West | ATC LLC | 1697 | 2010-09-15 | PR03227 | 3476 | 2010-04-30 | Lnup | 2020-06-01 | Brick Church | Walworth | 1 | 69 |  | 84 MVA | Uprate Brick Church-Walworth 69 kV line to 115 MVA |  | WI | 2.3 |  | Conceptual | 716000 | [5 empty] | Y | C
C | West | ATC LLC | 1700 | 2010-09-15 |  | 3480 | 2010-06-18 | LN | 2015-09-30 | SW Ripon | Ripon-Metomen | 1 | 69 |  | 56 MVA | Construct a 69 kV line from SW Ripon to the Ripon-Metomen 69 kV line |  | WI |  | 1.25 | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1703 | 2010-09-15 | PR03173 | 3484 | 2010-04-30 | CAP | 2019-06-01 | Boscobel | Capacitor bank |  | 69 |  | 8.16 MVAR | Upgrade existing 5.4 MVAR bank at Boscobel substation with an 8.16 MVAR bank |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1703 | 2010-09-15 | PR03173 | 3483 | 2010-04-30 | CAP | 2019-06-01 | Boscobel | Capacitor bank |  | 69 |  | 8.16 MVAR | Install one 8.16 MVAR capacitor bank at Boscobel 69 kV substation |  | WI |  |  | Conceptual | 1335173 | [5 empty] | Y | C
C | West | ATC LLC | 1707 | 2009-12-01 |  | 3489 | 2010-04-30 | LNrb | 2050-06-01 | Holmes | Chandler | 1 | 138 |  | 290 MVA | Rebuild/convert holmes-Chandler 69 kV line to 138 kV operation |  | MI/WI | 56.3 |  | Conceptual | 56300000 | [5 empty] | Y | C
C | West | ATC LLC | 1708 | 2010-09-15 | F2105, PRF1575a | 3490 | 2010-04-30 | LN | 2018-06-01 | Fairwater | Mackford Prairie | 1 | 69 |  | 72 MVA | Construct Fairwater-Mackford Prairie 69 kV line |  | WI |  | 3.5 | Conceptual | 3200000 | [5 empty] | Y | C
C | West | ATC LLC | 1708 | 2010-09-15 | F2105, PRF1575a | 3491 | 2010-04-30 | LN | 2018-06-01 | Ripon | Metomen | 2 | 69 |  | 59 MVA | Reconfigure the North Randolph-Ripon 69-kV line to form a second Ripon-Metomen 69-kV line and retire the circuit between Metomen and the Mackford Prairie tap |  | WI | 3.7 |  | Conceptual | 5679772.6 | [5 empty] | Y | C
C | West | ATC LLC | 1709 | 2010-09-15 | PR03176 | 3492 | 2010-04-30 | CAP | 2019-06-01 | Eden | Capacitor bank |  | 69 |  | 2x16.33 MVAR | Install two 16.33 MVAR 69 kV capacitor banks at Eden Substation |  | WI |  |  | Conceptual | 1568118 | [5 empty] | Y | C
C | West | ATC LLC | 1710 | 2010-09-15 | PR03174 | 3493 | 2010-04-30 | CAP | 2020-06-01 | Mazomanie | Capacitor bank |  | 69 |  | 2x12.25 MVAR | Install two 12.25 MVAR 69 kV capacitor banks at Mazomanie substation |  | WI |  |  | Conceptual | 1681113 | [5 empty] | Y | C
C | West | ATC LLC | 1712 | 2010-09-15 | PRF1007a | 3495 | 2010-04-30 | LN | 2022-06-01 | Horicon | East Beaver Dam | 1 | 138 |  | 293 MVA | Construct a Horicon-East Beaver Dam 138 kV line |  | WI |  | 10 | Conceptual | 18186000 | [5 empty] | Y | C
C | West | ATC LLC | 1717 | 2010-09-15 | PR03276 | 3503 | 2010-04-30 | TX | 2020-06-01 | Glenview | Transformer | 2 | 138 | 69 | 100 MVA | Replace two existing 138/69 kV transformers at Glenview Substaion with 100 MVA transformers |  | WI |  |  | Conceptual | 1720000 | [5 empty] | Y | C
C | West | ATC LLC | 1717 | 2010-09-15 | PR03276 | 3502 | 2010-04-30 | TX | 2020-06-01 | Glenview | Transformer | 1 | 138 | 69 | 100 MVA | Replace two existing 138/69 kV transformers at Glenview Substaion with 100 MVA transformers |  | WI |  |  | Conceptual | 1720000 | [5 empty] | Y | C
C | West | ATC LLC | 1718 | 2010-09-15 | F2081 | 3504 | 2010-04-30 | TX | 2022-06-01 | Custer | Transformer | 1 | 138 | 69 | 100 MVA | Install a 138/69 kV transformer at Custer substation |  | WI |  |  | Conceptual | 4904268 | [5 empty] | Y | C
C | West | ATC LLC | 1719 | 2010-09-15 | F2081 | 3505 | 2010-04-30 | LN | 2022-06-01 | Shoto | Custer | 1 | 138 |  | 290 MVA | Construct a Shoto-Custer 138 kV line |  | WI |  | 9.94 | Conceptual | 22938000 | [5 empty] | Y | C
C | West | ATC LLC | 1720 | 2010-09-15 | F2480 | 3506 | 2010-04-30 | TX | 2017-06-01 | Wautoma | Transformer | 2 | 138 | 69 | 100 MVA | Install a second 138/69-kV transformer at Wautoma Substation |  | WI |  |  | Conceptual | 1440000 | [5 empty] | Y | C
C | West | ATC LLC | 1721 | 2007-11-07 |  | 3509 | 2010-04-30 | LNrc | 2050-06-01 | Pulliam | Danz | 1 | 69 |  | 69 MVA | Reconductor Pulliam-Danz 69 kV line |  | WI | 2.63 |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1721 | 2007-11-07 |  | 3508 | 2010-04-30 | LNrc | 2050-06-01 | Pulliam | Van Buren | 1 | 69 |  | 69 MVA | Reconductor Pulliam-Van Buren 69 kV line |  | WI | 1.88 |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 1721 | 2007-11-07 |  | 3507 | 2010-06-18 | LNrc | 2050-06-01 | Danz | Henry Street | 1 | 69 |  | 57 MVA | Reconductor Danz-Henry Street 69 kV line |  | WI | 2.77 |  | Conceptual |  |  | Network |  |  |  | Y | C
C | West | ATC LLC | 1723 | 2010-09-15 | PR03962 | 3512 | 2010-04-30 | TX | 2024-06-01 | Sunset Point | Transformer | 2 | 138 | 69 | 100 MVA | Replace two existing 138/69-kV transformers at Sunset Point Substation with 100 MVA transformers |  | WI |  |  | Conceptual | 1770000 |  | Network |  |  |  | Y | C
C | West | ATC LLC | 1723 | 2010-09-15 | PR03962 | 3511 | 2010-04-30 | TX | 2024-06-01 | Sunset Point | Transformer | 1 | 138 | 69 | 100 MVA | Replace two existing 138/69-kV transformers at Sunset Point Substation with 100 MVA transformers |  | WI |  |  | Conceptual | 1770000 | [5 empty] | Y | C
C | West | ATC LLC | 1726 | 2010-09-15 | PR03902 | 3515 | 2010-04-30 | LNup | 2019-06-01 | Royster | Sycamore | 1 | 69 |  | 83 MVA | Uprate Royster-Sycamore 69 kV line to N/E = 200/275 deg F |  | WI | 3.35 |  | Conceptual | 790000 | [5 empty] | Y | C
C | West | ATC LLC | 1727 | 2010-09-15 | PR03957 | 3516 | 2010-04-30 | LN | 2018-06-01 | Dunn Road | Egg Harbor | 2 | 69 |  | 105 MVA | Construct a second Dunn Road-Egg Harbor 69 kV line |  | WI |  | 12.66 | Conceptual | 37194000 | [5 empty] | Y | C
C | West | ATC LLC | 1730 | 2010-12-03 |  | 3520 | 2010-04-30 | LN | 2020-06-01 | Cardinal | Blount | 1 | 138 |  | 290 MVA | Construct a West Middleton-Blount 138 kV line |  | WI |  | 6.15 | Conceptual | 60810250 | [5 empty] | Y | C
C | West | ATC LLC | 2029 | 2010-09-15 |  | 3903 | 2010-04-30 | CAP | 2017-06-01 | Brick Church | capacitor |  | 138 |  | 1x24.5 Mvar | Install 1-24.5 Mvar 138-kV capacitor bank at Brick Church |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 2029 | 2010-09-15 |  | 3904 | 2010-04-30 | CAP | 2017-06-01 | Brick Church | capacitor |  | 69 |  | 1x18Mvar | Install 1-18 Mvar 69-kV capacitor bank at Brick Church |  | WI |  |  | Conceptual | [6 empty] | Y | C
C | West | ATC LLC | 2030 | 2010-09-15 |  | 3905 | 2010-04-30 | CAP | 2020-06-01 | Concord | capacitor |  | 138 |  | 4x24.5 Mvar | Install 4-24.5 Mvar 138-kV capacitor bank at Concord |  | WI |  |  | Conceptual | 3358282 | [5 empty] | Y | C
C | West | ATC LLC | 2031 | 2010-09-15 |  | 3907 | 2010-04-30 | LNrb | 2018-06-01 | Enzyme Bio Systems Tap | RC3 (Clinton) | 1 | 69 |  | 84 MVA | Rebuild Enzyme Bio Systems Tap-RC3 (Clinton) 69 kV |  | WI |  | 5.33 | Conceptual | 3548749.4069 | [5 empty] | Y | C
C | West | ATC LLC | 2031 | 2010-09-15 |  | 3906 | 2010-04-30 | LNrb | 2018-06-01 | Colley Rd | Enzyme Bio Systems Tap | 1 | 69 |  | 84 MVA | Rebuild Colley Rd-Enzyme Bio Systems Tap 69 kV |  | WI |  | 0.98 | Conceptual | 652490.5101 | [5 empty] | Y | C
C | West | ATC LLC | 2031 | 2010-09-15 |  | 3908 | 2010-04-30 | LNrb | 2018-06-01 | RC3 (Clinton) | Clinton Tap | 1 | 69 |  | 146 MVA | Rebuild RC3 (Clinton)-Clinton Tap 69 kV |  | WI |  | 1.55 | Conceptual | 1032000.2966 | [5 empty] | Y | C
C | West | ATC LLC | 2031 | 2010-09-15 |  | 3909 | 2010-04-30 | LNrb | 2018-06-01 | Clinton Tap | Sharon Tap | 1 | 69 |  | 84 MVA | Rebuild Clinton Tap-Sharon Tap 69 kV |  | WI |  | 9 | Conceptual | 5992259.7865 | [5 empty] | Y | C
C | West | ATC LLC | 2038 | 2010-09-15 |  | 3918 | 2010-04-30 | LN | 2018-06-02 | Spring Valley | Twin Lakes | 1 | 138 |  | 293 MVA | Construct Spring Valley-Twin Lakes 138 kV |  | WI |  | 12 | Conceptual | 16642457.25 | [5 empty] | Y | C
C | West | ATC LLC | 2038 | 2010-09-15 |  | 3919 | 2010-04-30 | LN | 2018-06-02 | Twin Lakes | S Lake Geneva | 1 | 138 |  | 293 MVA | Construct Twin Lakes-S Lake Geneva 138 kV |  | WI |  | 12 | Conceptual | 16642457.25 | [5 empty] | Y | C
C | West | ATC LLC | 2040 | 2010-09-15 |  | 3921 | 2010-04-30 | CAP | 2020-06-01 | Sun Prairie | capacitor |  | 69 |  | 2x16.33 Mvar | Install 2x16.33 Mvar 69 kV capacitor banks at Sun Prairie |  | WI |  |  | Conceptual | 2566334.06 | [5 empty] | Y | C
C | West | ATC LLC | 2042 | 2010-09-15 |  | 3923 | 2010-06-18 | CAP | 2019-06-01 | Dam Heights | capacitor |  | 69 |  | 2x16.33 Mvar | Install 2x16.33 Mvar 69 kV caps at Dam Heights |  | WI |  |  | Conceptual | 2896361 | [5 empty] | Y | C
C | West | ATC LLC | 2043 | 2010-09-15 |  | 3924 | 2010-04-30 | SUB | 2018-06-01 | Necedah | sub conversion | 1 | 138 |  |  | Convert Necedah from 69 to 138 kV and tap into the Petenwell-Council Creek 138 kV line |  | WI |  |  | Conceptual | 761500 | [5 empty] | Y | C
C | West | ATC LLC | 2046 | 2010-09-15 |  | 3930 | 2010-04-30 | CAP | 2018-06-01 | North Monroe | capacitor |  | 69 |  | 2x16.33 Mvar | Install 2x16.33 Mvar 69 kV capacitor banks at North Monroe |  | WI |  |  | Conceptual | 2336040.28 | [5 empty] | Y | C
C | West | ATC LLC | 2056 | 2010-09-15 |  | 3943 | 2010-04-30 | LNup | 2020-06-01 | Oak Creek | Pennsylvania | 1 | 138 |  | 478 MVA | Uprate Oak Creek-Pennsylvania 138 kV |  | WI | 4.5 |  | Conceptual | 2409559 | [5 empty] | Y | C
C | West | ATC LLC | 2162 | 2010-09-15 |  | 4001 | 2010-04-30 | LN | 2017-06-01 | McCue | LaMar | 1 | 69 |  | 95 MVA | New 69-kV line with T2 4/0 ACSR |  | WI |  | 3.42 | Conceptual | 5009084.97 | [5 empty] | Y | C
C | West | ATC LLC | 2773 | 2010-05-08 | GPE | 4850 | 2010-04-30 | SUB | 2020-12-31 | North Madison | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in WI. Substation will have a single 765/345kV TRF tying to the North Madison 345kV system and a single 765kV line terminal. |  | WI |  |  | Conceptual | 85000000 | [5 empty] | Y | C
C | West | ATC LLC | 2779 | 2010-09-15 |  | 4883 | 2011-04-29 | TX | 2014-06-01 | 18th Road | Transformer | 1 | 138 | 69 | 60 MVA | Add a new 138/69 kV 150 MVA xfmr at 18th Road |  | MI |  |  | Proposed | 2000000 | [5 empty] | Y | C
C | West | ATC LLC | 2779 | 2010-09-15 |  | 4882 | 2011-04-29 | SUB | 2014-06-01 | 18th Road | Substation |  | 138 |  |  | Add a new 138/69 kV SS at 18th Road |  | MI |  |  | Proposed | 11000000 | [5 empty] | Y | C
C | West | ATC LLC | 2779 | 2010-09-15 |  | 4881 | 2011-04-29 | LN | 2014-06-01 | Chandler | 18th Road | 1 | 138 |  | 348 MVA | Buld a new 6-mile 138 kV line from Chandler to 18th Road |  | MI |  | 6 | Proposed | 6000000 | [5 empty] | Y | C
C | West | ATC LLC | 2779 | 2010-09-15 |  | 5478 | 2011-04-29 | LN | 2014-06-01 | Chandler | 18th Road | 2 | 138 |  | 348 MVA | Buld a new 6-mile 138 kV line from Chandler to 18th Road, that will be operated at 69 kV |  | MI |  | 6 | Proposed | 3000000 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 2779 | 2010-09-15 |  | 6483 | 2011-05-16 | CAP | 2014-06-01 | 18th Road |  |  | 69 |  |  | 2x4.08 Cap Bank at 18th Road Substation |  | WI |  |  | Proposed | [6 empty] | Y | C
C | West | ATC LLC | 2779 | 2010-09-15 |  | 6484 | 2011-05-16 | LN | 2014-06-01 | 18th Road | Mead | 1 | 69 |  | 57 | New 18th Rd -Mead 69 kV line |  | WI |  | 0.19 | Proposed | [6 empty] | Y | C
C | West | ATC LLC | 3096 | 2010-09-15 |  | 5422 | 2010-06-18 | LN | 2014-06-01 | Timber Products | Seney | 1 | 69 |  | 37 MVA | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance |  | MI | 28.4 |  | Conceptual | 11338403 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3096 | 2010-09-15 |  | 5421 | 2010-06-18 | LN | 2014-06-01 | Munising | Timber Products | 1 | 69 |  | 37 MVA | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance |  | MI | 6.2 |  | Conceptual | 2478285 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3096 | 2010-09-15 |  | 5423 | 2010-06-18 | LN | 2014-06-01 | Seney | Blaney Park | 1 | 69 |  | 37 MVA | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance |  | MI | 18 |  | Conceptual | 7186312 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3117 | 2010-09-15 |  | 5461 | 2010-06-18 | LN | 2021-06-01 | Townline Rd | Bass Creek | 1 | 138 |  | 211 MVA | Reconductor X-12 from Townline Rd to Bass Creek with 477 ACSR HAWK |  | WI | 11.7 |  | Conceptual | 1900000 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3124 | 2010-09-15 |  | 5475 | 2010-06-18 | LN | 2018-06-01 | Forsyth | Gwinn | 2 | 69 |  | 95 MVA | construct a 2nd Forsyth-Gwinn 69kV line |  | MI | 0.84 |  | Conceptual | 1000000 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3125 | 2010-09-15 |  | 5476 | 2011-08-24 | TX | 2015-06-01 | Arnold | transformer | 1 | 345 | 138 | 500 MVA | Tap the Plains-Dead River 345kV line into the Arnold 138kV substation and add a 345/138kV transformer |  | MI |  |  | Proposed | 16000000 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3158 | 2010-09-15 |  | 5546 | 2011-08-24 | TX | 2015-06-01 | Petenwell | transformer | 1 | 138 | 69 | 100 | Replace Petenwell Transformer, replace electromechanical relays, install highside circuit switchers on the GSUs for the Petenwell Hydro Plant |  | WI |  |  | proposed | 3246000 | planning preliminary estimate |  |  |  |  | Y | C
C | West | ATC LLC | 3159 | 2010-09-15 |  | 5547 | 2010-06-18 | LN | 2015-06-01 | West Middleton | Timberlane Tap | 1 | 69 |  | 83 | Uprate West Middleton to Timberlane Tap 69 kV Line |  | WI | 1.8 |  | Conceptual | 775650 | planning preliminary estimate |  |  |  |  | Y | C
C | West | ATC LLC | 3159 | 2010-09-15 |  | 5548 | 2010-06-18 | LN | 2015-06-01 | Timberlane Tap | Stage Coach | 1 | 69 |  | 84 | Uprate Timberlane Tap to Stage Coach 69 kV Line |  | WI | 2.4 |  | Conceptual | 1032393 | planning preliminary estimate |  |  |  |  | Y | C
C | West | ATC LLC | 3164 | 2010-09-15 | RGOS DC | 5563 | 2010-08-09 | LN | 2020-06-01 | Point Beach | Ludington | 1 | 350 |  | 1000 | Construct a HVDC line under Lake Michigan from Point Beach to Ludington |  | WI/MI |  | 64 | Conceptual | 828000000 | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3164 | 2010-09-15 | RGOS DC | 5564 | 2010-08-09 | SUB | 2020-06-01 | WI HVDC North | DC Station for 1000 MW |  | 350 |  |  | Install a HVDC converter station near Point Beach |  | WI |  |  | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3164 | 2010-09-15 | RGOS DC | 5565 | 2010-08-09 | SUB | 2020-06-01 | MI HVDC North | DC Station for 1000 MW |  | 350 |  |  | Install a HVDC converter station near Ludington |  | MI |  |  | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3164 | 2010-09-15 | RGOS DC | 5566 | 2010-08-09 | LN | 2020-06-01 | WI HVDC North | Point Beach |  | 345 |  | 1250 | Construct a 345 kV line to connect the WI HVDC North SS to Point Beach |  | WI |  | 0.5 | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3164 | 2010-09-15 | RGOS DC | 5567 | 2010-08-09 | LN | 2020-06-01 | MI HVDC North | Ludington |  | 345 |  | 1250 | Construct a 345 kV line to connect the MI HVDC North SS to Ludington |  | MI |  | 0.5 | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3165 | 2010-09-15 |  | 5569 | 2010-06-18 | SUB | 2020-06-01 | WI HVDC South | substation |  | 350 | 345 |  | Install a HVDC converter station near Elm Rd |  | WI |  |  | Conceptual |  | Preliminary |  |  |  |  | Y | C
C | West | ATC LLC | 3165 | 2010-09-15 |  | 5570 | 2010-06-18 | SUB | 2020-06-01 | MI HVDC South | substation |  | 765 | 350 |  | Install a HVDC converter station near DC Cook |  | MI |  |  | Conceptual |  | Preliminary |  |  |  |  | Y | C
C | West | ATC LLC | 3165 | 2010-09-15 |  | 5572 | 2010-06-18 | LN | 2020-06-01 | MI HVDC South | DC Cook |  | 765 |  | 1250 | Construct a 765 kV line to connect the MI HVDC South SS to DC Cook |  | MI |  | 0.5 | Conceptual |  | Preliminary |  |  |  |  | Y | C
C | West | ATC LLC | 3165 | 2010-09-15 |  | 5571 | 2010-06-18 | LN | 2020-06-01 | WI HVDC South | Elm Rd |  | 345 |  | 1250 | Construct a 345 kV line to connect the WI HVDC South SS to Elm Rd |  | WI |  | 0.5 | Conceptual |  | Preliminary |  |  |  |  | Y | C
C | West | ATC LLC | 3165 | 2010-09-15 |  | 5568 | 2010-08-09 | LN | 2020-06-01 | Elm Rd | DC Cook | 1 | 350 |  | 1000 | Construct a HVDC line under Lake Michigan from Elm Rd to DC Cook |  | WI/MI |  | 91 | Conceptual | 1071000000 | Preliminary |  |  |  |  | Y | C
C | West | ATC LLC | 3166 | 2010-09-15 |  | 5573 | 2010-06-18 | TR | 2018-06-01 | Hillman | transformer | 2 | 138 | 69 | 100 | Install a 2nd transformer |  | WI |  |  | Conceptual | 4843288 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 3167 | 2010-09-15 |  | 5574 | 2010-06-18 | LN | 2018-06-01 | South Monroe | Monroe Central Tap | 1 | 69 |  | 84 | Increase line clearance for 300 deg F Summer Emergency operation |  | WI | 0.8 |  | Conceptual | 871408 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 3167 | 2010-09-15 |  | 5575 | 2010-06-18 | LN | 2018-06-01 | Monroe Central Tap | Idle Hour Tap | 1 | 69 |  | 84 | Increase line clearance for 300 deg F Summer Emergency operation |  | WI | 1.6 |  | Conceptual | 1742817 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 3167 | 2010-09-15 |  | 5576 | 2010-06-18 | LN | 2018-06-01 | Idle Hour Tap | North Monroe | 1 | 69 |  | 84 | Increase line clearance for 300 deg F Summer Emergency operation |  | WI | 4.1 |  | Conceptual | 4465968 | Eng |  |  |  |  | Y | C
C | West | ATC LLC | 3189 | 2010-09-15 |  | 5630 | 2010-06-18 | LNrc | 2019-06-01 | Ripon | Northwest Ripon | 1 | 69 |  | 84 | Uprate line Y-93 from Ripon to Northwest Ripon from 167 deg F to SN/SE |  | WI | 1.8 |  | Conceptual | 2205426 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3190 | 2010-09-15 |  | 5631 | 2010-06-18 | LNrc | 2019-06-01 | Sunset Point | Winneconne | 1 | 69 |  | 84 | Rebuild line Y-103 from Sunset Point to Winneconne to SN/SE = 200/300 deg F |  | WI | 10.5 |  | Conceptual | 12366239 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3207 | 2010-09-15 |  | 5974 | 2010-07-19 | TX | 2016-06-01 | Harrison | Transformer | 1 | 138 | 69 | 100 | Replace Harrison 138/69kV Tr with a larger unit and uprate terminal equipment to a minimum of the transformer ratings |  | WI |  |  | Conceptual | 3229974 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3208 | 2010-09-15 |  | 5975 | 2010-07-19 | TX | 2018-06-01 | Caroline | Transformer | 1 | 115 | 69 | 100 | Replaces Caroline 115/69-kV transformer with a dual high side 138-115/69-kV 100 MVA transformer and uprate terminal equipment to a minimum of the transformer ratings |  | WI |  |  | Conceptual | 4010542 | eng |  |  |  |  | Y | C
C | West | ATC LLC | 3429 | 2010-10-20 | PR04087 | 6324 | 2011-03-18 | LNrb | 2020-06-01 | Sun Valley Tap | Oregon | 1 | 69 |  | 80 | Rebuild Sun Valley Tap-Oregon |  | WI | 6.7 |  | Conceptual | 5561798 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3430 | 2010-10-20 | PR03211 | 6326 | 2010-10-20 | LNrb | 2016-06-01 | Brusbay | Sawyer | 1 | 69 |  | 64 | Rebuild Brusbay-Sawyer 69 kV |  | WI | 7.9 |  | Conceptual | 3793968 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3430 | 2010-10-20 | PR03211 | 6325 | 2010-10-20 | LNrb | 2016-06-01 | Dyckesville | Brusbay | 1 | 69 |  | 80 | Rebuild Dyckesville-Brusbay 69 kV |  | WI | 16.7 |  | Conceptual | 8020160 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3487 | 2011-03-22 |  | 6445 | 2011-04-19 | Line | 2022-06-01 | West Middleton | Pheasant Branch | 2 | 69 |  | 173 | Replace existing single circuit from WMD-Pheasant Branch 69 kV with double circuit 69 kV lines. |  | WI |  | 4.52 | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3487 | 2011-03-22 |  | 6444 | 40652 | Line | 2022-06-01 | West Middleton | Pheasant Branch | 1 | 69 |  | 153 | Replace existing single circuit from WMD-Pheasant Branch 69 kV with double circuit 69 kV lines. |  | WI | 4.52 |  | Conceptual | 22711186 | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3506 | 2011-04-20 | PR04371 | 6475 | 2011-08-24 | Line | 2012-12-31 | Vinburn | Deforest | 1 | 69 |  | 80 | Y-104c, 1/4 mile of double circuit (minimum rating of 706 Amps, SN, 961 amps, SE) for the loop through feed off of line Y104 |  | WI |  | 0.25 | Proposed |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3506 | 2011-04-20 | PR04371 | 6473 | 2011-08-24 | Line | 2012-12-31 | Vinburn | Hampden | 1 | 69 |  | 72 | Y-104a, 1/4 mile of single circuit (minimum rating of 706 amps SN, 961 amps SE) to serve the Hampden tap |  | WI |  | 0.25 | Proposed | 3362287 | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3506 | 2011-04-20 | PR04371 | 6474 | 2011-08-24 | Line | 2012-12-31 | Vinburn | Sun Prairie Business Park | 1 | 69 |  | 80 | Y-104b, 1/4 mile of double circuit (minimum rating of 706 Amps, SN, 961 amps, SE) for the loop through feed off of line Y104 |  | WI |  | 0.25 | Proposed |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3507 | 2011-04-20 | PR04556 | 6476 | 2011-04-20 | Line | 2012-03-01 | Shoto | Manrap | 1 | 69 |  | 80 | Uprate of C-55 (MANRAP - SHOTO 69KV) |  | WI | 7.65 |  | Proposed | 319044 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3508 | 2011-08-24 | PR04554 | 6477 | 2011-04-20 | Line | 2012-01-01 | Revere | N. East | 1 | 69 |  | 83 | Uprate of C-103 (REVERE - N.EAST 69KV) |  | WI | 2.32 |  | Proposed | 171475 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3510 | 2011-05-16 |  | 6482 | 2011-05-16 | LN | 2017-06-01 | Edgewood | St. Martins | 1 | 138 |  | 287 | 3013 Edgewood-St. Martins 138-kV rebuild |  | WI | 7.07 |  | Proposed | 9200000 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3510 | 2011-05-16 |  | 6481 | 2011-05-16 | LN | 2017-06-01 | Mukwonago | Edgewood | 1 | 138 |  | 293 | 671K61 Mukwonago-Edgewood 138-kV rebuild |  | WI | 7.19 |  | Proposed | 10000000 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3511 | 2011-05-16 |  | 6485 | 2011-05-16 | LN | 2011-11-14 | Edgewater | Saukville | 1 | 345 |  | 785 | uprate Edgewater to Saukville 345 kV line |  | WI |  |  | Proposed | 1798252 | Engineering |  |  |  |  | Y | C
C | West | ATC LLC | 3512 | 2011-05-16 |  | 6490 | 40679 | LN | 2020-06-01 | MI HVDC North | Cook | 1 | 345 |  |  | Construct a 345 kV line to connect the MI HVDC North SS to Ludington |  | MI |  | 0.5 | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3512 | 2011-05-16 |  | 6489 | 40679 | LN | 2020-06-01 | WI HVDC North | Pleasant Prairie | 1 | 345 |  |  | Construct a 345 kV line to connect the WI HVDC North SS to Point Beach |  | WI |  | 0.5 | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3512 | 2011-05-16 |  | 6488 | 40679 | SUB | 2020-06-01 | MI HVDC North | DC Station for 1000 MW |  | 350 |  |  | Install a HVDC converter station near Ludington |  | MI |  |  | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3512 | 2011-05-16 |  | 6487 | 40679 | SUB | 2020-06-01 | WI HVDC North | DC Station for 1000 MW |  | 350 |  |  | Install a HVDC converter station near Point Beach |  | WI |  |  | Conceptual |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3512 | 2011-05-16 |  | 6486 | 40679 | LN | 2020-06-01 | Pleasant Prairie | Cook | 1 | 350 |  |  | Construct a HVDC line under Lake Michigan from Point Beach to Ludington |  | WI/MI |  | 86 | Conceptual | 828000000 | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3515 | 2011-06-07 | PR04627 | 6495 | 2011-06-07 | LN | 2011-12-31 | Granville | Tosa | 1 | 138 |  | 293 | Uprate Granville-Tosa 138 kV line |  | WI |  |  | Proposed | 1136322 | Planning |  |  |  |  | Y | C
C | West | ATC LLC | 3515 | 2011-06-07 | PR04627 | 6496 | 2011-06-07 | LN | 2011-12-31 | Granville | Butler | 1 | 138 |  | 293 | Uprate Granville-Butler 138 kV line |  | WI |  |  | Proposed |  | Planning |  |  |  |  | Y | C
C | West | ATC LLC, ALTW | 2230 | 2008-08-05 |  | 4143 | 2008-08-05 | LN | 2018-08-01 | Spring Green | West Middleton | 1 | 345 |  | 1412 | new line |  | WI |  | 18 | Conceptual | 23000000 | [5 empty] | Y | C
C | West | ATC LLC, ALTW | 2230 | 2008-08-05 |  | 4144 | 2008-08-05 | TX | 2018-08-01 | Spring Green | Transformer | 1 | 345 | 138 | 336 | new transformer |  | WI |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | ATC LLC, ALTW | 2230 | 2008-08-05 |  | 4105 | 2008-08-05 | LN | 2018-08-01 | Spring Green | Salem | 1 | 345 |  | 1412 | new line |  | WI |  | 54 | Conceptual | 69000000 | [5 empty] | Y | C
C | West | ATC LLC, XEL | 2211 | 2008-08-05 | 7 | 4037 | 2008-08-05 | LN | 2018-08-01 | Longwood | Greenwood | 1 | 345 |  | 1000 | new line |  | WI |  | 14 | Conceptual | 200000000 | [5 empty] | Y | C
C | West | ATC LLC, XEL | 2773 | 2010-05-08 | GPE | 4857 | 2009-08-14 | LN | 2020-12-31 | North Madison | Adams | 1 | 765 |  | 3975/4570 MVA | Build 250 miles of new 765kV from the Adams substation in southeast MN to the North Madison substaton in WI. |  | MN/WI |  | 250 | Conceptual | 900000000 | [5 empty] | Y | C
C | West | DEM, AmerenIL, ITCM | 2773 | 2010-05-08 | GPE | 4867 | 2009-08-14 | LN | 2020-12-31 | Sullivan | Grimes | 1 | 765 |  | 3975/4570 MVA | Build 455 miles of new 765kV from the Grimes substation in IA to the Sullivan substation in IN. |  | IA/MO/IL/IN |  | 455 | Conceptual | 1638000000 | [5 empty] | Y | C
C | West | DPC, ATC LLC | 2231 | 2008-08-05 |  | 4106 | 2008-08-05 | LN | 2018-08-01 | Hilltop | Columbia | 1 | 345 |  | 1195 | new line |  | WI |  | 50 | Conceptual | 68000000 | [5 empty] | Y | C
C | West | DPC, ATC LLC | 2231 | 2008-08-05 |  | 4107 | 2008-08-05 | TX | 2018-08-01 | Hilltop | Transformer | 1 | 345 | 138 | 500 | new transformer |  | WI |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | DPC, ATC LLC | 2231 | 2008-08-05 |  | 4145 | 2008-08-05 | LN | 2018-08-01 | Hilltop | LaCrosse | 1 | 345 |  | 1195 | new line |  | WI |  | 80 | Conceptual | 108000000 | [5 empty] | Y | C
C | West | GRE | 2569 | 2010-09-15 | 20138 | 4580 | 2010-09-15 | LN | 2013-12-02 | Shoal Lake | Nashwauk Tap | 1 | 115 |  |  | Distribution conversion to 115 kV |  | MN |  | 8 | Planned | 6450514.76 | Engineering |  |  |  |  | Y | C
C | West | GRE | 2600 | 2010-09-15 | 20339 | 4611 | 2011-03-28 | LN | 2015-10-30 | Big Sandy | Big Sandy Tap | 1 | 69 |  |  | New Distribution |  | MN |  | 4 | Planned | 5149000 | Planning |  |  |  |  | NT | C
C | West | GRE | 2632 | 2010-09-15 | 20385 | 4643 | 2009-12-29 | LN | 2013-12-01 | Onigum | Birch Lake | 1 | 115 |  | 140 | Onigum 115 kV conversion, Birch Lake 115 kV breaker and deadend |  | MN | 9.45 |  | Proposed | 5300000 | [5 empty] | Y | C
C | West | GRE | 2691 | 2010-09-15 | 20472 | 4709 | 2009-12-29 | LN | 2017-06-01 | Orrock | Waco | 1 | 115 | 69 | 315.9/135.9 | Double Circuit |  | MN | 3.5 |  | Conceptual | [6 empty] | Y | C
C | West | GRE | 2691 | 2010-09-15 | 20472 | 4711 | 2009-12-29 | LN | 2017-06-01 | Liberty | Thompson Lake | 1 | 115 |  | 135.9 | Reconductor |  | MN | 3.29 |  | Conceptual | [6 empty] | Y | C
C | West | GRE | 2691 | 2010-09-15 | 20472 | 4708 | 2009-12-29 | TX | 2017-06-01 | Orrock | transformer | 1 | 345 | 115 | 336 |  |  | MN |  |  | Conceptual | 19661825 | [5 empty] | Y | C
C | West | GRE | 2691 | 2010-09-15 | 20472 | 4710 | 2009-12-29 | LN | 2017-06-01 | Thompson Lake | Waco | 1 | 115 | 69 | 315.9/135.9 | Double Circuit |  | MN | 10.33 |  | Conceptual | [6 empty] | Y | C
C | West | GRE | 3393 | 2010-09-15 | 200340 | 6266 | 2010-09-15 | LN | 2013-11-01 | Peterson | 115 kV distribution tap switch |  | 115 |  | 0 | Convert Peterson 24 kV substation to 115 kV |  | MN | 0 | 0 | Planned | 742690 | Planning |  |  | N |  | Y | C
C | West | GRE | 3470 | 2011-01-11 |  | 6397 | 2011-07-01 | Gen | 2011-12-01 | G667 | [7 empty] | MN |  |  | Planned | 118182 | Eng |  |  |  |  | Y | C
C | West | GRE, OTP | 2773 | 2010-05-08 | GPE | 4865 | 2009-08-14 | LN | 2020-12-31 | Antelope Valley | New North Dakota | 1 | 765 |  | 3975/4570 MVA | Build 135 miles of new 765kV from the Chisago substation in MN to the new North Dakota substation in ND. |  | SD/ND/IA |  | 135 | Conceptual | 486000000 | [5 empty] | Y | C
C | West | GRE, OTP, XEL | 2773 | 2010-05-08 | GPE | 4864 | 2009-08-14 | LN | 2020-12-31 | Chisago | New North Dakota | 1 | 765 |  | 3975/4570 MVA | Build 355 miles of new 765kV from the Chisago substation in MN to the new Nroth Dakota substation in ND. |  | SD/ND/IA |  | 355 | Conceptual | 1278000000 | [5 empty] | Y | C
C | West | GRE, XEL | 2773 | 2010-05-08 | GPE | 4844 | 2009-08-14 | SUB | 2020-12-31 | Helena | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in MN. Substation will have a single 765/345kV TRF tying to the Helena 345kV system and three 765kV line terminals. |  | MN |  |  | Conceptual | 120000000 | [5 empty] | Y | C
C | West | GRE, XEL | 2773 | 2010-05-08 | GPE | 4854 | 2009-08-14 | LN | 2020-12-31 | Helena | Chisago | 1 | 765 |  | 3975/4570 MVA | Build 160 miles of new 765kV from the Helena Substation to the Adams substation in southeast MN. |  | MN |  | 160 | Conceptual | 576000000 | [5 empty] | Y | C
C | West | GRE, XEL | 2773 | 2010-05-08 | GPE | 4855 | 2009-08-14 | LN | 2020-12-31 | Helena | Adams | 1 | 765 |  | 3975/4570 MVA | Build 130 miles of new 765kV from the Helena Substation to the Adams substation in southeast MN. |  | MN |  | 130 | Conceptual | 468000000 | [5 empty] | Y | C
C | West | GRE, XEL | 2773 | 2010-05-08 | GPE | 4853 | 2009-08-14 | LN | 2020-12-31 | Helena | Lakefield | 1 | 765 |  | 3975/4570 MVA | Build 115 miles of new 765kV from the Helena Substation to the Lakefield substation in southwest MN. |  | MN |  | 115 | Conceptual | 414000000 | [5 empty] | Y | C
C | West | ITCM | 1738 | 2009-09-25 | Bert161 | 3536 | 2010-06-28 | LNrc | 2017-12-31 | Bertram | Hills | 1 | 161 |  | 446/446 MVA | Reconductor the Bertram-Rose Hollow-Hills |  | IA | 32.2 |  | Proposed | 22540000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1742 | 2009-09-25 | 3MN | 4392 | 2009-09-25 | LNrb | 2014-12-31 | Brewster | Heron Lake | 1 | 161 |  | 446 MVA | Rebuild existing line |  | MN | 14.64 |  | Proposed | 10220000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1742 | 2009-09-25 | 3MN | 3544 | 2009-09-25 | LNrb | 2015-12-31 | Elk | Brewster | 1 | 161 |  | 326/326 MVA | Rebuild existing line |  | MN | 3.32 |  | Proposed | 2324000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1742 | 2009-09-25 | 3MN | 3543 | 2009-09-25 | LNrb | 2015-12-31 | Magnolia | Elk | 1 | 161 |  | 326/326 MVA | Rebuild existing line |  | MN | 18.75 |  | Proposed | 13160000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1742 | 2009-09-25 | 3MN | 3542 | 2009-09-25 | LNrb | 2016-12-31 | Split Rock | Magnolia | 1 | 161 |  | 446/446 MVA | Rebuild existing line |  | MN | 11 |  | Proposed | 7700000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1746 | 2010-07-16 |  | 3549 | 2009-09-25 | LNrb | 2011-12-31 | Fox Lake | Rutland | 1 | 161 |  | 446/446 MVA | Rebuild existing line |  | MN | 17 |  | Proposed | 11900000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1746 | 2010-07-16 |  | 3550 | 2009-09-25 | LNrb | 2012-12-31 | Rutland | Winnebago | 1 | 161 |  | 446/446 MVA | Rebuild existing line |  | MN | 14.6 |  | Proposed | 10220000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1746 | 2010-07-16 |  | 3552 | 2009-09-25 | LNrb | 2014-12-31 | Winnebago | Hayward | 1 | 161 |  | 446/446 MVA | Rebuild existing line |  | MN | 49.09 |  | Proposed | 34370000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1746 | 2010-07-16 |  | 3553 | 2009-09-25 | LNrb | 2015-12-31 | Hayward | Adams | 1 | 161 |  | 446/446 MVA | Rebuild existing line |  | MN | 36.39 |  | Proposed | 25480000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 1746 | 2010-07-16 |  | 3551 | 2010-07-16 | LNrb | 2015-12-31 | Lakefield Jct | Fox | 1 | 161 |  | 446/446 MVA | Rebuild existing line |  | MN | 22.3 |  | Proposed | 15610000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 2773 | 2010-05-08 | GPE | 4849 | 2009-08-14 | SUB | 2020-12-31 | Hazleton | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in IA. Substation will have a single 765/345kV TRF tying to the Hazleton 345kV system and two 765kV line terminals. |  | IA |  |  | Conceptual | 110000000 | [5 empty] | Y | C
C | West | ITCM | 2773 | 2010-05-08 | GPE | 4847 | 2009-08-14 | SUB | 2020-12-31 | Iowa new substation | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in IA. Substation will have a single 765/345kV TRF and three 765kV line terminals. |  | IA |  |  | Conceptual | 120000000 | [5 empty] | Y | C
C | West | ITCM | 2773 | 2010-05-08 | GPE | 4845 | 2009-08-14 | SUB | 2020-12-31 | Lakefield | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new two TRF 765/345kV substation in southwest MN. Substation will have two 765/345kV TRFs tying to the Lakefield 345kV system and four 765kV line terminals. |  | MN |  |  | Conceptual | 220000000 | [5 empty] | Y | C
C | West | ITCM | 2773 | 2010-05-08 | GPE | 4860 | 2009-08-14 | LN | 2020-12-31 | Lakefield | New IA Substation | 1 | 765 |  | 3975/4570 MVA | Build 100 miles of new 765kV from the Lakefield substation in southwest MN to a new IA substation in western IA. |  | MN/IA |  | 100 | Conceptual | 360000000 | [5 empty] | Y | C
C | West | ITCM | 2773 | 2010-05-08 | GPE | 4858 | 2009-08-14 | LN | 2020-12-31 | Lakefield | Adams | 1 | 765 |  | 3975/4570 MVA | Build 140 miles of new 765kV from the Lakefield substation in southwest MN to the Adams substation in southeast MN. |  | MN |  | 140 | Conceptual | 504000000 | [5 empty] | Y | C
C | West | ITCM | 2773 | 2010-05-08 | GPE | 4862 | 2009-08-14 | LN | 2020-12-31 | Fort Thompson | New IA Substation | 1 | 765 |  | 3975/4570 MVA | Build 305 miles of new 765kV from the new IA substation to the Fort Thompson substation in SD. |  | SD/IA |  | 305 | Conceptual | 1098000000 | [5 empty] | Y | C
C | West | ITCM | 2830 | 2009-08-28 | FG5 | 4971 | 2009-08-28 | LN | 2014-01-01 | Lakefield Jct | Rutland | 1 | 345 |  | 1500 |  |  | MN | 39.4 |  | Proposed | 98500000 | [5 empty] | Y | C
C | West | ITCM | 2830 | 2009-08-28 | FG5 | 4972 | 2009-08-28 | TX | 2014-01-01 | Rutland | 345/161 kV transformer | 1 | 345 | 161 | 336 |  |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | ITCM | 2950 | 2010-09-01 | T3211 | 5137 | 2010-09-01 | LN | 2018-06-01 | Polk City | NE Ankeny | 1 | 161 |  |  | Polk City Sub dbl ckt line tap (cost is included with Bittersweet Road-Polk City line tap) | H8 | IA |  | 3.5 | Conceptual |  | Planning 2010$ |  |  |  |  | Y | C
C | West | ITCM | 2950 | 2010-09-01 | T3211 | 5136 | 2010-09-01 | LN | 2018-06-01 | Bittersweet Road | Polk City | 1 | 161 |  |  | Polk City Sub dbl ckt line tap | H8 | IA |  | 3.5 | Conceptual |  | Planning 2010$ |  |  |  |  | Y | C
C | West | ITCM | 3086 | 2009-09-25 | 8th-Lore | 5394 | 2009-09-25 | LN | 2013-12-31 | 8th Street | Kerper | 1 | 161 |  | 326 MVA | Rebuild 161kV line | J7 | IA | 2.6 |  | Proposed | 1430000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 3086 | 2009-09-25 | 8th-Lore | 5395 | 2009-09-25 | LN | 2014-12-31 | Kerper | Lore | 1 | 161 |  | 326 MVA | Rebuild 161kV line | J7 | IA | 10.23 |  | Proposed | 5626500 | Planning |  |  |  |  | Y | C
C | West | ITCM | 3087 | 2009-09-25 | Lansing-Harmony | 5396 | 2011-07-01 | LN | 2016-12-31 | Lansing | Harmony | 1 | 161 |  | 326 MVA | Rebuild part of IA line sections | J7 | IA |  |  | Proposed | 30000000 | Planning |  |  |  |  | Y | C
C | West | ITCM | 3500 | 2011-03-28 |  | 6460 | 40630 |  | 2012-12-31 | NERC Alert Facility Ratings for 2012 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | IA |  |  | Planned | [6 empty] | Y | C
C | West | ITCM | 3501 | 2011-03-28 |  | 6461 | 40630 |  | 2013-12-31 | NERC Alert Facility Ratings for 2013 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | IA |  |  | Planned | [6 empty] | Y | C
C | West | ITCM | 3502 | 2011-03-28 |  | 6462 | 40630 |  | 2014-12-31 | NERC Alert Facility Ratings for 2014 | Throughout system |  |  |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert |  | IA |  |  | Planned | [6 empty] | Y | C
C | West | ITCM, AmerenIL | 2785 | 2009-04-23 | 6 | 4893 | 2010-05-08 | TEQ | 2014-05-01 | New Substation in NW Iowa | +/- 800KV DC converter station | 1 | 800 |  | 6400 | new +/- 800KV DC converter station |  | IA |  |  | Proposed | [6 empty] | Y | C
C | West | ITCM, MEC | 2773 | 2010-05-08 | GPE | 4861 | 2009-08-14 | LN | 2020-12-31 | Grimes | New IA Substation | 1 | 765 |  | 3975/4570 MVA | Build 115 miles of new 765kV from the new IA substation to Grimes substation near Des Moines, IA. |  | IA |  | 115 | Conceptual | 414000000 | [5 empty] | Y | C
C | West | ITCM, XEL | 2773 | 2010-05-08 | GPE | 4856 | 2009-08-14 | LN | 2020-12-31 | Hazleton | Adams | 1 | 765 |  | 3975/4570 MVA | Build 85 miles of new 765kV from the Hazleton substation in IA to the Adams substation in southeast MN. |  | MN/IA |  | 85 | Conceptual | 306000000 | [5 empty] | Y | C
C | West | ITCM, XEL | 2773 | 2010-05-08 | GPE | 4859 | 2009-08-14 | LN | 2020-12-31 | Lakefield | Fort Thompson | 1 | 765 |  | 3975/4570 MVA | Build 240 miles of new 765kV from the Lakefield substation in southwest MN to the Fort Thompson substation in SD. |  | MN/SD |  | 240 | Conceptual | 864000000 | [5 empty] | Y | C
C | West | MDU | 3082 | 2009-09-15 | NW Bism | 5362 | 2009-09-15 | CB | 2014-06-01 | NW Bismarck | 3 PCB |  | 115 |  |  | Create a ring bus |  | ND |  |  | Planned | 3050000 | Engineering |  |  |  |  | Y | C
C | West | MDU | 3084 | 2009-09-15 | East Bism | 5370 | 2009-09-15 | TEQ | 2015-12-01 | East Bismarck | Termial Equipment |  | 115 |  |  | Upgrade Terminal Equip. to increase line rating |  | ND |  |  | Proposed | 100000 | Engineering |  |  |  |  | Y | C
C | West | MDU | 3084 | 2009-09-15 | East Bism | 5369 | 2009-09-15 | LN | 2015-12-01 | East Bismarck | Bismarck (WAPA) | 1 | 115 |  | 200 | New line Segment |  | ND |  | 0.1 | Proposed | 400000 | Engineering |  |  |  |  | Y | C
C | West | MDU | 3084 | 2009-09-15 | East Bism | 5368 | 2009-09-15 | CB | 2015-12-01 | East Bismarck | 4 PCB |  | 115 |  |  | Add bus tie breaker & new line terminal |  | ND |  |  | Proposed | 2000000 | Engineering |  |  |  |  | Y | C
C | West | MDU | 3456 | 2010-10-21 | Glenham xfmr | 6334 | 2010-10-21 | TX | 2016-06-01 | Glenham | Transformer | 1 | 230 | 115 | 50/40/20 | Replacement 230/115/41.6 transformer |  | SD |  |  | Planned | 2500000 | Planning |  |  |  |  | Y | C
C | West | MDU | 3456 | 2010-10-21 | Glenham xfmr | 6335 | 2010-10-21 | CB | 2016-06-01 | Glenham | 2 PCB |  | 230 |  |  | Create a ring bus |  | SD |  |  | Planned | 2500000 | Planning |  |  |  |  | Y | C
C | West | MDU | 3456 | 2010-10-21 | Glenham xfmr | 6336 | 2010-10-21 | CB | 2016-06-01 | Glenham | 2 PCB |  | 115 |  |  | Add low side transformer breakers |  | SD |  |  | Proposed | 2000000 | Planning |  |  |  |  | Y | C
C | West | MDU, NON-MISO | 2214 | 2008-08-05 | 53 | 4080 | 2008-08-05 | LN | 2018-08-01 | Glenham | Ellendale | 1 | 345 |  | 872 | new line |  | SD/ND |  | 86 | Conceptual | 37000000 | [5 empty] | Y | C
C | West | MDU, NON-MISO | 2214 | 2008-08-05 | 54 | 4081 | 2008-08-05 | TX | 2018-08-01 | Glenham | Transformer | 1 | 345 | 230 | 336 | new transformer |  | SD |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | MEC | 2773 | 2010-05-08 | GPE | 4848 | 2009-08-14 | SUB | 2020-12-31 | Grimes | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in IA. Substation will have a single 765/345kV TRF tying to the Grimes 345kV system and two 765kV line terminals. |  | IA |  |  | Conceptual | 110000000 | [5 empty] | Y | C
C | West | MEC | 2941 | 2010-09-21 |  | 5118 | 2010-12-01 | LN | 2014-12-31 | Sub T Fort Dodge | Boone Jct | 1 | 161 |  | 167 | Replace structures to increase operating temp | I8 | IA | 13.24 |  | Proposed | 1600000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2943 | 2010-09-01 | G0205 | 5120 | 2010-09-01 | TX | 2020-06-01 | Hills | Hills | 2 | 345 | 161 | 560 | Install 2nd 560 MVA 345-161 kV transformer at Hills Substation. Expand 345 and 161 kV ring busses to accommodate new transformer. | I8 | IA |  |  | Conceptual | 12000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2944 | 2010-09-01 | G0197 | 5121 | 2010-09-01 | LNrc | 2019-06-01 | Hills | Sub E | 1 | 161 |  | 410 | Reconductor the Hills - Sub E Iowa City 161 kV Line. | I8 | IA | 6.5 |  | Conceptual | 1800000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2945 | 2009-09-14 | G0126 | 5122 | 2009-09-14 | TX | 2019-06-01 | Grimes | Transformer | 2 | 345 | 161 | 560 | Add second transformer at Grimes | H8 | IA |  |  | Conceptual | 11900000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2946 | 2010-09-01 | G0124 | 5123 | 2010-09-01 | LNrc | 2018-06-01 | Greenfield Plaza | Army Post | 1 | 161 |  | 335 | Reconductor | H8 | IA | 5.25 |  | Proposed | 1200000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2947 | 2010-09-01 | T3204 | 5125 | 2010-09-01 | Dist | 2012-06-01 | North Grimes |  |  | 161 | 13.2 | 33 | New North Grimes 161-13 kV distribution sub | H8 | IA |  |  | Planned | 2700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2947 | 2010-09-01 | T3204 | 5126 | 2010-09-01 | TAP | 2012-06-01 | Granger | North Grimes | 1 | 161 |  | 410 | North Grimes Substation line tap | H8 | IA |  | 0.1 | Planned | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2947 | 2010-09-01 | T3204 | 5127 | 2010-09-01 | TAP | 2012-06-01 | North Grimes | Grimes Tap | 1 | 161 |  | 410 | North Grimes Substation line tap | H8 | IA |  | 0.1 | Planned | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2947 | 2010-09-01 | G0124 | 5124 | 2010-09-01 | LNrc | 2018-06-01 | Army Post | Ashawa | 1 | 161 |  | 335 | Reconductor | H8 | IA | 4.27 |  | Proposed | 1000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2948 | 2010-09-01 | T3228 | 5131 | 2010-09-01 | TAP | 2018-06-01 | W. Waukee Tap Structure | W. Waukee | 1 | 161 |  | 410 | Add 161 kV tap into and out of sub | H8 | IA |  | 0.2 | Proposed | 250000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2948 | 2010-09-01 | T3228 | 5133 | 2010-09-01 | CB | 2018-06-01 | Grimes |  |  | 161 |  |  | Add line terminal at Grimes | H8 | IA |  |  | Proposed | 700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2948 | 2010-09-01 | T3228 | 5128 | 2010-09-01 | Dist | 2018-06-01 | W. Waukee |  |  | 161 | 13.2 | 33 | Add W. Waukee distribution sub | H8 | IA |  |  | Proposed | 2700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2948 | 2010-09-01 | T3228 | 5134 | 2010-09-01 | CB | 2018-06-01 | Booneville |  |  | 161 |  |  | Add line terminal at Booneville | H8 | IA |  |  | Proposed | 700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2948 | 2010-09-01 | T3228 | 5129 | 2010-09-01 | LN | 2018-06-01 | Grimes | W. Waukee Tap Structure | 1 | 161 |  | 410 | Add Grimes-W Waukee 161 kV line | H8 | IA |  | 9.2 | Proposed | 3500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2948 | 2010-09-01 | T3228 | 5130 | 2010-09-01 | LN | 2018-06-01 | W. Waukee Tap Structure | Booneville | 1 | 161 |  | 410 | Add W Waukee-Booneville 161 kV line | H8 | IA |  | 7.4 | Proposed | 2800000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2949 | 2010-09-01 | T3344 | 5132 | 2010-09-01 | TX | 2020-06-01 | W. Waukee | 161/69 transformer | 1 | 161 | 69 |  | Add 161-69 kV transformer and 161 kV circuit breakers | H8 | IA |  |  | Conceptual | 3100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2950 | 2010-09-01 | T3211 | 5135 | 2010-09-01 | Dist | 2018-06-01 | Polk City |  |  | 161 | 13.2 | 33 | Add Polk City distribution sub | H8 | IA |  |  | Conceptual | 1500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2951 | 2009-09-14 | T3704 | 5140 | 2009-09-14 | LN | 2018-06-01 | Boston | Forest & Vermont | 1 | 161 |  | 410 | Boston Substation line tap | H8 | IA |  | 0.1 | Conceptual | 300000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2951 | 2009-09-14 | T3704 | 5138 | 2009-09-14 | SUB | 2018-06-01 | Boston |  |  | 161 | 13 | 33 | Add Boston distribution sub | H8 | IA |  |  | Conceptual | 1400000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2951 | 2009-09-14 | T3704 | 5139 | 2009-09-14 | LN | 2018-06-01 | Sycamore | Boston | 1 | 161 |  | 410 | Boston Substation line tap | H8 | IA |  | 0.1 | Conceptual | 300000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5147 | 2009-09-14 | TEQ | 2016-06-01 | D.M. Energy Center |  |  | 161 |  |  | Relay upgrade for Metro East line | H8 | IA |  |  | Conceptual | 100000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5146 | 2009-09-14 | TEQ | 2016-06-01 | Altoona |  |  | 161 |  |  | Relay upgrade for Metro East line | H8 | IA |  |  | Conceptual | 40000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5141 | 2009-09-14 | SUB | 2016-06-01 | East Altoona |  |  | 161 | 13 | 33 | Add E Altoona distribution sub | H8 | IA |  |  | Conceptual | 1400000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5142 | 2009-09-14 | LN | 2016-06-01 | Metro East | East Altoona | 1 | 161 |  | 410 | Add Metro E-E Altoona 161 kV line | H8 | IA |  | 7 | Conceptual | 4900000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5143 | 2009-09-14 | LN | 2016-06-01 | East Altoona | Bondurant | 1 | 161 |  | 410 | Add E Altoona-Bondurant 161 kV line | H8 | IA |  | 4 | Conceptual | 2900000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5144 | 2009-09-14 | CB | 2016-06-01 | Metro East |  |  | 161 |  |  | Add breakers at Metro E Substation | H8 | IA |  |  | Conceptual | 900000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2952 | 2009-09-14 | T3316 | 5145 | 2009-09-14 | CB | 2016-06-01 | Bondurant |  |  | 161 |  |  | Add breaker/line term at Bondurant | H8 | IA |  |  | Conceptual | 1100000 | Planning |  |  |  |  | Y | C
C | West | MEC | 2953 | 2010-09-01 | T2104 | 5151 | 2010-09-01 | LN | 2020-06-01 | Page County | Clarinda | 1 | 161 |  |  | Reconductor line | H9 | IA | 3 |  | Conceptual | 900000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2953 | 2010-09-01 | T2104 | 5148 | 2010-09-01 | TEQ | 2020-06-01 | Page County | Bus |  | 345 |  |  | 345 kV terminals for Page County Substation | H9 | IA |  |  | Conceptual | 1500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2953 | 2010-09-01 | T2104 | 5149 | 2010-09-01 | SUB | 2020-06-01 | Page County | Transformer | 1 | 345 | 161 |  | 345-161 kV transformer at new Page County Substation | H9 | IA |  |  | Conceptual | 15500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2953 | 2010-09-01 | T2104 | 5150 | 2010-09-01 | TEQ | 2020-06-01 | Page County | Bus |  | 161 |  |  | 161 kV terminals for Page County Substation | H9 | IA |  |  | Conceptual | 700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 2954 | 2010-09-01 | T2135 | 5152 | 2010-09-01 | CAP | 2018-06-01 | Clarinda | Capacitor |  | 161 |  |  | New capacitor | H9 | IA |  |  | Proposed | 1000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3217 | 2010-09-07 | MEC2011 C-1 | 6000 | 2010-09-07 | SUB | 2019-12-31 | Scott County |  |  | 765 |  |  | New 765 kV Substation in Iowa Quad Cities in Scott County, Iowa |  | IA | 0 | 0 | Proposed | 71000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3217 | 2010-09-07 | MEC2011 C-1 | 6001 | 2010-09-07 | LN | 2019-12-31 | Kewanee | Scott County | 1 | 765 |  | 7140 | New 765 kV line from Kewanee to Scott County and associated substation equipment additions. |  | IA/IL | 0 | 45 | Proposed | 122000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3218 | 2010-09-21 | MEC2011 C-2 | 6004 | 2010-09-07 | SUB | 2019-12-31 | Hazleton |  | 1 | 765 | 345 | 1200 | Expand Hazleton Substation to include 765 kV yard and 765-345 kV transformation |  | IA | 0 | 0 | Proposed | 66000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3219 | 2010-09-07 | MEC2011 C-3 | 6003 | 2010-09-07 | LN | 2019-12-31 | Kewanee | Louisa | 1 | 765 |  | 7140 | New 765 kV line from Kewanee to Louisa and associated substation equipment additions. |  | IA/IL | 0 | 80 | Proposed | 217000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3219 | 2010-09-07 | MEC2011 C-3 | 6002 | 2010-09-07 | SUB | 2019-12-31 | Louisa |  | 1 | 765 | 345 | 1200 | Expand Louisa Substation to include 765 kV yard and 765-345 kV transformation |  | IA | 0 | 0 | Proposed | 66000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3221 | 2010-09-21 | MEC2011 C-5 | 6007 | 2010-09-07 | SUB | 2019-12-31 | Pocahontas County |  |  | 765 | 345 |  | New 765-345 kV Substation in Pocahontas County, Iowa. Station includes two 765-345 kV transformers and taps the Raun-Lehigh 345 kV line |  | IA | 0 | 0 | Proposed | 92000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3221 | 2010-09-21 | MEC2011 C-5 | 6008 | 2010-09-07 | LN | 2019-12-31 | Pocahontas County | Hazleton | 1 | 765 |  | 3810 | New 765 kV line from Pocahontas County to Hazleton and associated substation equipment additions. |  | IA | 0 | 275 | Proposed | 745000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3224 | 2010-09-07 | MEC2011 C-8 | 6011 | 2010-09-07 | LN | 2019-12-31 | Woodbury County (Raun) | Hoskins |  | 345 |  |  | New double circuit 345 kV line from either Raun or new substation in Woodbury County to Hoskins and associated substation equipment additions. |  | IA/NE | 0 | 85 | Proposed | 167000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3225 | 2010-09-07 | MEC2011 C-9 | 6012 | 2010-09-07 | LN | 2019-12-31 | Woodbury County (Raun) | Broadland |  | 345 |  |  | New double circuit 345 kV line from either Raun or new substation in Woodbury County to Broadland and associated substation equipment additions. |  | IA/SD | 0 | 300 | Proposed | 591000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3226 | 2010-09-07 | MEC2011 C-10 | 6013 | 2010-09-07 | LN | 2024-12-31 | Pocahontas County | Woodbury County (Raun) | 1 | 765 |  | 4760 | New 765 kV line from Pocahontas County to Raun or new substation in Woodbury County and associated substation equipment additions. |  | IA | 0 | 85 | Proposed | 230000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3226 | 2010-09-07 | MEC2011 C-10 | 6014 | 2010-09-07 | SUB | 2024-12-31 | Woodbury County (Raun) |  | 1 | 765 | 345 | 1200 | New Substation in Woodbury County or Expansion of Raun Substation to include 765 kV yard and 765-345 kV transformation |  | IA | 0 | 0 | Proposed | 66000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3227 | 2010-09-07 | MEC2011 C-11 | 6015 | 2010-09-07 | LN | 2024-12-31 | Pocahontas County | Hoskins | 1 | 765 |  | 5300 | New 765 kV line from Pocahontas County to Hoskins and associated substation equipment additions. |  | IA/NE | 0 | 170 | Proposed | 461000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3228 | 2010-09-21 | MEC2011 C-12 | 6017 | 2010-09-07 | SUB | 2024-12-31 | Hills |  | 1 | 765 | 345 | 1200 | Expand Hills Substation to include 765 kV yard and 765-345 kV transformation |  | IA | 0 | 0 | Proposed | 66000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3229 | 2010-09-07 | MEC2011 C-13 | 6019 | 2010-09-07 | SUB | 2024-12-31 | Osceola County |  | 1 | 765 | 345 | 1200 | New 765-345 kV Substation in Osceola County, Iowa. Station includes one 765-345 kV transformer and taps the Raun-Lakefield Jct. 345 kV line |  | IA | 0 | 0 | Proposed | 71000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3229 | 2010-09-07 | MEC2011 C-13 | 6018 | 2010-09-07 | LN | 2029-12-31 | Pocahontas County | Osceola County | 1 | 765 |  | 4760 | New 765 kV line from Pocahontas County to Osceola County and associated substation equipment additions. |  | IA | 0 | 55 | Proposed | 149000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3230 | 2010-09-07 | MEC2011 C-14 | 6020 | 2010-09-07 | LN | 2029-12-31 | Osceola County | Chanarambie | 1 | 765 |  | 4760 | New 765 kV line from Osceola County to Chanarambie and associated substation equipment additions. |  | IA/MN | 0 | 135 | Proposed | 366000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3231 | 2010-09-07 | MEC2011 C-15 | 6021 | 2010-09-07 | LN | 2029-12-31 | Pocahontas County | Adair County | 1 | 765 |  | 4760 | New 765 kV line from Pocahontas County to Adair County and associated substation equipment additions. |  | IA | 0 | 150 | Proposed | 407000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3231 | 2010-09-07 | MEC2011 C-15 | 6022 | 2010-09-07 | SUB | 2029-12-31 | Adair County |  |  | 765 | 345 | 1200 | New 765-345 kV Substation in Adair County, Iowa. Station includes two 765-345 kV transformers and taps the Atchison County-Booneville and Council Bluffs-Madison County 345 kV lines near the crossing point of these two 345 kV circuits. |  | IA | 0 | 0 | Proposed | 92000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3232 | 2010-09-07 | MEC2011 C-16 | 6023 | 2010-09-07 | LN | 2029-12-31 | Adair County | St. Joe | 1 | 765 |  | 3810 | New 765 kV line from Adair County to St. Joe and associated substation equipment additions. |  | IA/MO | 0 | 150 | Proposed | 407000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3233 | 2010-09-07 | MEC2011 C-17 | 6024 | 2010-09-07 | LN | 2029-12-31 | Adair County | Hills | 1 | 765 |  | 2620 | New 765 kV line from Adair County to Hills and associated substation equipment additions. |  | IA | 0 | 255 | Proposed | 691000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3234 | 2010-09-07 | MEC2011 C-18 | 6025 | 2010-09-07 | LN | 2029-12-31 | Hills | Kincaid | 1 | 765 |  | 2380 | New 765 kV line from Hills to Kincaid and associated substation equipment additions. |  | IA/IL | 0 | 275 | Proposed | 745000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3237 | 2010-09-07 | MEC C-20 | 6031 | 2010-09-07 | LN | 2020-06-01 | Avoca 345-161 kV Sub | Page County Substation | 1 | 345 |  | 1700 | New 345 kV line from the Avoca 345--161 kV substation to the Page County Substation with 161 kV underbuild |  | IA | 0 | 70 | Conceptual | 125000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3237 | 2010-09-07 | MEC C-20 | 6030 | 2010-09-07 | LN | 2020-06-01 | Page County Substation | Maryville Substation | 1 | 345 |  | 1700 | New 345 kV line from the Page County substation to the Maryville Substation with 161 kV underbuild and associated substation equipment additions. |  | IA/MO | 0 | 35 | Conceptual | 63000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3237 | 2010-09-07 | MEC C-20 | 6029 | 2010-09-07 | SUB | 2020-06-01 | Page County Substation |  | 1 | 345 | 161 | 560 | Construct a new 345-161 kV substation and associated substation equipment on the Booneville-Atchison County 345 kV line and the Clarinda-Hastings 161 kV line |  | IA |  |  | Conceptual | 7500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3237 | 2010-09-07 | MEC C-20 | 6028 | 2010-09-07 | SUB | 2020-06-01 | Avoca Substation |  | 1 | 345 | 161 | 560 | Expand the Avoca Substation to add a 345 kV Yard and a 345-161 kV transformer and associated substation equipment additions. |  | IA |  |  | Conceptual | 7500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3238 | 2010-09-07 | MEC C-21 | 6032 | 2010-09-07 | LN | 2019-06-01 | CBEC | S3456 | 2 | 345 |  | 1700 | New 345 kV line from the CBEC substation to OPPD's S3456 substation and associated substation equipment additions. |  | IA/NE |  | 9.19 | Conceptual | 29100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3239 | 2010-09-07 | MEC C-22 | 6033 | 2010-09-07 | LN | 2018-06-01 | Bunge | Hastings | 1 | 161 |  | 410 | Rebuild the Bunge-Hastings 161 kV line and associated substation equipment additions. |  | IA | 21 | 0 | Conceptual | 11000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3239 | 2010-09-07 | MEC C-22 | 6034 | 2010-09-07 | LNrb | 2018-12-01 | Hastings | Clarinda | 1 | 161 |  | 410 | Rebuild the Hastings-Clarinda 161 kV line and associated substation equipment additions. |  | IA | 31.2 | 0 | Conceptual | 17200000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3239 | 2010-09-07 | MEC C-22 | 6035 | 2010-09-07 | LNrb | 2018-12-01 | Clarinda | Page County Substation | 1 | 161 |  | 410 | Rebuild the Clarinda-Page County 161 kV line and associated substation equipment additions. |  | IA | 2 | 0 | Conceptual | 900000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3240 | 2010-09-07 | MEC C-23 | 6036 | 2010-09-07 | LNrb | 2020-06-01 | Denison | Avoca | 1 | 161 |  | 410 | New 161 kV line from NIPCO's Denison substation to the Avoca Sub and associated substation equipment additions. |  | IA | 0 | 38 | Conceptual | 20900000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3241 | 2010-09-07 | MEC C-24 | 6037 | 2010-09-07 | LN | 2018-06-01 | CBEC | Sub 701 | 1 | 161 |  | 410 | New 161 kV line from CBEC substation to Sub 701 and associated substation equipment additions. |  | IA | 0 | 8.31 | Conceptual | 4600000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3242 | 2010-09-07 | MEC C-25 | 6038 | 2010-09-07 | LN | 2018-06-01 | Quick | Sub 701 | 1 | 161 |  | 410 | New 161 kV line from Quick substation to Sub 701 and associated substation equipment additions. |  | IA | 0 | 14 | Conceptual | 7700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3243 | 2010-09-07 | MEC C-26 | 6039 | 2010-09-07 | LN | 2016-06-01 | Quick | Avoca | 1 | 161 |  | 410 | New 161 kV line from the Quick substation to the Avoca substation and associated substation equipment additions. |  | IA | 0 | 21.3 | Conceptual | 11700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3244 | 2010-09-21 | MEC C-27 | 6044 | 2010-09-07 | SUB | 2017-06-01 | Pleasant Corner Substation |  |  | 161 |  |  | New 161 kV substation |  | IA |  |  | Conceptual | 3500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3244 | 2010-09-21 | MEC C-27 | 6042 | 2010-09-07 | LN | 2017-06-01 | Beacon | Pella | 1 | 161 |  | 410 | New 161 kV line from the Beacon substation to Pella and associated substation equipment additions. |  | IA | 0 | 18 | Conceptual | 9900000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3244 | 2010-09-21 | MEC C-27 | 6040 | 2010-09-07 | LN | 2017-06-01 | OGS | Pleasant Corner Substation | 1 | 161 |  | 410 | New 161 kV line from the OGS substation to the Pleasant Corner substation and associated substation equipment additions. |  | IA | 0 | 15 | Conceptual | 8250000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3244 | 2010-09-21 | MEC C-27 | 6041 | 2010-09-07 | LN | 2017-06-01 | Pleasant Corner Substation | Beacon | 1 | 161 |  | 410 | New 161 kV line from the Pleasant Corner substation-Beacon substation and associated substation equipment additions. |  | IA | 0 | 11 | Conceptual | 6000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3245 | 2010-09-21 | MEC C-28 | 6046 | 2010-09-07 | LN | 2017-06-01 | Knoxville | Pella | 1 | 161 |  | 410 | New 161 kV line from the Knoxville substation to Pella and associated substation equipment additions. |  | IA | 0 | 14 | Conceptual | 7700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3246 | 2010-09-07 | MEC C-29 | 6065 | 2010-09-07 | LN | 2016-06-01 | Webster South | Lehigh | 1 | 161 |  | 410 | Webster South-Lehigh 161 kV Line |  | IA | 0 | 6.9 | Conceptual | 3500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3247 | 2010-09-07 | MEC C-30 | 6066 | 2010-09-07 | TX | 2016-06-01 | Lehigh | Lehigh |  | 345 | 161 | 560 | Lehigh 345-161 kV transformer |  | IA | 0 | 0 | Conceptual | 7500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3248 | 2010-09-21 | MEC C-31 | 6050 | 2010-09-07 | LN | 2016-06-01 | DPS | DPS-Reasnor Switching Station | 1 | 161 |  | 325 | Bisect existing DPS-Reasnor 161 kV line and associated substation equipment additions. |  | IA |  | 0.1 | Conceptual | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3248 | 2010-09-21 | MEC C-31 | 6049 | 2010-09-07 | SwSt | 2016-06-01 | DPS-Reasnor Switching Station |  |  | 161 |  |  | New 161 kV breakered switching station off the DPS-Reasnor 161 kV line |  | IA |  |  | Conceptual | 3000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3248 | 2010-09-21 | MEC C-31 | 6048 | 2010-09-07 | LN | 2016-06-01 | DPS-Reasnor Switching Station | East Altoona | 1 | 161 |  | 410 | New 161 kV line from switching station on DPS-Reasnor line to East Altoona and associated substation equipment additions. |  | IA | 0 | 6 | Conceptual | 3300000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3250 | 2010-09-07 | MEC C-33 | 6056 | 2010-09-07 | LN | 2018-06-01 | West Grand | 88th St | 1 | 161 |  | 410 | West Grand-88th St 161 kV Line and associated substation equipment additions. |  | IA | 0 | 3.3 | Conceptual | 1800000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3251 | 2010-09-07 | MEC C-34 | 6057 | 2010-09-07 | LN | 2018-06-01 | Army Post | West Grand | 1 | 161 |  | 410 | Army Post-West Grand 161 kV Line and associated substation equipment additions. |  | IA | 0 | 8 | Conceptual | 4400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3252 | 2010-09-07 | MEC C-35 | 6058 | 2010-09-07 | LN | 2020-06-01 | Norwalk | Scotch Ridge | 1 | 161 |  | 410 | Norwalk-Scotch Ridge 161 kV Line and associated substation equipment additions. |  | IA | 0 | 8 | Conceptual | 4400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3252 | 2010-09-07 | MEC C-35 | 6059 | 2010-09-07 | Dist | 2020-06-01 | Scotch Ridge |  |  | 161 | 13.2 | 33 | New 161 kV distribution substation |  | IA |  |  | Conceptual | 2700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3253 | 2010-09-07 | MEC C-36 | 6061 | 2010-09-07 | Dist | 2020-06-01 | Avon Lake |  |  | 161 | 13.2 | 33 | New 161 kV distribution substation and associated substation equipment additions. |  | IA |  |  | Conceptual | 2700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3253 | 2010-09-07 | MEC C-36 | 6060 | 2010-09-07 | LN | 2020-06-01 | Scotch Ridge | Avon Lake | 1 | 161 |  | 410 | Scotch Ridge-Avon Lake 161 kV Line and associated substation equipment additions. |  | IA | 0 | 5.5 | Conceptual | 3000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3254 | 2010-09-07 | MEC C-37 | 6062 | 2010-09-07 | LN | 2020-06-01 | Avon Lake | SE Polk | 1 | 161 |  | 410 | Avon Lake-SE Polk 161 kV Line and associated substation equipment additions. |  | IA | 0 | 2.5 | Conceptual | 1400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3255 | 2010-09-07 | MEC C-38 | 6063 | 2010-09-07 | LN | 2015-06-01 | Sub 91 | Cordova | 1 | 345 |  | 1738 | Sub 91-Cordova 345 kV Line and associated substation equipment additions. |  | IA/IL |  | 18 | Conceptual | 23400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3256 | 2010-09-07 | MEC C-39 | 6064 | 2010-09-07 | LN | 2015-06-01 | Sub 39 | Cordova | 1 | 345 |  | 1738 | Sub 39-Cordova 345 kV Line and associated substation equipment additions. |  | IL |  | 16 | Conceptual | 20800000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3257 | 2010-09-07 | MEC C-40 | 6081 | 2010-09-07 | LN | 2016-06-01 | LeMars | Sioux County | 1 | 161 |  | 410 | New 161 kV line from a new LeMars substation to a new Sioux Co substation |  | IA | 0 | 24 | Conceptual | 13200000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3257 | 2010-09-07 | MEC C-40 | 6084 | 2010-09-07 | SUB | 2016-06-01 | Sioux County Substation |  |  | 161 |  |  | New 161 kV substation |  | IA |  |  | Conceptual | 3500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3257 | 2010-09-07 | MEC C-40 | 6083 | 2010-09-07 | LN | 2016-06-01 | Spencer | Sioux County | 1 | 161 |  | 410 | New 161 kV line from the Spencer substation to a new Sioux Co. substation |  | IA | 0 | 50 | Conceptual | 27500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3257 | 2010-09-07 | MEC C-40 | 6082 | 2010-09-07 | LN | 2016-06-01 | Eagle | Sioux County | 1 | 161 |  | 410 | New 161 kV line from the Eagle substation to a new Sioux Co. substation |  | IA | 0 | 18 | Conceptual | 9900000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3258 | 2010-09-07 | MEC C-41 | 6067 | 2010-09-07 | LN | 2020-06-01 | Little Sioux | Monona | 1 | 161 |  | 410 | Little Sioux-Monona 161 kV line |  | IA | 0 | 34 | Conceptual | 18700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3259 | 2010-09-07 | MEC C-42 | 6068 | 2010-09-07 | LN | 2020-06-01 | Carroll | Denison | 1 | 161 |  | 410 | Carroll-Denison 161 kV line |  | IA | 0 | 30 | Conceptual | 16500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3260 | 2010-09-07 | MEC C-43 | 6069 | 2010-09-07 | LN | 2020-06-01 | Odebolt | Carroll | 1 | 161 |  | 410 | Odebolt-Carroll 161 kV line |  | IA | 20 | 16 | Conceptual | 18000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3260 | 2010-09-07 | MEC C-43 | 6070 | 2010-09-07 | LN | 2020-06-01 | Odebolt | Carroll | 1 | 345 |  | 1700 | Odebolt-Carroll 345 kV line |  | IA | 0 | 36 | Conceptual | 39000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3261 | 2010-09-07 | MEC C-44 | 6071 | 2010-09-07 | LN | 2020-06-01 | Wisdom | Buena Vista | 1 | 345 |  | 1700 | Wisdom-Buena Vista 345 kV line |  | IA | 0 | 20 | Conceptual | 26000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3261 | 2010-09-07 | MEC C-44 | 6073 | 2010-09-07 | LN | 2020-06-01 | Sac County | Odebolt | 1 | 345 |  | 1700 | Sac County-Odebolt 345 kV line |  | IA | 0 | 17 | Conceptual | 22100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3261 | 2010-09-07 | MEC C-44 | 6072 | 2010-09-07 | LN | 2020-06-01 | Buena Vista | Sac County | 1 | 345 |  | 1700 | Buena Vista-Sac County 345 kV line |  | IA | 0 | 24 | Conceptual | 31200000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3262 | 2010-09-21 | MEC C-45 | 6074 | 2010-09-07 | LN | 2020-06-01 | Odebolt | Grand Junction | 1 | 345 |  | 1700 | Odebolt-Grand Junction 345 kV line |  | IA | 0 | 68 | Conceptual | 88400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3265 | 2010-09-21 | MEC C-48 | 6079 | 2010-09-07 | LN | 2020-06-01 | Carroll | Grand Junction | 1 | 161 |  | 410 | Carroll-Grand Junction 161 kV line |  | IA | 32 | 0 | Conceptual | 16000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3267 | 2010-09-07 | T7018 | 6086 | 2010-09-07 | TX | 2016-06-01 | NW Sioux City |  |  | 230 | 69 | 150 | NW Sioux City 230-69 kV Sub |  | IA |  |  | Conceptual | 10000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3267 | 2010-09-07 | T7018 | 6087 | 2010-09-07 | LN | 2016-06-01 | NW Sioux City | TWIN CH4 230.00 | 1 | 230 |  | 319 | Bisect existing 230 kV line |  | IA |  | 0.1 | Conceptual | 250000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3267 | 2010-09-07 | T7018 | 6088 | 2010-09-07 | LN | 2016-06-01 | NW Sioux City | Sioux City | 1 | 230 |  | 319 | Bisect existing 230 kV line |  | IA |  | 0.1 | Conceptual | 250000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3269 | 2011-02-15 | G1458 | 6092 | 2010-09-07 | LNrb | 2012-06-01 | Black Hawk | Hazleton |  | 161 |  | 410 | Blackhawk-Hazleton 161 kV Rebuild (MEC Section) |  | IA | 11.8 |  | Planned | 3400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3371 | 2010-09-15 | MEC C-49 | 6242 | 2010-09-15 | LN | 2014-12-31 | Hills | Parnell | 1 | 161 |  | 278 | Replace structures to increase operating temp. |  | IA |  |  | Proposed | 90000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3372 | 2010-09-15 | MEC C-50 | 6243 | 2010-09-15 | LN | 2014-12-31 | Parnell | Poweshiek | 1 | 161 |  | 289 | Replace structures to increase operating temp. |  | IA |  |  | Proposed | 540000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC | 3477 | 2011-02-15 | MEC C-52 | 6420 | 2011-08-25 | LN | 2014-12-01 | Oak Grove | Galesburg | 1 | 161 | 138 | 410 | Rebuild Oak Grove - Galesburg 161 kV line |  | IL | 32 |  | Proposed |  | Planning 2011$ |  |  |  |  | Y | C
C | West | MEC | 3478 | 2011-02-15 | MEC C-51 | 6421 | 2011-02-15 | LNup | 2018-12-31 | Webster | Wright | 1 | 161 |  | 410 | Rebuild Webster-Wright 161 kV line. |  | IA | 11.77 |  | Planned | 6768000 | Planning 2011$ |  |  |  |  | Y | C
C | West | MEC | 3478 | 2011-02-15 | MEC C-51 | 6422 | 2011-02-15 | LNup | 2018-12-31 | Wright | Wall Lake | 1 | 161 |  | 410 | Rebuild Wright-Wall Lake 161 kV. |  | IA | 11.65 |  | Planned | 6700000 | Planning 2011$ |  |  |  |  | Y | C
C | West | MEC | 3478 | 2011-02-15 | MEC C-51 | 6423 | 2011-02-15 | LNup | 2018-12-31 | Wall Lake | Franklin | 1 | 161 |  | 410 | Rebuild Wall Lake-Franklin 161 kV line. |  | IA | 17.76 |  | Planned | 10212000 | Planning 2011$ |  |  |  |  | Y | C
C | West | MEC, ALTW | 2193 | 2008-08-05 | 13 | 4043 | 2008-08-05 | LN | 2018-08-01 | Lehigh | Toledo | 1 | 765 |  | 4008 | new line |  | IA |  | 97 | Conceptual | 313000000 | [5 empty] | Y | C
C | West | MEC, ITCM | 3218 | 2010-09-21 | MEC2011 C-2 | 6005 | 2010-09-21 | LN | 2019-12-31 | Scott County | Hazleton | 1 | 765 |  | 4760 | New 765 kV line from Scott County to Hazleton and associated substation equipment additions. |  | IA | 0 | 145 | Proposed | 393000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3220 | 2010-09-21 | MEC2011 C-4 | 6006 | 2010-09-21 | LN | 2019-12-31 | Louisa | Hazleton | 1 | 765 |  | 4760 | New 765 kV line from Louisa to Hazleton and associated substation equipment additions. |  | IA | 0 | 95 | Proposed | 257000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3222 | 2010-09-21 | MEC2011 C-6 | 6009 | 2010-09-21 | LN | 2019-12-31 | Hills | Hazleton | 2 | 345 |  | 1700 | New 345 kV line from Hills to Hazleton and associated substation equipment additions. |  | IA | 0 | 55 | Proposed | 83000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3223 | 2010-09-21 | MEC2011 C-7 | 6010 | 2010-09-21 | LN | 2019-12-31 | Hazleton | Adams |  | 345 |  |  | New double circuit 345 kV line from Hazleton to Adams and associated substation equipment additions. |  | IA/MN | 0 | 115 | Proposed | 227000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3228 | 2010-09-21 | MEC2011 C-12 | 6016 | 2010-09-21 | LN | 2024-12-31 | Hills | Hazleton | 1 | 765 |  | 4760 | New 765 kV line from Hills to Hazleton and associated substation equipment additions. |  | IA | 0 | 55 | Proposed | 149000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3235 | 2010-09-21 | MEC2011 C-19 | 6026 | 2010-09-21 | LN | 2029-12-31 | Osceola County | Lakefield Jct. | 1 | 765 |  | 4760 | New 765 kV line from Osceola County to Lakefield Jct. and associated substation equipment additions. |  | IA/MN | 0 | 85 | Proposed | 230000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3236 | 2010-09-21 | MEC2011 C-20 | 6027 | 2010-09-21 | LN | 2029-12-31 | Hazleton | Adams | 1 | 765 |  | 4760 | New 765 kV line from Hazleton to Adams and associated substation equipment additions. |  | IA/MN | 0 | 115 | Proposed | 312000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3244 | 2010-09-21 | MEC C-27 | 6043 | 2010-09-21 | LN | 2017-06-01 | Pella | Reasnor Switching Station | 1 | 161 |  | 410 | New 161 kV line from Pella to Reasnor Switching Station with 69 kV underbuild |  | IA | 0 | 20 | Conceptual | 11000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3245 | 2010-09-21 | MEC C-28 | 6045 | 2010-09-21 | LN | 2017-06-01 | Lucas County | Knoxville | 1 | 161 |  | 410 | New 161 kV line from Lucas County Substation to the Knoxville Substation and associated substation equipment additions. |  | IA | 0 | 28 | Conceptual | 15400000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3245 | 2010-09-21 | MEC C-28 | 6047 | 2010-09-21 | LN | 2017-06-01 | Pella | Reasnor Switching Station | 1 | 161 |  | 410 | New 161 kV line from Pella to Reasnor Switching Station and associated substation equipment additions. |  | IA | 0 | 20 | Conceptual | 11000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3248 | 2010-09-21 | MEC C-31 | 6051 | 2010-09-21 | LN | 2016-06-01 | DPS-Reasnor Switching Station | Reasnor Switching Station | 1 | 161 |  | 325 | Bisect existing DPS-Reasnor 161 kV line and associated substation equipment additions. |  | IA |  | 0.1 | Conceptual | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3249 | 2010-09-21 | MEC C-32 | 6053 | 2010-09-21 | SwSt | 2016-06-01 | NE Ankeny/Jasper County Sub |  |  | 161 |  |  | New 161 kV breakered switching station off the NE Ankeny-Jasper 161 kV line. |  | IA |  |  | Conceptual | 3000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3249 | 2010-09-21 | MEC C-32 | 6054 | 2010-09-21 | LN | 2016-06-01 | NE Ankeny | NE Ankeny/Jasper County Sub | 1 | 161 |  | 240 | Bisect existing NE Ankeny-Jasper County 161 kV line and associated substation equipment additions. |  | IA |  | 0.1 | Conceptual | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3249 | 2010-09-21 | MEC C-32 | 6055 | 2010-09-21 | LN | 2016-06-01 | NE Ankeny/Jasper County Sub | Jasper County | 1 | 161 |  | 240 | Bisect existing NE Ankeny-Jasper County 161 kV line and associated substation equipment additions. |  | IA |  | 0.1 | Conceptual | 100000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3249 | 2010-09-21 | MEC C-32 | 6052 | 2010-09-21 | LN | 2016-06-01 | East Altoona | NE Ankeny/Jasper County Sub | 1 | 161 |  | 410 | New 161 kV line from East Altoona to a new sub off NE Ankeny/Jasper County line and associated substation equipment additions. |  | IA | 0 | 8.3 | Conceptual | 4600000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3262 | 2010-09-21 | MEC C-45 | 6075 | 2010-09-21 | LN | 2020-06-01 | Grand Junction | Adair County | 1 | 345 |  | 1700 | Grand Junction-Adair County 345 kV line |  | IA | 0 | 89 | Conceptual | 115700000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3263 | 2010-09-21 | MEC C-46 | 6078 | 2010-09-21 | LN | 2020-06-01 | Ottumwa | Sub T | 1 | 345 |  | 1700 | Ottumwa-Sub T 345 kV line |  | IA | 0 | 70 | Conceptual | 100500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3263 | 2010-09-21 | MEC C-46 | 6076 | 2010-09-21 | LN | 2020-06-01 | Adair County | Ottumwa | 1 | 345 |  | 1700 | Adair-Ottumwa 345 kV line |  | IA | 0 | 100 | Conceptual | 143500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3264 | 2010-09-21 | MEC C-47 | 6077 | 2010-09-21 | LN | 2020-06-01 | S.E. Polk | Ottumwa | 1 | 161 |  | 410 | S.E. Polk-Ottumwa 161 kV line |  | IA | 0 | 80 | Conceptual | 40000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MEC, ITCM | 3265 | 2010-09-21 | MEC C-48 | 6080 | 2010-09-21 | LN | 2020-06-01 | Grand Junction | Adair County | 1 | 161 |  | 410 | Grand Junction-Adair County 161 kV line |  | IA | 0 | 89 | Conceptual | 44500000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MH | 3398 | 2010-09-15 | Option W6 | 6273 | 2010-09-15 | LN | 2017-12-31 | Dorsey | US/MB Border | 1 | 500 |  | 1732 | Dorsey-US/Manitoba Border 500 kV line |  | MB | 80 | 80 | Proposed | 204000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | MH, OTP | 2180 | 2011-07-01 | 27 | 4055 | 2011-07-01 | TX | 2018-08-01 | Maple River | Transformer | 1 | 500 | 230 | 1200 | new transformer |  | ND |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | West | MH, OTP | 2180 | 2011-07-01 | 1 | 4031 | 2011-07-01 | LN | 2018-08-01 | Riel | Maple River | 1 | 500 |  | 2673 | new line |  | Manitoba/ND |  | 203 | Conceptual | 344000000 | [5 empty] | Y | C
C | West | MH, OTP | 2180 | 2011-07-01 | 26 | 4054 | 2011-07-01 | TX | 2018-08-01 | Riel | Transformer | 1 | 500 | 115 | 430 | new transformer |  | Manitoba |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | West | MISO TSR | 3085 | 2009-09-15 | MISO TSR | 5375 | 2009-09-15 | TX | 2017-06-01 | Helena 500kV | Helena 345kV | 2 | 500 | 345 | 1200 | New transformer |  | MN |  |  | Proposed | 60000000 | Planning |  |  |  |  | Y | C
C | West | MISO TSR | 3085 | 2009-09-15 | MISO TSR | 5374 | 2009-09-15 | TX | 2017-06-01 | Helena 500kV | Helena 345kV | 1 | 500 | 345 | 1200 | New transformer |  | MN |  |  | Proposed | 60000000 | Planning |  |  |  |  | Y | C
C | West | MISO TSR | 3085 | 2009-09-15 | MISO TSR | 5373 | 2009-09-15 | LN | 2017-06-01 | Maple River 500kV | Helena 500kV | 1 | 500 |  | 1732 | New 500kV line Maple River to Helena |  | MN |  | 200 | Proposed | 500000000 | Planning |  |  |  |  | Y | C
C | West | MISO TSR | 3085 | 2009-09-15 | MISO TSR | 5372 | 2009-09-15 | TX | 2017-06-01 | Maple River 500kV | Maple River, 345kV | 1 | 500 | 345 | 1200 | New transformer |  | MN |  |  | Proposed | 60000000 | Planning |  |  |  |  | Y | C
C | West | MISO TSR | 3085 | 2009-09-15 | MISO TSR | 5371 | 2009-09-15 | LN | 2017-06-01 | Dorsey 500kV, Manitoba | Maple River 500kV, MN | 1 | 500 |  | 1732 | New 500kV line from Dorsey to Maple River |  | MN |  | 200 | Proposed | 500000000 | Planning |  |  |  |  | Y | C
C | West | MP | 2548 | 2009-11-13 | Hilltop | 4565 | 2009-12-08 | LN | 2019-06-01 | Hilltop | Arrowhead |  | 230 |  | 470 | Upgrade 115 kV line to 230 kV |  | MN | 10 |  | Proposed |  |  | Network |  | y |  | y | C
C | West | MP | 2548 | 2009-11-13 | Hilltop | 4564 | 2009-12-08 | SUB | 2019-06-01 | Hilltop | Substation Equipment |  | 230 | 115 | 366 | Add second 183 MVA 230/115 kV Transformer |  | MN |  |  | Proposed |  |  | Network |  | y |  | y | C
C | West | MP | 2551 | 2011-09-06 | 28L Tap | 4562 | 2011-09-06 | LN | 2014-06-30 | Boswell | Deer River | 1 | 115 |  |  | Move 28L Tap to it own Breaker |  | MN |  | 0.5 | Proposed | 1250000 | [5 empty] | Y | C
C | West | MP | 2551 | 2011-09-06 | 28L Tap | 4563 | 2011-09-06 | SUB | 2014-06-30 | Boswell | Substation Equipment | 1 | 115 |  |  | 115 kV Line entrance |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | MP | 2551 | 2011-09-06 | 28L tap | 6590 | 2011-09-06 | LNup | 2014-06-30 | Boswell | Deer River | 1 | 115 |  | 182 | rebuild to higher capacity |  | MN | 8 | 0 | proposed | [6 empty] | Y | C
C | West | Non-MISO | 2773 | 2010-05-08 | GPE | 4842 | 2009-08-14 | SUB | 2020-12-31 | Fort Thompson | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new two TRF 765/345kV substation in SD. Substation will have two 765/345kV TRFs tying to the Fort Thompson 345kV system and three 765kV line terminals. |  | SD |  |  | Conceptual | 205000000 | [5 empty] | Y | C
C | West | Non-MISO | 2773 | 2010-05-08 | GPE | 4851 | 2009-08-14 | SUB | 2020-12-31 | Plano | Line tap and terminal equipment | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765kV tap & associated 765kV terminal equipment into the Plano substation in IL |  | IL |  |  | Conceptual | 5000000 | [5 empty] | Y | C
C | West | Non-MISO | 2773 | 2010-05-08 | GPE | 4840 | 2009-08-14 | SUB | 2020-12-31 | Antelope Valley | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in ND. Substation will have a single 765/345kV TRF tying to the Antelope Valley 345kV system and a single 765kV line terminal. |  | ND |  |  | Conceptual | 85000000 | [5 empty] | Y | C
C | West | Non-MISO | 2773 | 2010-05-08 | GPE | 4852 | 2009-08-14 | SUB | 2020-12-31 | Sullivan | Line tap and terminal equipment | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765kV tap & associated 765kV terminal equipment into the AEP Sullivan substation in IN. |  | IN |  |  | Conceptual | 5000000 | [5 empty] | Y | C
C | West | OTP | 2746 | 2010-01-06 | Turtle Lake-Mercer 41.6 kV Line Upgrade | 4769 | 2009-12-23 | LN | 2015-11-01 | Turtle Lake 41.6 kV | Mercer 41.6 kV |  | 41.6 |  | 30 MVA | Rebuild Existing 18-Mile 41.6 kV Line |  | ND |  |  | Proposed | 500000 | Proposed |  |  |  |  | NT | C
C | West | OTP | 2773 | 2010-05-08 | GPE | 4841 | 2009-11-18 | SUB | 2020-12-31 | North Dakota new substation | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in ND. Substation will have a single 765/345kV TRF and three 765kV line terminals. |  | ND |  |  | Conceptual | 120000000 | [5 empty] | Y | C
C | West | OTP | 2857 | 2010-09-28 | Green Valley 41.6 kV Line Upgrade | 5010 | 2010-11-04 | LN | 2014-12-31 | Green Valley 41.6 kV | Marshall 41.6 kV |  | 41.6 |  | 34 MVA | Rebuild Existing 4-Mile 41.6 kV Line |  | MN |  |  | Proposed | 550000 | Proposed |  |  |  |  | Y | C
C | West | OTP | 3484 | 2011-02-24 | Big Stone AQCS Addition | 6441 | 2011-02-24 | TX | 2015-07-01 | Big Stone 230 kV | Big Stone 13.8 kV | 1 | 230 | 13.8 | 50 MVA | Install a new 230/13.8 kV transformer to accommodate a new load increase at Big Stone related to new pollution control equipment |  | SD |  |  | Proposed | 3000000 | Planning |  |  |  |  | Y | C
C | West | OTP | 3513 | 2011-06-07 | CAPX Fargo-Alex-Monti | 6492 | 40701 | TX | 2015-03-31 | Bison | 345/230 transformer | 2 | 345 | 230 | 336 | new transformer and terminal works |  | ND |  |  | Planned | 8817500 | Engineering |  |  |  |  | Y | C
C | West | OTP | 3513 | 2011-06-07 | CAPX Fargo-Alex-Monti | 6491 | 40701 | TX | 2015-03-31 | Bison | 345/230 transformer | 1 | 345 | 230 | 336 | new transformer and terminal works |  | ND |  |  | Planned | 8817500 | Engineering |  |  |  |  | Y | C
C | West | OTP, GRE | 2225 | 2011-07-01 | 75 | 4099 | 2011-07-01 | LN | 2018-08-01 | Willmar | Big Stone | 1 | 345 |  | 972 | new line |  | MN/SD |  | 75 | Conceptual | 159000000 | [5 empty] | Y | C
C | West | OTP, GRE | 2225 | 2011-07-01 |  | 4101 | 2011-07-01 | LN | 2018-08-01 | Crow River | Big Swan | 1 | 345 |  | 1000 | new line |  | MN |  | 25.3 | Conceptual | 54000000 | [5 empty] | Y | C
C | West | OTP, GRE | 2225 | 2011-07-01 |  | 4131 | 2011-07-01 | TX | 2018-08-01 | Willmar | Transformer | 1 | 345 | 230 | 336 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | OTP, GRE | 2225 | 2011-07-01 |  | 4133 | 2011-07-01 | TX | 2018-08-01 | Crow River | Transformer | 1 | 345 | 115 | 448 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | OTP, GRE | 2225 | 2011-07-01 |  | 4132 | 2011-07-01 | TX | 2018-08-01 | Big Swan | Transformer | 1 | 345 | 115 | 448 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | OTP, GRE | 2225 | 2011-07-01 | 76 | 4100 | 2011-07-01 | LN | 2018-08-01 | Big Swan | Willmar | 1 | 345 |  | 1000 | new line |  | MN |  | 40 | Conceptual | 85000000 | [5 empty] | Y | C
C | West | OTP, MDU | 2219 | 2011-07-01 |  | 4115 | 2011-07-01 | TX | 2018-08-01 | Ellendale | Transformer | 1 | 345 | 230 | 336 | new transformer |  | ND |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | OTP, MDU | 2219 | 2011-07-01 | 64 | 4091 | 2011-07-01 | LN | 2018-08-01 | Ellendale | Maple River | 1 | 345 |  | 740 | new line |  | ND |  | 103 | Conceptual | 229000000 | [5 empty] | Y | C
C | West | OTP, NON-MISO | 2182 | 2011-07-01 | 56 | 4083 | 2011-07-01 | LN | 2018-08-01 | Maple River | Watertown | 1 | 345 |  | 600 | new line |  | ND/SD |  | 142 | Conceptual | 202000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2181 | 2011-07-01 | 2 | 4032 | 2011-07-01 | LN | 2018-08-01 | Maple River | Blue Lake | 1 | 500 |  | 1540 | new line |  | SD/MN |  | 222 | Conceptual | 381000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2181 | 2011-07-01 | 28 | 4056 | 2011-07-01 | TX | 2018-08-01 | Blue Lake | Transformer | 1 | 500 | 345 | 2000 | new transformer |  | MN |  |  | Conceptual | 20000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2224 | 2011-07-01 |  | 4129 | 2011-07-01 | TX | 2018-08-01 | Morris | Transformer | 1 | 345 | 230 | 336 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2224 | 2011-07-01 | 74 | 4098 | 2011-07-01 | LN | 2018-08-01 | Morris | Johnson Junction | 1 | 345 |  | 1000 | new line |  | MN |  | 16 | Conceptual | 34000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2224 | 2011-07-01 |  | 4128 | 2011-07-01 | LN | 2018-08-01 | Morris | Alexandria | 1 | 345 |  | 1000 | new line |  | MN |  | 44 | Conceptual | 93000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2224 | 2011-07-01 | 72 | 4097 | 2011-07-01 | LN | 2018-08-01 | Johnson Junction | Big Stone | 1 | 345 |  | 1000 | new line |  | SD\MN |  | 32 | Conceptual | 68000000 | [5 empty] | Y | C
C | West | OTP, XEL | 2224 | 2011-07-01 |  | 4130 | 2011-07-01 | TX | 2018-08-01 | Johnson Junction | Transformer | 1 | 345 | 230 | 336 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | OTP, XEL | 3204 | 2011-06-23 | Sheyenne - Audubon 230 kV line | 5950 | 2011-06-23 | LN | 2015-12-31 | Sheyenne 230 kV | Audubon 230 kV | 1 | 230 |  | 350 MVA | Upgrade Existing 230 kV line for Maple River Wind Interconnection by replacing structures to increase operating temperature of line. |  | ND/MN | 44 |  | Planned | 6000000 | Planning |  |  |  |  | Y | C
C | West | XEL | 2177 | 2008-06-30 | 230 kV Corridor | 4019 | 2008-06-30 | LN | 2016-06-01 | West Waconia | Blue Lake | 1 | 345 |  | 2066 MVA | Upgrade McLeod - Blue Lake 230 kV line to double circuit 345 kV with a step down to 115 kV at WestWaconia. |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | XEL | 2177 | 2008-06-30 | 230 kV Corridor | 4020 | 2008-06-30 | TX | 2016-06-01 | West Waconia | transformer | 1 | 345 | 115 | 448 MVA | 345/115 kV transformer at West Waconia |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | XEL | 2177 | 2008-06-30 | 230 kV Corridor | 4018 | 2008-06-30 | LN | 2016-06-01 | McLeod | Blue Lake | 2 | 345 |  | 2066 MVA | Upgrade McLeod - Blue Lake 230 kV line to double circuit 345 kV with a step down to 115 kV at WestWaconia. |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | XEL | 2177 | 2008-06-30 | 230 kV Corridor | 4017 | 2008-06-30 | LN | 2016-06-01 | McLeod | West Waconia | 1 | 345 |  | 2066 MVA | Upgrade McLeod - Blue Lake 230 kV line to double circuit 345 kV with a step down to 115 kV at WestWaconia. |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | XEL | 2177 | 2008-06-30 | 230 kV Corridor | 4016 | 2008-06-30 | LN | 2016-06-01 | Hazel | McLeod | 2 | 345 |  | 2066 MVA | Upgrade Minn Valley - McLeod 230 kV line to double circuit 345 kV |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | XEL | 2177 | 2008-06-30 | 230 kV Corridor | 4015 | 2008-06-30 | LN | 2016-06-01 | Hazel | McLeod | 1 | 345 |  | 2066 MVA | Upgrade Minn Valley - McLeod 230 kV line to double circuit 345 kV |  | MN |  |  | Proposed | [6 empty] | Y | C
C | West | XEL | 2184 | 2008-08-05 | 24 | 4052 | 2008-08-05 | TX | 2018-08-01 | Blue Earth | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | MN |  |  | Conceptual | 20000000 | [5 empty] | Y | C
C | West | XEL | 2184 | 2008-08-05 | 51 | 4078 | 2008-08-05 | LN | 2018-08-01 | Blue Earth | Split Rock | 1 | 345 |  | 628 | new line |  | SD/MN |  | 130 | Conceptual | 185000000 | [5 empty] | Y | C
C | West | XEL | 2185 | 2008-08-05 | 31 | 4058 | 2008-08-05 | TX | 2018-08-01 | Adams | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | MN |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | West | XEL | 2186 | 2008-08-05 | 58 | 4085 | 2008-08-05 | LN | 2018-08-01 | Sherbourne County | Chisago County | 1 | 345 |  | 1000 | new line |  | MN |  | 48.4 | Conceptual | 69000000 | [5 empty] | Y | C
C | West | XEL | 2187 | 2008-08-05 | 52 | 4079 | 2008-08-05 | LN | 2018-08-01 | SW Minneapolis | Sherbourne County | 1 | 345 |  | 1000 | new line |  | MN |  | 47.9 | Conceptual | 68000000 | [5 empty] | Y | C
C | West | XEL | 2188 | 2008-08-05 | 5 | 4035 | 2008-08-05 | LN | 2018-08-01 | SW Minneapolis | Hampton Corner | 1 | 765 |  | 4008 | new line |  | MN |  | 93 | Conceptual | 260000000 | [5 empty] | Y | C
C | West | XEL | 2189 | 2008-08-05 | 59 | 4086 | 2008-08-05 | LN | 2018-08-01 | Hampton Corner | Chisago County | 1 | 345 |  | 972 | new line |  | MN |  | 72.2 | Conceptual | 103000000 | [5 empty] | Y | C
C | West | XEL | 2191 | 2008-08-05 | 6 | 4036 | 2008-08-05 | LN | 2018-08-01 | SW Minneapolis | Blue Earth | 1 | 765 |  | 4776 | new line |  | MN |  | 73 | Conceptual | 215000000 | [5 empty] | Y | C
C | West | XEL | 2217 | 2008-08-05 |  | 4110 | 2008-08-05 | LN | 2018-08-01 | West Waconia | Blue Lake | 2 | 345 |  | 2066 | new line |  | MN |  | 20 | Conceptual | 25000000 | [5 empty] | Y | C
C | West | XEL | 2217 | 2008-08-05 |  | 4109 | 2008-08-05 | LN | 2018-08-01 | West Waconia | Blue Lake | 1 | 345 |  | 2066 | new line |  | MN |  | 20 | Conceptual | 25000000 | [5 empty] | Y | C
C | West | XEL | 2217 | 2008-08-05 | 61 | 4088 | 2008-08-05 | LN | 2018-08-01 | West Waconia | Hazel | 1 | 345 |  | 800 | new line |  | MN |  | 92.3 | Conceptual | 112000000 | [5 empty] | Y | C
C | West | XEL | 2222 | 2008-08-05 |  | 4121 | 2008-08-05 | TX | 2018-08-01 | West Waconia | Transformer | 2 | 345 | 230 | 448 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | XEL | 2222 | 2008-08-05 | 66 | 4093 | 2008-08-05 | LN | 2018-08-01 | West Waconia | McLeod | 1 | 230 |  | 600 | new line |  | MN |  | 26 | Conceptual | 78000000 | [5 empty] | Y | C
C | West | XEL | 2222 | 2008-08-05 |  | 4118 | 2008-08-05 | LNrb | 2018-08-01 | Minnesota Valley | Panther | 1 | 230 |  | 600 | Rebuild Line |  | MN | 30.4 |  | Conceptual | 91000000 | [5 empty] | Y | C
C | West | XEL | 2222 | 2008-08-05 |  | 4120 | 2008-08-05 | TX | 2018-08-01 | West Waconia | Transformer | 1 | 345 | 230 | 448 | new transformer |  | MN |  |  | Conceptual | 10000000 | [5 empty] | Y | C
C | West | XEL | 2222 | 2008-08-05 |  | 4119 | 2008-08-05 | LNrb | 2018-08-01 | McLeod | Panther | 1 | 230 |  | 600 | Rebuild Line |  | MN | 28.2 |  | Conceptual | 85000000 | [5 empty] | Y | C
C | West | XEL | 2226 | 2008-08-05 |  | 4134 | 2008-08-05 | LN | 2018-08-01 | Adams | Pleasant Valley | 2 | 345 |  | 1000 | new line |  | MN |  | 16.8 | Conceptual | 39000000 | [5 empty] | Y | C
C | West | XEL | 2226 | 2008-08-05 |  | 4135 | 2008-08-05 | LN | 2018-08-01 | Byron | Pleasant Valley | 2 | 345 |  | 1000 | new line |  | MN |  | 16.3 | Conceptual | 38000000 | [5 empty] | Y | C
C | West | XEL | 2226 | 2008-08-05 |  | 4136 | 2008-08-05 | LN | 2018-08-01 | North Rochester | Byron | 2 | 345 |  | 1000 | new line |  | MN |  | 10 | Conceptual | 24000000 | [5 empty] | Y | C
C | West | XEL | 2227 | 2008-08-05 |  | 4139 | 2008-08-05 | LN | 2018-08-01 | Crow River | West Waconia | 1 | 345 |  | 1000 | new line |  | MN |  | 23.9 | Conceptual | 34000000 | [5 empty] | Y | C
C | West | XEL | 2227 | 2008-08-05 |  | 4140 | 2008-08-05 | LN | 2018-08-01 | West Waconia | Helena | 1 | 345 |  | 1000 | new line |  | MN |  | 26 | Conceptual | 37000000 | [5 empty] | Y | C
C | West | XEL | 2227 | 2008-08-05 |  | 4138 | 2008-08-05 | LN | 2018-08-01 | Dickinson | Crow River | 1 | 345 |  | 1000 | new line |  | MN |  | 3.8 | Conceptual | 6000000 | [5 empty] | Y | C
C | West | XEL | 2227 | 2008-08-05 |  | 4137 | 2008-08-05 | LN | 2018-08-01 | Monticello | Dickinson | 1 | 345 |  | 1000 | new line |  | MN |  | 17.4 | Conceptual | 25000000 | [5 empty] | Y | C
C | West | XEL | 2773 | 2010-05-08 | GPE | 4846 | 2009-08-14 | SUB | 2020-12-31 | Adams | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in MN. Substation will have a single 765/345kV TRF tying to the Adams 345kV system and a four 765kV line terminals. |  | MN |  |  | Conceptual | 135000000 | [5 empty] | Y | C
C | West | XEL | 2773 | 2010-05-08 | GPE | 4843 | 2009-08-14 | SUB | 2020-12-31 | Chisago | New 765/345 kV substation | 1 | 765 | 345 | 2640/3040 MVA | Construct a new 765/345kV substation in MN. Substation will have a single 765/345kV TRF tying to the Chisago Co. 345kV system and two 765kV line terminals. |  | MN |  |  | Conceptual | 110000000 | [5 empty] | Y | C
C | West | XEL, ALTW | 2212 | 2008-08-05 | 14 | 4044 | 2008-08-05 | LN | 2018-08-01 | Adams | Rock Creek | 1 | 765 |  | 2808 | new line |  | MN/IA |  | 204 | Conceptual | 627000000 | [5 empty] | Y | C
C | West | XEL, ATC LLC | 2210 | 2008-08-05 | 33 | 4060 | 2008-08-05 | LN | 2018-08-01 | Longwood | Chisago County | 1 | 345 |  | 692 | new line |  | MN/WI |  | 116 | Conceptual | 165000000 | [5 empty] | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6283 | 2010-09-15 | Lnup | 2017-12-31 | Alexandria SS | Quarry | 2 | 345 |  | 2085 | Alexandria SS-Quarry 345 kV 2nd ckt |  | MN | 65 | 65 | Proposed | 15000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6281 | 2010-09-15 | Lnup | 2017-12-31 | Bison | SD/MN Border | 2 | 345 |  | 2085 | Bison-SD/MN Border 345 kV 2nd ckt |  | ND | 20 | 20 | Proposed | 5000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6284 | 2010-09-15 | Lnup | 2017-12-31 | Quarry | Monticello | 2 | 345 |  | 2085 | Quarry-Monticello 345 kV 2nd ckt |  | MN | 30 | 30 | Proposed | 8000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6282 | 2010-09-15 | Lnup | 2017-12-31 | SD/MN Border | Alexandria SS | 2 | 345 |  | 2085 | SD/MN Border-Alexandria SS 345 kV 2nd ckt |  | MN | 110 | 110 | Proposed | 24000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6279 | 2010-09-15 | TX | 2017-12-31 | Brookings | Transformer | 1 | 500 | 345 | 1200 | Brookings 1200 MVA345/500 kV transformer |  | SD |  |  | Proposed | 25000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6278 | 2010-09-15 | TX | 2017-12-31 | Bison | Transformer | 1 | 500 | 345 | 1200 | Bison 1200 MVA 345/500 kV transformer |  | ND |  |  | Proposed | 25000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6277 | 2010-09-15 | LN | 2017-12-31 | Brookings | Split Rock | 1 | 500 |  | 1732 | Brookings-Split Rock 500 kV line |  | SD | 95 | 95 | Proposed | 325000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6276 | 2010-09-15 | LN | 2017-12-31 | ND/SD Border | Brookings | 1 | 500 |  | 1732 | ND/SD Border-Brookings 500 kV line |  | SD | 130 | 130 | Proposed | 349000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6274 | 2010-09-15 | LN | 2017-12-31 | US/MB Border | Bison | 1 | 500 |  | 1732 | US/Manitoba Border-Bison 500 kV line |  | ND | 165 | 165 | Proposed | 421000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6275 | 2010-09-15 | LN | 2017-12-31 | Bison | ND/SD Border | 1 | 500 |  | 1732 | Bison-ND/SD Border 500 kV line |  | ND | 75 | 75 | Proposed | 201000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, GRE, OTP, MP, MRES | 3398 | 2010-09-15 | Option W6 | 6280 | 2010-09-15 | TX | 2017-12-31 | Split Rock | Transformer | 1 | 500 | 345 | 1200 | Split Rock 1200 MVA345/500 kV transformer |  | SD |  |  | Proposed | 25000000 | Planning 2010$ |  |  |  |  | Y | C
C | West | XEL, MEC | 2192 | 2008-08-05 | 29 | 4057 | 2008-08-05 | TX | 2018-08-01 | Lehigh | Transformer | 1 | 765 | 345 | 2767.5 | new transformer |  | IA |  |  | Conceptual | 15000000 | [5 empty] | Y | C
C | West | XEL, MEC | 2192 | 2008-08-05 | 3 | 4033 | 2008-08-05 | LN | 2018-08-01 | Blue Earth | Lehigh | 1 | 765 |  | 4368 | new line |  | MN/IA |  | 85 | Conceptual | 258000000 | [5 empty] | Y | C
C | West | XEL, Non-MISO | 2183 | 2008-08-05 | 57 | 4084 | 2008-08-05 | LN | 2018-08-01 | Watertown | Split Rock | 1 | 345 |  | 800 | new line |  | SD |  | 92.4 | Conceptual | 131000000 | [5 empty] | Y | C
C | West, Central, East | ITCM, AmerenIL | 2785 | 2009-04-23 | 6 | 4894 | 40306 | LN | 2014-05-01 | New Substation in NW Iowa | Sorenson | 1 | 800 |  | 6400 | new +/- 800KV DC line |  | IA, IL, IN |  | 667 | Proposed | [6 empty] | Y | C
Note on T3: Upgraded or on existing rights of way