## Instructions
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION
CY 2024
INSTRUCTIONS
These worksheet tabs correspond closely to the tables in the forecast instructions received by the utility.
The forecast instructions pertain to the data to be entered in each of the worksheet tabs.
PLEASE DO NOT CHANGE THE NAME OR ORDER OF ANY OF THE WORKSHEET TABS OR CHANGE THE NAME OF THIS WORKBOOK.
In general, the following color scheme is used on each worksheet:
Cells shown with a dark blue background correspond to applicable Minnesota Rules section number/names on each worksheet tab.
Cells shown with a light green background correspond to headings for sections, columns, row, or individual fields on each worksheet tab.
Cells shown with a light yellow background require data to be entered by the utility.
Cells shown with a light brown background generally correspond to fields that are calculated from the data entered, or
correspond to fields that are informational and not to be modified by the utility.
Each worksheet tab contains a section labeled "Comments" below the main data entry area.
You may enter any comments in that section to provide an explaination or clarification on the data entered; OR
why data IS NOT being entered on the worksheet tab (for example: cells left blank).
Cells with automatic calculations (typically totals) are provided on some worksheets to assist with the accuracy of the data provided by the utility. It is recognized that there may be circumstances in which the data entered by the utility is more appropriate or accurate than the value in the corresponding automatically-calculated cell. If the value in the automatically-calculated cell does not match the value that your utility entered, please provide an explanation in the Comments area at the bottom of the worksheet tab.
Please complete the required worksheet tabs and save the completed workbook to your local computer.
Then attach the completed workbook to an email message, include your contact information, and send it to the following email address:
rule7610.reports@state.mn.us
If you have any questions please contact:
Anne Sell
MN Department of Commerce, Division of Energy Resources
Email: rule7610.reports@state.mn.us (preferred)
Direct: 651-539-1851 (leave a message)
COMM Website: https://mn.gov/commerce/industries/energy/utilities/annual-reporting/

## Registration
MINNESOTA ELECTRIC UTILITY ANNUAL REPORT - FORECAST SECTION |  |  | * * * CORRECTED * * * | < < If this spreadsheet needs to be updated and re-submitted, please
CY 2024 |  |  |  | change the Font color in Cell G1 from White to Automatic (Black).
7610.0120 REGISTRATION
ENTITY ID# | 85 | RILS ID# | U12000
REPORT YEAR | 2024
UTILITY DETAILS |  | CONTACT INFORMATION
UTILITY NAME | Xcel Energy | CONTACT NAME | Christine Schwartz
STREET ADDRESS | 414 Nicollet Mall | CONTACT TITLE | Regulatory Administrator
CITY | Minneapolis | CONTACT STREET ADDRESS | 414 Nicollet Mall
STATE | MN | CITY | Minneapolis
ZIP CODE | 55401 | STATE | MN
TELEPHONE | 612-330-1925 | ZIP CODE | 55401
| Scroll down to see allowable UTILITY TYPES | TELEPHONE | 612-330-6193
* UTILITY TYPE | PUBLIC | CONTACT E-MAIL | regulatory.records@xcelenergy.com
COMMENTS |  | PREPARER INFORMATION | (do not type "Same as Above")
|  | PERSON PREPARING FORMS | Christine Schwartz
|  | PREPARER'S TITLE | Regulatory Administrator
|  | DATE | 2025-07-01
|  | PREPARER'S EMAIL ADDRESS | regulatory.records@xcelenergy.com
ALLOWABLE UTILITY TYPES
Code
Private
Public
Co-op
Hide BlankPlant Sheet
Un-Hide BlankPlant Sheet
Un-Hide All Sheets

## SysConsumers
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [10 empty] | * * * CORRECTED * * *
CY 2024
7610.0310 Item A. SYSTEM FORECAST OF ANNUAL ELECTRIC CONSUMPTION BY ULTIMATE CONSUMERS
Provide actual data for your entire system for the past year, your estimate for the present year and all future forecast years.
Please remember that the number of customers should reflect the number of customers at year's end, not the number of meters.
|  |  | FARM | NON-FARM RESIDENTIAL | COMMERCIAL | MINING * | INDUSTRIAL | STREET & HIGHWAY LIGHTING | OTHER | SYSTEM TOTALS | Calculated System Totals
Past Year | 2024 | No. of Customers | NA | 1633400.75 | 205004.4167 | NA | 648.9167 | 7829.6667 | 1946.0833 | 1848829.8333 | 1848829.8333
|  | MWH | NA | 12112643.9085 | 16713236.9001 | NA | 9753402.8028 | 120904.5804 | 94870.2764 | 38795058.4682 | 38795058.4682
Present Year | 2025 | No. of Customers | NA | 1658455.6432 | 207633.6418 | NA | 648.9074 | 8025.5673 | 1941.2158 | 1876704.9755 | 1876704.9755
|  | MWH | NA | 12638128.886 | 16877091.7036 | NA | 9804727.8982 | 122300.5667 | 94031.3266 | 39536280.3812 | 39536280.3812
1st Forecast Year | 2026 | No. of Customers | NA | 1669794.0421 | 207770.8776 | NA | 649.3146 | 8175.0729 | 1944.1305 | 1888333.4377 | 1888333.4377
|  | MWH | NA | 12813475.9772 | 16727270.0087 | NA | 10433251.2054 | 122698.0866 | 94123.8438 | 40190819.1217 | 40190819.1217
2nd Forecast Year | 2027 | No. of Customers | NA | 1685596.7171 | 208831.8157 | NA | 649.6282 | 8318.1364 | 1947.12 | 1905343.4174 | 1905343.4174
|  | MWH | NA | 13031976.6499 | 16657372.4035 | NA | 11681607.5618 | 123609.7258 | 94240.0737 | 41588806.4147 | 41588806.4147
3rd Forecast Year | 2028 | No. of Customers | NA | 1699991.1754 | 209737.1985 | NA | 650.492 | 8446.8379 | 1950.1792 | 1920775.883 | 1920775.883
|  | MWH | NA | 13345736.3037 | 16668886.1939 | NA | 14329978.8557 | 124553.1525 | 94155.8653 | 44563310.371 | 44563310.371
4th Forecast Year | 2029 | No. of Customers | NA | 1713164.5943 | 210612.9834 | NA | 651.1797 | 8561.1097 | 1953.3035 | 1934943.1706 | 1934943.1706
|  | MWH | NA | 13577925.9214 | 16549161.3173 | NA | 17504747.6219 | 124531.202 | 94031.3266 | 47850397.3892 | 47850397.3892
5th Forecast Year | 2030 | No. of Customers | NA | 1725356.6643 | 211468.7363 | NA | 651.4414 | 8664.9391 | 1956.4884 | 1948098.2695 | 1948098.2695
|  | MWH | NA | 13934811.5561 | 16522776.4656 | NA | 20394530.8452 | 125145.606 | 94123.8438 | 51071388.3168 | 51071388.3168
6th Forecast Year | 2031 | No. of Customers | NA | 1736841.9603 | 212328.7729 | NA | 651.6929 | 8760.6419 | 1959.7298 | 1960542.7977 | 1960542.7977
|  | MWH | NA | 14381167.2131 | 16520142.1026 | NA | 22011195.6805 | 125912.9523 | 94240.0737 | 53132658.0222 | 53132658.0222
7th Forecast Year | 2032 | No. of Customers | NA | 1747895.0733 | 213177.4651 | NA | 651.9338 | 8849.4486 | 1963.024 | 1972536.9448 | 1972536.9448
|  | MWH | NA | 15021723.3673 | 16622472.5576 | NA | 23303879.7163 | 126845.9517 | 94155.8653 | 55169077.4582 | 55169077.4582
8th Forecast Year | 2033 | No. of Customers | NA | 1758670.9438 | 214008.9967 | NA | 652.1637 | 8931.8513 | 1966.3674 | 1984230.3228 | 1984230.3228
|  | MWH | NA | 15494850.3101 | 16560577.0118 | NA | 23261908.049 | 126755.3731 | 94031.3266 | 55538122.0707 | 55538122.0707
9th Forecast Year | 2034 | No. of Customers | NA | 1769225.5632 | 214793.0727 | NA | 652.3817 | 9008.8239 | 1969.7566 | 1995649.5981 | 1995649.5981
|  | MWH | NA | 15992483.993 | 16557845.4807 | NA | 23301874.1545 | 127221.4449 | 94123.8438 | 56073548.9169 | 56073548.9169
10th Forecast Year | 2035 | No. of Customers | NA | 1779528.978 | 215484.3251 | NA | 652.5887 | 9080.8533 | 1973.1886 | 2006719.9337 | 2006719.9337
|  | MWH | NA | 16564246.87 | 16608606.3478 | NA | 23352147.9621 | 127839.1047 | 94240.0737 | 56747080.3584 | 56747080.3584
11th Forecast Year | 2036 | No. of Customers | NA | 1789375.5383 | 216108.7654 | NA | 652.7846 | 9148.1375 | 1976.6605 | 2017261.8864 | 2017261.8864
|  | MWH | NA | 17254982.7632 | 16795680.933 | NA | 23526502.5068 | 128625.6978 | 94155.8653 | 57799947.766 | 57799947.766
12th Forecast Year | 2037 | No. of Customers | NA | 1798580.8745 | 216720.3386 | NA | 652.9743 | 9211.3437 | 1980.1697 | 2027145.7008 | 2027145.7008
|  | MWH | NA | 17804124.0079 | 16828564.6723 | NA | 23562467.4414 | 128382.6496 | 94031.3266 | 58417570.0978 | 58417570.0978
13th Forecast Year | 2038 | No. of Customers | NA | 1807224.2438 | 217289.5297 | NA | 653.1611 | 9270.8318 | 1983.7135 | 2036421.4799 | 2036421.4799
|  | MWH | NA | 18425959.4348 | 16917674.8649 | NA | 23670096.1768 | 128704.4376 | 94123.8438 | 59236558.758 | 59236558.758
14th Forecast Year | 2039 | No. of Customers | NA | 1815432.9029 | 217832.2231 | NA | 653.3455 | 9326.8471 | 1987.2897 | 2045232.6083 | 2045232.6083
|  | MWH | NA | 19073419.1336 | 17027724.9674 | NA | 23794777.2233 | 129185.3359 | 94240.0737 | 60119346.7338 | 60119346.7338
* MINING needs to be reported as a separate category only if annual sales are greater than 1,000 GWH. Otherwise, include MINING in the INDUSTRIAL category.
COMMENTS

## MNConsumers
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [10 empty] | * * * CORRECTED * * *
CY 2024
7610.0310 Item A. MINNESOTA-ONLY FORECAST OF ANNUAL ELECTRIC CONSUMPTION BY ULTIMATE CONSUMERS
Provide actual data for your Minnesota service area only, for the past year, your best estimate for the present year and all future forecast years.
Please remember that the number of customers should reflect the actual number of customers the utility has in that category at year's end, not the number of meters.
|  |  | FARM | NON-FARM RESIDENTIAL | COMMERCIAL | MINING * | INDUSTRIAL | STREET & HIGHWAY LIGHTING | OTHER | MN-ONLY TOTALS | Calculated MN-Only Totals
Past Year | 2024 | No. of Customers | NA | 1230056.5 | 137191.1667 | NA | 480.0833 | 6085.6667 | 1449.75 | 1375263.1667 | 1375263.1667
|  | MWH | NA | 8676639.3042 | 12052977.3857 | NA | 6838714.6035 | 84914.6781 | 68944.9597 | 27722190.9312 | 27722190.9312
Present Year | 2025 | No. of Customers | NA | 1244506.3739 | 138084.8023 | NA | 480.0833 | 6229.2685 | 1440.0868 | 1390740.6149 | 1390740.6149
|  | MWH | NA | 9080583.8331 | 12140448.9204 | NA | 6923209.5317 | 86081.4377 | 67508.3214 | 28297832.0442 | 28297832.0442
1st Forecast Year | 2026 | No. of Customers | NA | 1258343.9956 | 138723.2673 | NA | 480.0833 | 6342.3025 | 1434.4011 | 1405324.0498 | 1405324.0498
|  | MWH | NA | 9246199.8319 | 11985317.3522 | NA | 7499551.5245 | 86435.2941 | 67589.8089 | 28885093.8116 | 28885093.8116
2nd Forecast Year | 2027 | No. of Customers | NA | 1270998.0515 | 139317.2173 | NA | 480.0833 | 6454.3013 | 1428.7155 | 1418678.3689 | 1418678.3689
|  | MWH | NA | 9437584.1987 | 11917557.8429 | NA | 8672621.5474 | 87245.1885 | 67671.7103 | 30182680.4878 | 30182680.4878
3rd Forecast Year | 2028 | No. of Customers | NA | 1282630.7067 | 139806.2798 | NA | 480.0833 | 6556.0608 | 1423.0301 | 1430896.1607 | 1430896.1607
|  | MWH | NA | 9703473.604 | 11910075.0371 | NA | 11278945.0838 | 88061.722 | 67598.2372 | 33048153.6841 | 33048153.6841
4th Forecast Year | 2029 | No. of Customers | NA | 1293270.1056 | 140294.8061 | NA | 480.0833 | 6646.1372 | 1417.3449 | 1442108.4771 | 1442108.4771
|  | MWH | NA | 9925481.8979 | 11809777.0449 | NA | 14394546.1335 | 88312.073 | 67508.3214 | 36285625.4707 | 36285625.4707
5th Forecast Year | 2030 | No. of Customers | NA | 1303063.2041 | 140785.0401 | NA | 480.0833 | 6726.8044 | 1411.6599 | 1452466.7918 | 1452466.7918
|  | MWH | NA | 10248151.2614 | 11786670.066 | NA | 16525672.9712 | 88882.8135 | 67589.8089 | 38716966.9211 | 38716966.9211
6th Forecast Year | 2031 | No. of Customers | NA | 1312260.4926 | 141298.0635 | NA | 480.0833 | 6799.8923 | 1405.975 | 1462244.5068 | 1462244.5068
|  | MWH | NA | 10652005.9251 | 11788354.5647 | NA | 17572088.1074 | 89548.415 | 67671.7103 | 40169668.7225 | 40169668.7225
7th Forecast Year | 2032 | No. of Customers | NA | 1321126.8723 | 141814.1551 | NA | 480.0833 | 6866.7001 | 1400.2904 | 1471688.1012 | 1471688.1012
|  | MWH | NA | 11210316.7152 | 11866032.5356 | NA | 18839155.6027 | 90354.5213 | 67598.2372 | 42073457.612 | 42073457.612
8th Forecast Year | 2033 | No. of Customers | NA | 1329831.8546 | 142338.4581 | NA | 480.0833 | 6928.3121 | 1394.6059 | 1480973.3141 | 1480973.3141
|  | MWH | NA | 11631101.188 | 11815796.3043 | NA | 18787390.9198 | 90536.2441 | 67508.3214 | 42392332.9777 | 42392332.9777
9th Forecast Year | 2034 | No. of Customers | NA | 1338457.1028 | 142834.4718 | NA | 480.0833 | 6985.5677 | 1388.9216 | 1490146.1473 | 1490146.1473
|  | MWH | NA | 12059842.4435 | 11811485.4257 | NA | 18805027.199 | 90958.6524 | 67589.8089 | 42834903.5294 | 42834903.5294
10th Forecast Year | 2035 | No. of Customers | NA | 1346947.7471 | 143259.4936 | NA | 480.0833 | 7039.0081 | 1383.2375 | 1499109.5697 | 1499109.5697
|  | MWH | NA | 12560016 | 11860066.3331 | NA | 18829444.2454 | 91474.5674 | 67671.7103 | 43408672.8562 | 43408672.8562
11th Forecast Year | 2036 | No. of Customers | NA | 1355123.7386 | 143652.5008 | NA | 480.0833 | 7089.3014 | 1377.5536 | 1507723.1778 | 1507723.1778
|  | MWH | NA | 13156833.1813 | 12021839.9409 | NA | 18963177.7933 | 92134.2673 | 67598.2372 | 44301583.42 | 44301583.42
12th Forecast Year | 2037 | No. of Customers | NA | 1362835.7458 | 144056.3649 | NA | 480.0833 | 7136.8131 | 1371.8699 | 1515880.877 | 1515880.877
|  | MWH | NA | 13649171.0839 | 12066721.5702 | NA | 18972049.8397 | 92163.5205 | 67508.3214 | 44847614.3357 | 44847614.3357
13th Forecast Year | 2038 | No. of Customers | NA | 1370113.6637 | 144434.9302 | NA | 480.0833 | 7181.6409 | 1366.1863 | 1523576.5044 | 1523576.5044
|  | MWH | NA | 14186696.3694 | 12147994.3885 | NA | 19038285.4074 | 92441.6451 | 67589.8089 | 45533007.6194 | 45533007.6194
14th Forecast Year | 2039 | No. of Customers | NA | 1377056.3144 | 144807.0204 | NA | 480.0833 | 7223.8631 | 1360.503 | 1530927.7842 | 1530927.7842
|  | MWH | NA | 14739175.4143 | 12246222.6339 | NA | 19113823.2843 | 92820.7986 | 67671.7103 | 46259713.8414 | 46259713.8414
* MINING needs to be reported as a separate category only if annual sales are greater than 1,000 GWH. Otherwise, include MINING in the INDUSTRIAL category.
COMMENTS

## Consumption
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [9 empty] | PUBLIC DOCUMENT -
CY 2024 | [9 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0310 Item B. FORECAST OF ANNUAL SYSTEM CONSUMPTION AND GENERATION DATA | [5 empty] | (Express in MWH)
NOTE: (Column 1 + Column 2) = (Column 3 + Column 5) - (Column 4 + Column 6)
It is recognized that there may be circumstances in which the data entered by the utility is more appropriate or accurate than the value in the corresponding automatically-calculated cell. If the value in the automatically-calculated cell does not match the value that your utility entered, please provide an explanation in the Comments area at the bottom of the worksheet tab.
|  | Column 1 | Column 2 | Column 3 | Column 4 | Column 5 | Column 6 | Column 7 | Column 8 | CALCULATED
|  | CONSUMPTION BY ULTIMATE CONSUMERS IN MINNESOTA MWH [7610.0310 B(1)] | CONSUMPTION BY ULTIMATE CONSUMERS OUTSIDE OF MINNESOTA MWH [7610.0310 B(2)] | RECEIVED FROM OTHER UTILITIES MWH [7610.0310 B(3)] | DELIVERED FOR RESALE MWH [7610.0310 B(4)] | TOTAL ANNUAL NET GENERATION MWH [7610.0310 B(5)] | TRANSMISSION LINE SUBSTATION AND DISTRIBUTION LOSSES MWH [7610.0310 B(6)] | TOTAL WINTER CONSUMPTION MWH [7610.0310 B(7)] | TOTAL SUMMER CONSUMPTION MWH [7610.0310 B(7)] | (GENERATION + RECEIVED) MINUS (RESALE + LOSSES) MINUS (CONSUMPTION) SHOULD EQUAL ZERO
[PROTECTED DATA BEGINS
Past Year | 2024 | 27722190.9312 | 11072867.537 | 18050356.9643 |  |  | 3561730.236 | 18657494.1503 | 20137564.3179 | 0
Present Year | 2025 | 28297832.0442 | 11238448.3369 | 15526468.8672 |  |  | 3647904.7888 | 19069645.7139 | 20466634.6672 | 0
1st Forecast Year | 2026 | 28885093.8116 | 11305725.3101 | 15572376.624 |  |  | 3686479.713 | 19399712.985 | 20791106.1367 | 0
2nd Forecast Year | 2027 | 30182680.4878 | 11406125.9268 | 18048806.4671 |  |  | 3760694.9122 | 20087414.5332 | 21501391.8815 | 0
3rd Forecast Year | 2028 | 33048153.6841 | 11515156.6869 | 23174924.6542 |  |  | 3904026.2765 | 21556466.5599 | 23006843.8111 | 0
4th Forecast Year | 2029 | 36285625.4707 | 11564771.9185 | 27004024.9265 |  |  | 4052102.0196 | 23190359.3847 | 24660038.0045 | 0
5th Forecast Year | 2030 | 38716966.9211 | 12354421.3957 | 29100336.7358 |  |  | 4212390.058 | 24749025.3234 | 26322362.9934 | 0
6th Forecast Year | 2031 | 40169668.7225 | 12962989.2997 | 32332544.7509 |  |  | 4328639.1931 | 25837141.3405 | 27295516.6818 | 0
7th Forecast Year | 2032 | 42073457.612 | 13095619.8462 | 34123053.3706 |  |  | 4461435.3396 | 26902538.5278 | 28266538.9303 | -1.4901e-08
8th Forecast Year | 2033 | 42392332.9777 | 13145789.093 | 34981483.6636 |  |  | 4499594.9098 | 27123058.4586 | 28415063.6121 | 0
9th Forecast Year | 2034 | 42834903.5294 | 13238645.3874 | 35919305.3685 |  |  | 4551011.0132 | 27435498.6603 | 28638050.2566 | 0
10th Forecast Year | 2035 | 43408672.8562 | 13338407.5022 | 37482828.3049 |  |  | 4616706.1114 | 27822013.3874 | 28925066.971 | 0
11th Forecast Year | 2036 | 44301583.42 | 13498364.346 | 39175073.8747 |  |  | 4717790.6567 | 28429747.2704 | 29370200.4956 | 0
12th Forecast Year | 2037 | 44847614.3357 | 13569955.762 | 40576601.606 |  |  | 4780832.0977 | 28772222.0127 | 29645348.0851 | 0
13th Forecast Year | 2038 | 45533007.6194 | 13703551.1386 | 42618738.2606 |  |  | 4860546.1945 | 29245847.3035 | 29990711.4545 | 0
14th Forecast Year | 2039 | 46259713.8414 | 13859632.8924 | 44535928.1049 |  |  | 4945886.9012 | 29757032.0858 | 30362314.648 | 0
PROTECTED DATA ENDS]
COMMENTS

## PeakDemand
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [12 empty] | * * * CORRECTED * * *
CY 2024
7610.0310 Item C. PEAK DEMAND BY ULTIMATE CONSUMERS AT THE TIME OF ANNUAL SYSTEM PEAK (in MW)
|  | FARM | NON-FARM RESIDENTIAL | COMMERCIAL | MINING | INDUSTRIAL | STREET & HIGHWAY LIGHTING | OTHER | SYSTEM TOTALS | Calculated System Totals
Last Year Peak Day | 2024 | 0 | 3619.9106 | 3798.9433 | 0 | 1389.6107 | 0 | 13.7303 | 8822.1949 | 8822.1949
7610.0310 Item D. PEAK DEMAND BY MONTH FOR THE LAST CALENDAR YEAR (in MW)
|  | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER
Last Year | 2024 | 6269.9698 | 5583.7398 | 5564.8273 | 5247.3309 | 5779.0338 | 7306.0125 | 8316.0067 | 8822.1949 | 7614.0286 | 5798.2025 | 5490.46 | 6263.75
COMMENTS

## FirmPurch
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [5 empty] | PUBLIC DOCUMENT -
CY 2024 | [5 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0310 Item E. PART 1: FIRM PURCHASES |  |  |  | (Express in MegaWatts)
[PROTECTED DATA BEGINS
NAME OF OTHER UTILITY =>
Past Year | 2024 | Summer 2024
Fall 2024
Winter 2024-2025
Spring 2025
Present Year | 2025 | Summer 2025
Fall 2025
Winter 2025-2026
Spring 2026
1st Forecast Year | 2026 | Summer 2026
Fall 2026
Winter 2026-2027
Spring 2027
2nd Forecast Year | 2027 | Summer 2027
Fall 2027
Winter 2027-2028
Spring 2028
3rd Forecast Year | 2028 | Summer 2028
Fall 2028
Winter 2028-2029
Spring 2029
4th Forecast Year | 2029 | Summer 2029
Fall 2029
Winter 2029-2030
Spring 2030
5th Forecast Year | 2030 | Summer 2030
Fall 2030
Winter 2030-2031
Spring 2031
6th Forecast Year | 2031 | Summer 2031
Fall 2031
Winter 2031-2032
Spring 2032
7th Forecast Year | 2032 | Summer 2032
Fall 2032
Winter 2032-2033
Spring 2033
8th Forecast Year | 2033 | Summer 2033
Fall 2033
Winter 2033-2034
Spring 2034
9th Forecast Year | 2034 | Summer 2034
Fall 2034
Winter 2034-2035
Spring 2035
10th Forecast Year | 2035 | Summer 2035
Fall 2035
Winter 2035-2036
Spring 2036
11th Forecast Year | 2036 | Summer 2036
Fall 2036
Winter 2036-2037
Spring 2037
12th Forecast Year | 2037 | Summer 2037
Fall 2037
Winter 2037-2038
Spring 2038
13th Forecast Year | 2038 | Summer 2038
Fall 2038
Winter 2038-2039
Spring 2039
14th Forecast Year | 2039 | Summer 2039
Fall 2039
Winter 2039-2040
Spring 2040
PROTECTED DATA ENDS]
[PROTECTED DATA BEGINS
COMMENTS
PROTECTED DATA ENDS]

## FirmSales
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [5 empty] | PUBLIC DOCUMENT -
CY 2024 | [5 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0310 Item E. PART 2: FIRM SALES |  |  |  | (Express in MegaWatts)
[PROTECTED DATA BEGINS
NAME OF OTHER UTILITY =>
Past Year | 2024 | Summer 2024
Fall 2024
Winter 2024-2025
Spring 2025
Present Year | 2025 | Summer 2025
Fall 2025
Winter 2025-2026
Spring 2026
1st Forecast Year | 2026 | Summer 2026
Fall 2026
Winter 2026-2027
Spring 2027
2nd Forecast Year | 2027 | Summer 2027
Fall 2027
Winter 2027-2028
Spring 2028
3rd Forecast Year | 2028 | Summer 2028
Fall 2028
Winter 2028-2029
Spring 2029
4th Forecast Year | 2029 | Summer 2029
Fall 2029
Winter 2029-2030
Spring 2030
5th Forecast Year | 2030 | Summer 2030
Fall 2030
Winter 2030-2031
Spring 2031
6th Forecast Year | 2031 | Summer 2031
Fall 2031
Winter 2031-2032
Spring 2032
7th Forecast Year | 2032 | Summer 2032
Fall 2032
Winter 2032-2033
Spring 2033
8th Forecast Year | 2033 | Summer 2033
Fall 2033
Winter 2033-2034
Spring 2034
9th Forecast Year | 2034 | Summer 2034
Fall 2034
Winter 2034-2035
Spring 2035
10th Forecast Year | 2035 | Summer 2035
Fall 2035
Winter 2035-2036
Spring 2036
11th Forecast Year | 2036 | Summer 2036
Fall 2036
Winter 2036-2037
Spring 2037
12th Forecast Year | 2037 | Summer 2037
Fall 2037
Winter 2037-2038
Spring 2038
13th Forecast Year | 2038 | Summer 2038
Fall 2038
Winter 2038-2039
Spring 2039
14th Forecast Year | 2039 | Summer 2039
Fall 2039
Winter 2039-2040
Spring 2040
PROTECTED DATA ENDS]
[PROTECTED DATA BEGINS
COMMENTS
PROTECTED DATA ENDS]

## ParticipPurch
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [5 empty] | * * * CORRECTED * * * | PUBLIC DOCUMENT -
CY 2024 | [6 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0310 Item F. PART 1: PARTICIPATION PURCHASES |  |  |  | (Express in MegaWatts)
[PROTECTED DATA BEGINS
NAME OF OTHER UTILITY =>
Past Year | 2024 | Summer 2024
Fall 2024
Winter 2024-2025
Spring 2025
Present Year | 2025 | Summer 2025
Fall 2025
Winter 2025-2026
Spring 2026
1st Forecast Year | 2026 | Summer 2026
Fall 2026
Winter 2026-2027
Spring 2027
2nd Forecast Year | 2027 | Summer 2027
Fall 2027
Winter 2027-2028
Spring 2028
3rd Forecast Year | 2028 | Summer 2028
Fall 2028
Winter 2028-2029
Spring 2029
4th Forecast Year | 2029 | Summer 2029
Fall 2029
Winter 2029-2030
Spring 2030
5th Forecast Year | 2030 | Summer 2030
Fall 2030
Winter 2030-2031
Spring 2031
6th Forecast Year | 2031 | Summer 2031
Fall 2031
Winter 2031-2032
Spring 2032
7th Forecast Year | 2032 | Summer 2032
Fall 2032
Winter 2032-2033
Spring 2033
8th Forecast Year | 2033 | Summer 2033
Fall 2033
Winter 2033-2034
Spring 2034
9th Forecast Year | 2034 | Summer 2034
Fall 2034
Winter 2034-2035
Spring 2035
10th Forecast Year | 2035 | Summer 2035
Fall 2035
Winter 2035-2036
Spring 2036
11th Forecast Year | 2036 | Summer 2036
Fall 2036
Winter 2036-2037
Spring 2037
12th Forecast Year | 2037 | Summer 2037
Fall 2037
Winter 2037-2038
Spring 2038
13th Forecast Year | 2038 | Summer 2038
Fall 2038
Winter 2038-2039
Spring 2039
14th Forecast Year | 2039 | Summer 2039
Fall 2039
Winter 2039-2040
Spring 2040
PROTECTED DATA ENDS]
[PROTECTED DATA BEGINS
COMMENTS
PROTECTED DATA ENDS]

## ParticipSales
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [5 empty] | * * * CORRECTED * * * | PUBLIC DOCUMENT -
CY 2024 | [6 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0310 Item F. PART 2: PARTICIPATION SALES |  |  |  | (Express in MegaWatts)
[PROTECTED DATA BEGINS
NAME OF OTHER UTILITY =>
Past Year | 2024 | Summer 2024
Fall 2024
Winter 2024-2025
Spring 2025
Present Year | 2025 | Summer 2025
Fall 2025
Winter 2025-2026
Spring 2026
1st Forecast Year | 2026 | Summer 2026
Fall 2026
Winter 2026-2027
Spring 2027
2nd Forecast Year | 2027 | Summer 2027
Fall 2027
Winter 2027-2028
Spring 2028
3rd Forecast Year | 2028 | Summer 2028
Fall 2028
Winter 2028-2029
Spring 2029
4th Forecast Year | 2029 | Summer 2029
Fall 2029
Winter 2029-2030
Spring 2030
5th Forecast Year | 2030 | Summer 2030
Fall 2030
Winter 2030-2031
Spring 2031
6th Forecast Year | 2031 | Summer 2031
Fall 2031
Winter 2031-2032
Spring 2032
7th Forecast Year | 2032 | Summer 2032
Fall 2032
Winter 2032-2033
Spring 2033
8th Forecast Year | 2033 | Summer 2033
Fall 2033
Winter 2033-2034
Spring 2034
9th Forecast Year | 2034 | Summer 2034
Fall 2034
Winter 2034-2035
Spring 2035
10th Forecast Year | 2035 | Summer 2035
Fall 2035
Winter 2035-2036
Spring 2036
11th Forecast Year | 2036 | Summer 2036
Fall 2036
Winter 2036-2037
Spring 2037
12th Forecast Year | 2037 | Summer 2037
Fall 2037
Winter 2037-2038
Spring 2038
13th Forecast Year | 2038 | Summer 2038
Fall 2038
Winter 2038-2039
Spring 2039
14th Forecast Year | 2039 | Summer 2039
Fall 2039
Winter 2039-2040
Spring 2040
PROTECTED DATA ENDS]
[PROTECTED DATA BEGINS
COMMENTS
PROTECTED DATA ENDS]

## Load&GenCap
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [11 empty] | * * * CORRECTED * * * |  |  |  |  | PUBLIC DOCUMENT -
CY 2024 | [16 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0310 Item G. LOAD AND GENERATION CAPACITY |  |  |  |  | (Express in MegaWatts)
|  |  | Column 1 | Column 2 | Column 3 | Column 4 | Column 5 | Column 6 | Column 7 | Column 8 | Column 9 | Column 10 | Column 11 | Column 12 | Column 13 | Column 14 | Column 15
|  |  | Generation Zonal Resource Credits (ZRCs) | Demand Response ZRCs | ZRC Purchases | ZRC Sales | Total ZRCs [1 + 2 + 3 - 4] | Forecasted Non-Coincident Peak Demand for NSP System | Energy Efficiency Adjustment to Base Demand Forecast | Adjusted Forecasted Non-Coincident Summer Peak Demand for NSP System [6 - 7] | Coincidence Factor with MISO Peak Demand | Forecasted Demand Coincident with MISO Peak [ 8 x 9] | Firm Purchases | Firm Sales | Total Load Serving Obligation [10 - 11 + 12] | Capacity Obligation (Column 13 plus the planning reserve margin) | Total System Surplus/Deficit [5 - 14]
[PROTECTED DATA BEGINS
Past Year | 2024 | Summer 2024
Fall 2024
Winter 2024-2025
Spring 2025
Present Year | 2025 | Summer 2025
Fall 2025
Winter 2025-2026
Spring 2026
1st Forecast Year | 2026 | Summer 2026
Fall 2026
Winter 2026-2027
Spring 2027
2nd Forecast Year | 2027 | Summer 2027
Fall 2027
Winter 2027-2028
Spring 2028
3rd Forecast Year | 2028 | Summer 2028
Fall 2028
Winter 2028-2029
Spring 2029
4th Forecast Year | 2029 | Summer 2029
Fall 2029
Winter 2029-2030
Spring 2030
5th Forecast Year | 2030 | Summer 2030
Fall 2030
Winter 2030-2031
Spring 2031
6th Forecast Year | 2031 | Summer 2031
Fall 2031
Winter 2031-2032
Spring 2032
7th Forecast Year | 2032 | Summer 2032
Fall 2032
Winter 2032-2033
Spring 2033
8th Forecast Year | 2033 | Summer 2033
Fall 2033
Winter 2033-2034
Spring 2034
9th Forecast Year | 2034 | Summer 2034
Fall 2034
Winter 2034-2035
Spring 2035
10th Forecast Year | 2035 | Summer 2035
Fall 2035
Winter 2035-2036
Spring 2036
11th Forecast Year | 2036 | Summer 2036
Fall 2036
Winter 2036-2037
Spring 2037
12th Forecast Year | 2037 | Summer 2037
Fall 2037
Winter 2037-2038
Spring 2038
13th Forecast Year | 2038 | Summer 2038
Fall 2038
Winter 2038-2039
Spring 2039
14th Forecast Year | 2039 | Summer 2039
Fall 2039
Winter 2039-2040
Spring 2040
PROTECTED DATA ENDS]
[PROTECTED DATA BEGINS
COMMENTS
PROTECTED DATA ENDS]

## Add&Retire
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued)
CY 2024 |  |  |  |  | * * * CORRECTED * * * |  |  | * * * CORRECTED * * *
7610.0310 Item H. ADDITIONS AND RETIREMENTS |  |  | (Express in MegaWatts)
|  | ADDITIONS | RETIREMENTS
Past Year | 2024 | Summer = 27, Fall = 56, Winter = 93, Spring = 33 | Summer = 46, Fall = 40, Winter = 47, Spring = 37
Present Year | 2025 | Summer = 724, Fall = 183, Winter = -332, Spring = 184 | Summer = 1169, Fall = 1168, Winter = 534, Spring = 445
1st Forecast Year | 2026 | Summer = 601, Fall = 598, Winter = 278, Spring = 605 | Summer = 563, Fall = 623, Winter = 655, Spring = 670
2nd Forecast Year | 2027 | Summer = 943, Fall = 1061, Winter = 919, Spring = 1071 | Summer = 237, Fall = 252, Winter = 260, Spring = 263
3rd Forecast Year | 2028 | Summer = 1495, Fall = 1599, Winter = 1706, Spring = 1537 | Summer = 902, Fall = 748, Winter = 1232, Spring = 868
4th Forecast Year | 2029 | Summer = 110, Fall = 148, Winter = 235, Spring = 160 | Summer = 1, Fall = 1, Winter = 1, Spring = 1
5th Forecast Year | 2030 | Summer = 865, Fall = 779, Winter = 652, Spring = 692 | Summer = 1100, Fall = 712, Winter = 646, Spring = 509
6th Forecast Year | 2031 | Summer = 100, Fall = 144, Winter = 232, Spring = 155 | Summer = 4, Fall = 4, Winter = 4, Spring = 4
7th Forecast Year | 2032 | Summer = 1109, Fall = 1171, Winter = 1107, Spring = 1129 | Summer = 324, Fall = 294, Winter = 252, Spring = 254
8th Forecast Year | 2033 | Summer = 129, Fall = 134, Winter = 195, Spring = 148 | Summer = 2, Fall = 4, Winter = 5, Spring = 4
9th Forecast Year | 2034 | Summer = 43, Fall = 58, Winter = 93, Spring = 63 | Summer = 26, Fall = 25, Winter = 28, Spring = 24
10th Forecast Year | 2035 | Summer = 6, Fall = 2, Winter = 1, Spring = 3 | Summer = 9, Fall = 10, Winter = 9, Spring = 10
11th Forecast Year | 2036 | Summer = 0, Fall = 0, Winter = 0, Spring = 0 | Summer = 38, Fall = 49, Winter = 80, Spring = 53
12th Forecast Year | 2037 | Summer = 0, Fall = 0, Winter = 0, Spring = 0 | Summer = 30, Fall = 28, Winter = 25, Spring = 25
13th Forecast Year | 2038 | Summer = 0, Fall = 0, Winter = 0, Spring = 0 | Summer = 0, Fall = 0, Winter = 0, Spring = 0
14th Forecast Year | 2039 | Summer = 0, Fall = 0, Winter = 0, Spring = 0 | Summer = 570, Fall = 546, Winter = 496, Spring = 466
COMMENTS
Additions and Retirements are expressed in anticipated Seasonal Accredited Capacity (SAC) values.
Note: Addition year reflects when capacity accreditation is first realized
|  | Year of Addition: |  | Summer MW | Fall MW | Winter MW | Spring MW
|  | 2024 | Deuel Harvest Wind (100 MW) | 19 | 33 | 91 | 19
|  | 2024 | Solar - CSG | 8 | 23 | 2 | 14
|  | 2025 | Manitoba Hydro System Power (200 MW) | 196 | 0 | 0 | 0
|  | 2025 | Manitoba Hydro Diversity (350/200 MW) | 343 | 0 | -350 | 0
|  | 2025 | Solar - Sherco Solar 1 (261 MW) | 131 | 131 | 13 | 131
|  | 2025 | Solar - Lake Hallie (5 MW) | 4 | 2 | 0 | 3
|  | 2025 | Solar - CSG (100 MW) | 50 | 50 | 5 | 50
|  | 2026 | Solar - Apple River (100 MW) | 50 | 50 | 5 | 50
|  | 2026 | Solar - Sherco Solar 2 (230 MW) | 115 | 115 | 12 | 115
|  | 2026 | Solar - Sherco Solar 3 (250 MW) | 125 | 125 | 13 | 125
|  | 2026 | Solar - CSG (99 MW) | 50 | 50 | 5 | 50
|  | 2026 | Blue Lake 9-11 RICE (28 MW) | 23 | 24 | 21 | 25
|  | 2026 | Wheaton 8 (210 MW) | 200 | 195 | 188 | 199
|  | 2026 | Wheaton RICE 9-13 (46 MW) | 38 | 39 | 34 | 41
|  | 2027 | Solar - CSG (99 MW) | 50 | 50 | 5 | 50
|  | 2027 | Storage - Sherco West (300 MW) | 261 | 297 | 276 | 300
|  | 2027 | Storage - Northstar (80 MW) | 70 | 79 | 74 | 80
|  | 2027 | Storage - Form Energy (10 MW) | 9 | 10 | 9 | 10
|  | 2027 | Storage - ESS 4 Hour (600 MW) | 522 | 594 | 552 | 600
|  | 2027 | Solar - DSES (62 MW) | 31 | 31 | 3 | 31
|  | 2028 | Cannon Falls PPA extension (358 MW) | 259 | 287 | 348 | 277
|  | 2028 | Mankato Energy Center 1 PPA Ext (359 MW) | 288 | 285 | 238 | 268
|  | 2028 | Lyon County CT 439 MW) | 417 | 399 | 338 | 342
|  | 2028 | Anson RICE (28 MW) | 27 | 25 | 22 | 22
|  | 2028 | Lake Wilson Solar (150 MW) | 15 | 6 | 3 | 8
|  | 2028 | Solar - CSG (79 MW) | 8 | 3 | 2 | 4
|  | 2028 | Solar - DSES (188 MW) | 19 | 8 | 4 | 9
|  | 2028 | Wind - Plum Creek (230 MW) | 21 | 32 | 53 | 35
|  | 2028 | Wind (1800 MW) | 162 | 252 | 414 | 270
|  | 2028 | Storage - Plum Creek (150 MW) | 137 | 149 | 140 | 149
|  | 2028 | Storage - Lake Wilson (95 MW) | 87 | 94 | 88 | 94
|  | 2028 | Storage - ESS 4 Hour (60 MW) | 55 | 59 | 56 | 59
|  | 2029 | Solar - CSG (78 MW) | 8 | 3 | 2 | 4
|  | 2029 | Solar - DSES (123 MW) | 12 | 5 | 3 | 6
|  | 2029 | Wind (1000 MW) | 90 | 140 | 230 | 150
|  | 2030 | CT addition (748 MW) | 711 | 681 | 576 | 583
|  | 2030 | Solar - Utility Scale (700 MW) | 70 | 28 | 14 | 35
|  | 2030 | Solar - CSG (78 MW) | 8 | 3 | 2 | 4
|  | 2030 | Solar - DSES (209 MW) | 21 | 8 | 4 | 11
|  | 2030 | Storage - ESS 4 Hour (60 MW) | 55 | 59 | 56 | 59
|  | 2031 | Solar - CSG (77 MW) | 8 | 3 | 2 | 4
|  | 2031 | Solar - DSES (22 MW) | 2 | 1 | 0 | 1
|  | 2031 | Wind (1000 MW) | 90 | 140 | 230 | 150
|  | 2032 | CT addition (374 MW) | 355 | 340 | 288 | 292
|  | 2032 | Solar - CSG (57 MW) | 6 | 2 | 1 | 3
|  | 2032 | Solar - DSES (29 MW) | 2 | 1 | 1 | 2
|  | 2032 | Storage - ESS 4 Hour (780 MW) | 710 | 772 | 725 | 772
|  | 2032 | Wind (400 MW) | 36 | 56 | 92 | 60
|  | 2033 | Solar - Utility Scale (500 MW) | 50 | 20 | 10 | 25
|  | 2033 | Solar - CSG (57 MW) | 6 | 2 | 1 | 3
|  | 2033 | Solar - DSES (5 MW) | 1 | 0 | 0 | 0
|  | 2033 | Wind (800 MW UCAP) | 72 | 112 | 184 | 120
|  | 2034 | Solar - CSG (56 MW) | 6 | 2 | 1 | 3
|  | 2034 | Solar - DSES (6 MW) | 1 | 0 | 0 | 0
|  | 2034 | Wind (400 MW) | 36 | 56 | 92 | 60
|  | 2035 | Solar - CSG (56 MW) | 6 | 2 | 1 | 3
Note: Retirement year reflects when capacity accreditation is first lost
|  | Year of Retirement: |  | Summer MW | Fall MW | Winter MW | Spring MW
|  | 2024 | Hennepin Co. Energy Recovery Center | 24 | 17 | 24 | 22
|  | 2024 | St. Paul Cogeneration | 20 | 20 | 18 | 12
|  | 2024 | Renewable PPAs | 2 | 3 | 5 | 3
|  | 2025 | Blue Lake 1-4 | 128 | 127 | 162 | 121
|  | 2025 | Manitoba Hydro System Power (375/325 MW) | 367 | 366 | 319 | 320
|  | 2025 | Manitoba Hydro System Power (125 MW) | 122 | 122 | 123 | 123
|  | 2025 | Manitoba Hydro Diversity (350 MW) | 343 | 342 | -350 | -350
|  | 2025 | Wheaton 1-4 | 203 | 206 | 264 | 224
|  | 2025 | Renewable PPAs | 6 | 5 | 16 | 7
|  | 2026 | Sherburne County 1 | 522 | 571 | 602 | 622
|  | 2026 | MinnDakota Wind PPA | 40 | 51 | 48 | 46
|  | 2026 | Renewable PPAs | 1 | 1 | 5 | 2
|  | 2027 | LSP Cottage Grove | 232 | 244 | 253 | 256
|  | 2027 | Renewable PPAs | 5 | 8 | 7 | 7
|  | 2028 | Allen S King | 309 | 107 | 517 | 241
|  | 2028 | Cannon Falls | 279 | 315 | 385 | 325
|  | 2028 | Mankato Energy Center 2 | 299 | 297 | 291 | 268
|  | 2028 | Moraine 2 Wind PPA | 6 | 15 | 17 | 12
|  | 2028 | Renewable PPAs | 9 | 14 | 22 | 22
|  | 2029 | Renewable PPAs | 1 | 1 | 1 | 1
|  | 2030 | Manitoba Hydro System Power (200 MW) | 196 | 0 | 0 | 0
|  | 2030 | Manitoba Hydro Diversity (350/200 MW) | 196 | 0 | -200 | 0
|  | 2030 | Sherburne County 3 | 396 | 381 | 418 | 180
|  | 2030 | French Island 3-4 Gas | 86 | 78 | 125 | 85
|  | 2030 | Inver Hills 1-6 | 213 | 231 | 272 | 221
|  | 2030 | Renewable PPAs | 13 | 22 | 31 | 23
|  | 2031 | Renewable PPAs | 4 | 4 | 4 | 4
|  | 2032 | Black Dog 5/2 | 265 | 213 | 155 | 187
|  | 2032 | Dakota Ridge 3 Wind PPA | 15 | 25 | 31 | 20
|  | 2032 | Fenton Wind PPA | 12 | 18 | 27 | 15
|  | 2032 | Renewable PPAs | 32 | 38 | 39 | 32
|  | 2033 | Renewable PPAs | 2 | 4 | 5 | 4
|  | 2034 | Owned Renewable | 9 | 6 | 4 | 5
|  | 2034 | Bayfront | 17 | 19 | 24 | 19
|  | 2035 | Form Energy Sherco Battery | 9 | 10 | 9 | 10
|  | 2036 | Aurora Distributed Solar | 10 | 4 | 2 | 5
|  | 2036 | Odell Wind PPA | 19 | 31 | 55 | 33
|  | 2036 | Deuel Harwest Wind PPA | 9 | 14 | 23 | 15
|  | 2037 | Red Wing 1-2 RDF | 18 | 17 | 15 | 13
|  | 2037 | Wilmarth 1-2 RDF | 12 | 11 | 10 | 12
|  | 2039 | Mankato Energy Center 1 PPA Ext (359 MW) | 288 | 285 | 238 | 268
|  | 2039 | Mankato Energy Center 2 PPA Ext (359 MW) | 269 | 238 | 230 | 177
|  | 2039 | Renewable PPAs | 13 | 23 | 28 | 21

## FuelRequirements
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [11 empty] | * * * CORRECTED * * * | * * * CORRECTED * * * |  |  |  |  | PUBLIC DOCUMENT -
CY 2024 | [17 empty] | NOT PUBLIC DATA HAS BEEN EXCISED
7610.0430 FUEL REQUIREMENTS AND GENERATION BY FUEL TYPE
Please use the appropriate code for the fuel type as shown in the list at the bottom of this worksheet tab.
|  | FUEL TYPE 1 |  | FUEL TYPE 2 |  | FUEL TYPE 3 |  | FUEL TYPE 4 |  | FUEL TYPE 5 |  | FUEL TYPE 6 |  | FUEL TYPE 7 |  | FUEL TYPE 8
|  | Name of Fuel | Coal | Name of Fuel | NUC | Name of Fuel | REF | Name of Fuel | NG | Name of Fuel | Oil | Name of Fuel | HYD | Name of Fuel | Wind | Name of Fuel | Solar
|  | Unit of Measure | mmBtu | Unit of Measure | mmBtu | Unit of Measure | mmBtu | Unit of Measure | mmBtu | Unit of Measure | mmBtu | Unit of Measure | mmBtu | Unit of Measure | mmBtu | Unit of Measure | mmBtu
|  | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED | QUANTITY OF FUEL USED | NET MWH GENERATED
[PROTECTED DATA BEGINS
Past Year | 2024
Present Year | 2025
1st Forecast Year | 2026
2nd Forecast Year | 2027
3rd Forecast Year | 2028
4th Forecast Year | 2029
5th Forecast Year | 2030
6th Forecast Year | 2031
7th Forecast Year | 2032
8th Forecast Year | 2033
9th Forecast Year | 2034
10th Forecast Year | 2035
11th Forecast Year | 2036
12th Forecast Year | 2037
13th Forecast Year | 2038
14th Forecast Year | 2039
PROTECTED DATA ENDS]
LIST OF FUEL TYPES
|  | BIT - Bituminous Coal |  | LPG - Liquefied Propane Gas |  |  | HYD - Hydro (Water)
|  | COAL - Coal (General) |  | NG - Natural Gas |  |  | WIND - Wind
|  | DIESEL - Diesel |  | NUC - Nuclear |  |  | WOOD - Wood
|  | FO2 - Fuel Oil #2 (Mid-Distillate) |  | REF - Refuse, Bagasse, Peat, Non-wood waste |  |  | SOLAR - Solar
|  | FO6 - Fuel Oil #6 (Residual Fuel Oil) |  | STM - Steam
|  | LIG - Lignite |  | SUB - Sub-bituminous coal
COMMENTS
Note on H7: Fuller, Marit: French Island 1-2, Redwing 1-2, Wilmarth 1-2
Note on R7: Fuller, Marit: Solar PV and Demand:Distributed Solar

## Transmission
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued) | [8 empty] | * * * CORRECTED * * *
CY 2024
7610.0500 TRANSMISSION LINES
Subpart 1. Existing transmission lines. Each utility shall report the following information in regard to each transmission line of 200 kilovolts now in existence:
A. | a map showing the location of each line;
B. | the design voltage of each line;
C. | the size and type of conductor;
D. | the approximate location of d.c. terminals or a.c. substations; and
E. | the approximate length of each line in Minnesota.
Subpart 2. Transmission line additions. Each generating and transmission utility, as defined in part 7610.0100, shall report the information required in subpart 1 for all future transmission lines over 200 kilovolts that the utility plans to build within the next 15 years.
Subpart 3. Transmission line retirements. Each generating and transmission utility, as defined in part 7610.0100, shall identify all present transmission lines over 200 kilovolts that the utility plans to retire within the next 15 years.
In Use (enter X for selection) | To Be Built (enter X for selection) | To Be Retired (enter X for selection) | DESIGN VOLTAGE | SIZE OF CONDUCTOR | TYPE OF CONDUCTOR | D.C. OR A.C. (specify) | LOCATION OF D.C. TERMINALS OR A.C. SUBSTATIONS | INDICATE YEAR IF "TO BE BUILT" OR "RETIRED" | LENGTH IN MINNESOTA (miles)
X |  |  | 500 kV | 3-1192 kcmil | ACSR | A.C. | Forbes - Chisago North |  | 61.50
X |  |  | 500 kV | 3-1192 kcmil | ACSS | A.C. | Forbes - Roseau County South |  | 193.30
X |  |  | 500 kV | 3-1192 kcmil | ACSS | A.C. | Riel(Manitoba Hyd) - Roseau Co N |  | 10.50
X |  |  | 345 kV | 2-795, 2-954 kcmil | ACSR | A.C. | A.S. King - Chisago County |  | 38.0
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | A.S. King - Eau Claire |  | 19.60
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | A.S. King - Kohlman Lake |  | 12.70
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | A.S. King - Red Rock |  | 25.40
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Adams - Pleasant Valley |  | 16.90
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | North Rochester - Briggs Road |  | 42.37
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Bison - Alexandria Switching Stat. |  | 101.21
X |  |  | 345 kV | 2-795, 2312 kcmil | ACSR | A.C. | Blue Lake - Eden Prairie |  | 5.50
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Blue Lake - Parkers Lake |  | 14.90
X |  |  | 345 kV | 2-795 kcmil | ACSR, ACSS | A.C. | Blue Lake - Scott County |  | 8.16
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Briggs Road - North Rochester |  | 43.54
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Brookings Co - Steep Bank Lake |  | 8.73
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Bunker Lake (GRE) - Coon Creek |  | 6.60
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Byron - North Rochester |  | 13.64
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Byron - Pleasant Valley |  | 16.30
X |  |  | 345 kV | 2-795, 2-954 kcmil | ACSR | A.C. | Chisago Co - Kohlman Lake |  | 36.75
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Coon Creek - Kohlman Lake |  | 19.94
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Coon Creek - Sherburne Co (1) |  | 33.10
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Coon Creek - Sherburne Co (3) |  | 43.49
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Coon Creek - Terminal |  | 13.70
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Crandal - Fieldon South |  | 23.27
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Crandal - Lakefield Gen SW |  | 2.20
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Dickinson (GRE) - Parkers Lake |  | 9.72
X |  |  | 345 kV | 2-795, 2312 kcmil | ACSR | A.C. | Eden Prairie - Parkers Lake |  | 9.50
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Elm Creek - Monticello |  | 26.1
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Elm Creek - Parkers Lake |  | 11.01
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Fieldon North - Wilmarth |  | 29.16
X |  |  | 345 kV | 2-954, 2-795 kcmil | ACSR | A.C. | Hampton Corners - Blue Lake |  | 33.10
X |  |  | 345 kV | 2-954 kcmil | ACSS TW | A.C. | Hampton Corners - Chub Lake (GRE) |  | 18.40
X |  |  | 345 kV | 2-397.5 kcmil | TACSR/VR2 | A.C. | Hampton Corners - North Rochester |  | 37.30
X |  |  | 345 kV | 2-954 kcmil | ACSS | A.C. | Hampton Corners - Prairie Island |  | 19.60
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Hawks Nest - Lyon Co |  | 30.50
X |  |  | 345 kV | 2-954 kcmil | ACSS TW | A.C. | Helena - Cedar Mountain (GRE) (1) |  | 72.40
X |  |  | 345 kV | 2-954 kcmil | ACSS TW | A.C. | Helena - Cedar Mountain (GRE) (2) |  | 73.40
X |  |  | 345 kV | 2-954 kcmil | ACSS TW | A.C. | Helena - Chub Lake (GRE) |  | 20.80
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Helena - Sheas Lake |  | 7.50
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Inver Hills - Blue Lake |  | 22.40
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Kohlman Lake - Terminal |  | 10.14
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Lakefield Jct - Lakefield Gen SW |  | 18.62
X |  |  | 345 kV | 2-954, 2-397 kcmil | ACSS/TW, TACSR/TP | A.C. | Lakefield Jct - Nobles County |  | 35.81
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Lyon Co - Cedar Mountain (GRE) (1) |  | 50.40
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Lyon Co - Cedar Mountain (GRE) (2) |  | 50.80
X |  |  | 345 kV | 2-954 kcmil | ACSS | A.C. | Lyon Co - Hazel Creek |  | 24.20
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Mankato Energy Center - Wilmart |  | 0.22
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Monticello - Sherburne Co |  | 5.80
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Nobles County - Split Rock |  | 42.57
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | North Rochester - Prairie Island |  | 27.20
X |  |  | 345 kV | 2-795, 2-954 kcmil | ACSR | A.C. | Prairie Island - Red Rock (1) |  | 32.20
X |  |  | 345 kV | 2-795, 2-954 kcmil | ACSR | A.C. | Prairie Island - Red Rock (2) |  | 31.99
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Quarry - Monticello |  | 28.80
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Quarry - Riverview Road (GRE) |  | 35.10
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Red Rock - Inver Hills |  | 8.60
X |  |  | 345 kV | 2-795 kcmil | ACSR, ACSS | A.C. | Scott County - Helena |  | 17.17
X |  |  | 345 kV | 2-795 kcmil | ACSR | A.C. | Sheas Lake - Wilmarth |  | 24.75
X |  |  | 345 kV | 2-954 kcmil | ACSR | A.C. | Sherburne Co - Bunker Lake (GRE) |  | 36.56
X |  |  | 345 kV | 2-954 kcmil | ACSS/TW | A.C. | Steep Bank Lake - Hawks Nest |  | 9.90
X |  |  | 230 kV | 795, 183 kcmil | ACSR, ACCR | A.C. | Auduban (OTP) - Hubbard |  | 38.56
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Blue Lake - McLeod (GRE) |  | 44.60
X |  |  | 230 kV | 795 kcmil | ACSS | A.C. | Boswell (MP) - Zemple (MP) |  | 7.15
X |  |  | 230 kV | 795 kcmil | ACSS | A.C. | Cass Lake (OTP) - Wilton (MPC) |  | 19.37
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Granite Falls (WAPA) - Minn Valley Tap |  | 2.50
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | McLeod (GRE) - Panther (GRE) |  | 28.50
X |  |  | 230 kV | 2-954 kcmil | ACSR | A.C. | Minn Valley - Hazel Creek |  | 4.60
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Minn Valley - Minn Valley Tap |  | 0.20
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Minn Valley Tap - Panther (GRE) |  | 30.20
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Paynesville Tran - Willmar |  | 29.87
X |  |  | 230 kV | 795, 1272 kcmil | ACSR | A.C. | Red Rock - Rush City (GRE) |  | 59.63
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Rock Creek - Bear Creek (GRE) |  | 12.0
X |  |  | 230 kV | 795 kcmil | ACSR | A.C. | Rock Creek - Rush City (GRE) |  | 8.30
X |  |  | 230 kV | 795 kcmil | ACSS | A.C. | Zemple (MP) - Cass Lake (OTP) |  | 44.16
X |  |  | 345 kV | 2-556 kcmil | ACSR/T2 | A.C. | Huntley - Wilmarth |  | 52.04
X |  |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Brookings County - Lyon County (2) |  | 59.24
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Hampton - Helena (2) | 2025 | 38.98
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Big Oaks - Riverview (GRE) - Alexandria | 2030 | 95
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Wilmarth - North Rochester | 2029 | 72
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | North Rochester - Tremval | 2029 | 44
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Sherburne Co Gen Tie | 2028 | 160
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Bison - Alexandria (MRES) | 2032 | 136
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Bison-Hankinson (OTP) | 2034 | 40
|  |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Lyon Co-Lakefield Jct (ITC) | 2034 | 65
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | Pleasant Valley (GRE)-North Rochester | 2032 | 31
| X |  | 345 kV | 2-636 kcmil | ACSR/TP | A.C. | North Rochester-Hampton (2) | 2032 | 38
| X |  | 765 kV |  |  | A.C. | Big Stone (OTP)-Brookings | 2034 | 65
| X |  | 765 kV |  |  | A.C. | Brookings-Lakeifeld Jct (ITC) | 2034 | 103
| X |  | 765 kV |  |  | A.C. | Pleasant Valley (GRE)-North Rochester | 2034 | 31
| X |  | 765 kV |  |  | A.C. | North Rochester-Mississippi River | 2034 | 139
COMMENTS
Rows 102-105 do not indicate size of conductor or type of conductor as they are unknown at this time while standards are still being developed.

## PeakDay
MINNESOTA ELECTRIC UTILITY INFORMATION REPORTING - FORECAST SECTION (Continued)
CY 2024 |  |  |  | * * * CORRECTED * * * | * * * CORRECTED * * *
7610.0600, item A. 24 - HOUR PEAK DAY DEMAND
Each utility shall provide the following information for the last calendar year:
A table of the demand in megawatts by the hour over a 24-hour period for:
1. the 24-hour period during the summer season when the megawatt demand on the system was the greatest; and
2. the 24-hour period during the winter season when the megawatt demand on the system was the greatest.
| DATE OF PEAK DAY DEMAND | DATE OF PEAK DAY DEMAND
| 2024-08-26 | 2024-01-15 | <= ENTER DATES
TIME OF DAY | MW USED ON SUMMER PEAK DAY | MW USED ON WINTER PEAK DAY
0100 | 5567.04 | 4806.3501
0200 | 5322.77 | 4712.8601
0300 | 5191.59 | 4704.4101
0400 | 5100.24 | 4694.5801
0500 | 5184.07 | 4840.1501
0600 | 5487 | 5076.7708
0700 | 5972.2556 | 5463.8827
0800 | 6390.6597 | 5736.168
0900 | 6737.8882 | 5863.2094
1000 | 7131.4734 | 5921.0862
1100 | 7594.0492 | 5948.6554
1200 | 8002.3856 | 5951.4133
1300 | 8327.577 | 5938.0094
1400 | 8603.4334 | 5930.6913
1500 | 8746.3722 | 5864.118
1600 | 8809.042 | 5884.5431
1700 | 8822.1949 | 5992.7282
1800 | 8763.9225 | 6269.9698
1900 | 8524.7646 | 6255.3201
2000 | 7694.762 | 6102.5101
2100 | 7052.3023 | 5946.4201
2200 | 6622.09 | 5712.0301
2300 | 6057.15 | 5428.9701
2400 | 5565.01 | 5169.9701
COMMENTS

## Attachments
MINNESOTA ELECTRIC UTILITY ANNUAL REPORT - FORECAST SECTION
CY 2024
REMEMBER TO SEND/UPLOAD THE FOLLOWING ATTACHMENTS:
DO NOT INSERT THE ATTACHMENT INTO THIS WORKBOOK |  | < = < = < | NOTE < = <
1 | Each utility shall report the following information in regard to each transmission line of 200 kilovolts now in existence: a. a map showing the location of each line; b. the design voltage of each line; c. the size and type of conductor; d. the approximate location of d.c. terminals or a.c. substations; and e. the approximate length of each line in Minnesota. (pursuant to MN Rules Chapter 7610.0500 Subpart 1, Existing transmission lines)
When submitting this workbook and attachments, please following the file naming format of:
ELEC_###_2024 Forecast Report (this workbook)
ELEC_###_2024 TL Map
NOTE: ### is your Utility Entity number found in Cell C5 on the Registration Tab

## BlankPlant (hidden)
MINNESOTA ELECTRIC UTILITY ANNUAL REPORT (Continued)
7610.0430 FUEL REQUIREMENTS AND GENERATION BY FUEL TYPE
POWER PLANT AND GENERATING UNIT DATA REPORT: 2003
INSTRUCTIONS: | Complete one worksheet for each power plant
Scroll down below the data entry tables to see the ALLOWABLE CODES to be used for Unit Status, Unit Type, Energy Source, Fuel Type, and Unit of Measure fields
Scroll down below the ALLOWABLE CODES to see DEFINITIONS for Capacity Factor, Operating Factor and Forced Outage Rate.
A. PLANT DATA
PLANT NAME |  |  | PLANT ID | (leave this cell blank)
STREET ADDRESS
CITY
STATE |  |  | NUMBER OF UNITS
ZIP CODE
COUNTY
CONTACT PERSON
TELEPHONE
B. INDIVIDUAL GENERATING UNIT DATA
| Unit ID # | Unit Status * | Unit Type ** | Year Installed | Energy Source *** | Net Generation (mwh) | Comments
C. UNIT CAPABILITY DATA |  | CAPACITY (MEGAWATTS)
| Unit ID # | Summer | Winter | Capacity Factor (%) | Operating Factor (%) | Forced Outage Rate (%) | Comments
D. UNIT FUEL USED |  | PRIMARY FUEL USE |  |  |  | SECONDARY FUEL USE
| Unit ID # | Fuel Type *** | Quantity | Unit of Measure **** | BTU Content (for coal only) | Fuel Type | Quantity | Unit of Measure **** | BTU Content (for coal only)
ALLOWABLE CODES
Cell Heading | Code | Code Definition |  | Cell Heading | Code | Code Definition
* Unit Status | USE | In-use |  | ** Unit Type | CS | Combined Cycle
| STB | Stand-by |  |  | IC | Internal Combustion (Diesel)
| RET | Retired |  |  | GT | Combustion (Gas) Turbine
| FUT | Future |  |  | HC | Hydro
| OTHER | Other - provide description |  |  | ST | Steam Turbine (Boiler)
[5 empty] | NC | Nuclear
*** Energy Source & | BIT | Bituminous Coal |  |  | WI | Wind
Fuel Type | COAL | Coal (general) |  |  | OTHER | Other - provide description
| DIESEL | Diesel
| FO2 | Fuel Oil #2 (Mid Distillate) |  | **** Unit of Measure | GAL | Gallons
| FO6 | Fuel Oil #6 (Residual Fuel Oil) |  |  | MCF | Thousand cubic feet
| LIG | Lignite |  |  | MMCF | Million cubic feet
| LPG | Liquefied Propane Gas |  |  | TONS | Tons
| NG | Natural Gas |  |  | BBL | Barrels
| NUC | Nuclear |  |  | THERMS | Therms
| REF | Refuse, Bagasse, Peat, Non-wood waste
| STM | Steam
| SUB | Sub-Bituminous Coal
| HYD | Hydro (Water)
| WIND | Wind
| WOOD | Wood
| SOLAR | Solar
| OTHER | Other - provide description
DEFINITIONS
Forced Outage Rate = | Hours Unit Failed to be Available X 100 |  |  | Note: Failure of a unit to be available does not include down time for scheduled maintenance.
(percentage) | Hours Unit Called Upon to Produce
Operating Availability = | 100 - Maintenance percentage - Forced Outage percentage |  |  | Note: Maintenance percentage is the number of hours of scheduled maintenance divided by 8,760.
(percentage)
Capacity Factor = | Total Annual MWH of Production X 100
(percentage) | Accredited Capacity Rating (MW) of the Unit X 8,760